## Table 1
Fan Performance — Vertical Discharge Units
48A2,A3,A6,A7 020 (20 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
4000 | 328 |  | 0.62 |  |  | 406 |  | 0.84 | 472 |  | 1.07 | 529 |  | 1.3 |  |  | 580 |  | 1.54 |  |  | 626 |  |  | 1.78 |  |  | 668 |  | 2.02 |  |  | 708 |  | 2.27 | 745 |  | 2.51 | 780 |  | 2.76
5000 | 369 |  | 0.97 |  |  | 439 |  | 1.19 | 500 |  | 1.43 | 554 |  | 1.69 |  |  | 604 |  | 1.95 |  |  | 650 |  |  | 2.21 |  |  | 692 |  | 2.48 |  |  | 731 |  | 2.74 | 769 |  | 3.01 | 804 |  | 3.28
6000 | 415 |  | 1.43 |  |  | 477 |  | 1.65 | 533 |  | 1.9 | 584 |  | 2.17 |  |  | 631 |  | 2.45 |  |  | 676 |  |  | 2.73 |  |  | 717 |  | 3.01 |  |  | 756 |  | 3.3 | 793 |  | 3.59 | 828 |  | 3.88
7000 | 463 |  | 2.01 |  |  | 519 |  | 2.25 | 570 |  | 2.5 | 618 |  | 2.78 |  |  | 662 |  | 3.06 |  |  | 704 |  |  | 3.36 |  |  | 744 |  | 3.65 |  |  | 782 |  | 3.96 | 818 |  | 4.27 | 852 |  | 4.58
7500 | 488 |  | 2.36 |  |  | 541 |  | 2.6 | 590 |  | 2.86 | 636 |  | 3.13 |  |  | 679 |  | 3.42 |  |  | 720 |  |  | 3.72 |  |  | 759 |  | 4.02 |  |  | 796 |  | 4.33 | 832 |  | 4.65 | 866 |  | 4.96
8000 | 513 |  | 2.74 |  |  | 564 |  | 2.98 | 611 |  | 3.24 | 655 |  | 3.52 |  |  | 697 |  | 3.81 |  |  | 737 |  |  | 4.11 |  |  | 775 |  | 4.42 |  |  | 811 |  | 4.74 | 846 |  | 5.06 | 879 |  | 5.38
9000 | 564 |  | 3.61 |  |  | 612 |  | 3.87 | 655 |  | 4.13 | 696 |  | 4.42 |  |  | 735 |  | 4.71 |  |  | 772 |  |  | 5.02 |  |  | 808 |  | 5.33 |  |  | 843 |  | 5.65 | 876 |  | 5.98 | 909 |  | 6.32
10000 | 616 |  | 4.64 |  |  | 661 |  | 4.91 | 701 |  | 5.18 | 739 |  | 5.47 |  |  | 776 |  | 5.77 |  |  | 811 |  |  | 6.08 |  |  | 845 |  | 6.4 |  |  | 878 |  | 6.72 | 909 |  | 7.06 | 940 |  | 7.4
48A2,A3,A6,A7 020 (20 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
4000 | 814 |  | 3.01 |  |  | 845 |  | 3.26 | 876 |  | 3.51 | 905 |  | 3.76 |  |  | 934 |  | 4.02 |  |  | 961 |  |  | 4.28 |  |  | 987 |  | 4.54 |  |  | 1013 |  | 4.8 | 1038 |  | 5.06 | 1062 |  | 5.32
5000 | 837 |  | 3.55 |  |  | 869 |  | 3.82 | 900 |  | 4.1 | 929 |  | 4.37 |  |  | 958 |  | 4.64 |  |  | 985 |  |  | 4.92 |  |  | 1012 |  | 5.2 |  |  | 1038 |  | 5.48 | 1063 |  | 5.76 | 1087 |  | 6.04
6000 | 861 |  | 4.17 |  |  | 893 |  | 4.46 | 923 |  | 4.76 | 953 |  | 5.05 |  |  | 981 |  | 5.35 |  |  | 1009 |  |  | 5.65 |  |  | 1036 |  | 5.94 |  |  | 1062 |  | 6.24 | 1087 |  | 6.54 | 1111 |  | 6.84
7000 | 885 |  | 4.89 |  |  | 917 |  | 5.2 | 947 |  | 5.51 | 977 |  | 5.83 |  |  | 1005 |  | 6.14 |  |  | 1033 |  |  | 6.46 |  |  | 1059 |  | 6.78 |  |  | 1085 |  | 7.09 | 1110 |  | 7.41 | 1135 |  | 7.73
7500 | 898 |  | 5.28 |  |  | 930 |  | 5.61 | 960 |  | 5.93 | 989 |  | 6.25 |  |  | 1017 |  | 6.58 |  |  | 1045 |  |  | 6.9 |  |  | 1071 |  | 7.23 |  |  | 1097 |  | 7.56 | 1122 |  | 7.88 | 1147 |  | 8.21
8000 | 912 |  | 5.71 |  |  | 943 |  | 6.04 | 973 |  | 6.37 | 1002 |  | 6.7 |  |  | 1030 |  | 7.04 |  |  | 1057 |  |  | 7.37 |  |  | 1083 |  | 7.71 |  |  | 1109 |  | 8.04 | 1134 |  | 8.38 | 1159 |  | 8.72
9000 | 940 |  | 6.66 |  |  | 970 |  | 7 | 999 |  | 7.35 | 1028 |  | 7.69 |  |  | 1055 |  | 8.04 |  |  | 1082 |  |  | 8.39 |  |  | 1109 |  | 8.75 |  |  | 1134 |  | 9.1 | 1159 |  | 9.45 | 1183 |  | 9.81
10000 | 971 |  | 7.75 |  |  | 1000 |  | 8.1 | 1028 |  | 8.46 | 1056 |  | 8.82 |  |  | 1083 |  | 9.18 |  |  | 1109 |  |  | 9.54 |  |  | 1135 |  | 9.91 |  |  | 1160 |  | 10.28 | 1185 |  | 10.65 | — |  | —
48A2,A3,A6,A7 025-030 (25 THRU 30 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
5000 | 374 |  | 0.98 |  |  | 443 |  | 1.2 | 503 |  | 1.45 | 558 |  | 1.7 |  |  | 607 |  | 1.96 |  |  | 653 |  |  | 2.23 |  |  | 695 |  | 2.49 |  |  | 734 |  | 2.76 | 771 |  | 3.03 | 806 |  | 3.3
6000 | 421 |  | 1.45 |  |  | 482 |  | 1.68 | 538 |  | 1.93 | 589 |  | 2.2 |  |  | 636 |  | 2.47 |  |  | 680 |  |  | 2.75 |  |  | 721 |  | 3.04 |  |  | 759 |  | 3.33 | 796 |  | 3.62 | 831 |  | 3.91
7000 | 471 |  | 2.04 |  |  | 526 |  | 2.28 | 576 |  | 2.54 | 623 |  | 2.81 |  |  | 668 |  | 3.1 |  |  | 710 |  |  | 3.39 |  |  | 749 |  | 3.69 |  |  | 787 |  | 4 | 823 |  | 4.31 | 857 |  | 4.62
8000 | 522 |  | 2.78 |  |  | 572 |  | 3.03 | 619 |  | 3.29 | 662 |  | 3.57 |  |  | 704 |  | 3.86 |  |  | 743 |  |  | 4.16 |  |  | 781 |  | 4.47 |  |  | 817 |  | 4.79 | 851 |  | 5.11 | 885 |  | 5.44
9000 | 574 |  | 3.66 |  |  | 621 |  | 3.92 | 664 |  | 4.19 | 704 |  | 4.47 |  |  | 743 |  | 4.77 |  |  | 780 |  |  | 5.08 |  |  | 815 |  | 5.4 |  |  | 850 |  | 5.72 | 883 |  | 6.05 | 915 |  | 6.39
10000 | 628 |  | 4.71 |  |  | 671 |  | 4.97 | 711 |  | 5.25 | 748 |  | 5.54 |  |  | 784 |  | 5.84 |  |  | 819 |  |  | 6.15 |  |  | 853 |  | 6.47 |  |  | 885 |  | 6.81 | 917 |  | 7.14 | 948 |  | 7.49
11000 | 682 |  | 5.91 |  |  | 722 |  | 6.19 | 759 |  | 6.48 | 795 |  | 6.77 |  |  | 828 |  | 7.08 |  |  | 861 |  |  | 7.4 |  |  | 893 |  | 7.72 |  |  | 924 |  | 8.06 | 954 |  | 8.4 | 983 |  | 8.75
12000 | 736 |  | 7.3 |  |  | 774 |  | 7.59 | 809 |  | 7.88 | 842 |  | 8.18 |  |  | 874 |  | 8.49 |  |  | 905 |  |  | 8.82 |  |  | 935 |  | 9.15 |  |  | 965 |  | 9.48 | 993 |  | 9.83 | 1021 |  | 10.19
13000 | 791 |  | 8.86 |  |  | 827 |  | 9.16 | 860 |  | 9.46 | 891 |  | 9.78 |  |  | 922 |  | 10.09 |  |  | 951 |  |  | 10.42 |  |  | 979 |  | 10.75 |  |  | 1007 |  | 11.1 | 1034 |  | 11.45 | 1061 |  | 11.8
14000 | 846 |  | 10.61 |  |  | 880 |  | 10.93 | 912 |  | 11.24 | 941 |  | 11.56 |  |  | 970 |  | 11.88 |  |  | 998 |  |  | 12.21 |  |  | 1025 |  | 12.56 |  |  | 1052 |  | 12.9 | 1078 |  | 13.26 | 1103 |  | 13.62
15000 | 902 |  | 12.56 |  |  | 934 |  | 12.89 | 964 |  | 13.21 | 992 |  | 13.54 |  |  | 1020 |  | 13.87 |  |  | 1046 |  |  | 14.21 |  |  | 1072 |  | 14.55 |  |  | 1098 |  | 14.91 | 1122 |  | 15.26 | 1147 |  | 15.63
48A2,A3,A6,A7 025-030 (25 THRU 30 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
5000 | 839 |  | 3.57 |  |  | 871 |  | 3.84 | 902 |  | 4.11 | 931 |  | 4.39 |  |  | 960 |  | 4.66 |  |  | 987 |  |  | 4.94 |  |  | 1014 |  | 5.22 |  |  | 1039 |  | 5.5 | 1064 |  | 5.78 | 1089 |  | 6.06
6000 | 864 |  | 4.2 |  |  | 896 |  | 4.49 | 926 |  | 4.79 | 956 |  | 5.08 |  |  | 984 |  | 5.38 |  |  | 1012 |  |  | 5.68 |  |  | 1038 |  | 5.97 |  |  | 1064 |  | 6.27 | 1089 |  | 6.57 | 1114 |  | 6.87
7000 | 890 |  | 4.93 |  |  | 921 |  | 5.24 | 951 |  | 5.55 | 980 |  | 5.87 |  |  | 1009 |  | 6.18 |  |  | 1036 |  |  | 6.5 |  |  | 1063 |  | 6.82 |  |  | 1088 |  | 7.14 | 1114 |  | 7.45 | 1138 |  | 7.77
8000 | 917 |  | 5.76 |  |  | 948 |  | 6.09 | 977 |  | 6.42 | 1006 |  | 6.76 |  |  | 1034 |  | 7.09 |  |  | 1061 |  |  | 7.43 |  |  | 1088 |  | 7.76 |  |  | 1113 |  | 8.1 | 1138 |  | 8.43 | 1163 |  | 8.77
9000 | 946 |  | 6.73 |  |  | 976 |  | 7.07 | 1005 |  | 7.42 | 1033 |  | 7.76 |  |  | 1061 |  | 8.11 |  |  | 1088 |  |  | 8.46 |  |  | 1114 |  | 8.82 |  |  | 1139 |  | 9.17 | 1164 |  | 9.52 | 1188 |  | 9.88
10000 | 978 |  | 7.84 |  |  | 1007 |  | 8.19 | 1035 |  | 8.55 | 1063 |  | 8.91 |  |  | 1089 |  | 9.27 |  |  | 1116 |  |  | 9.63 |  |  | 1141 |  | 10 |  |  | 1166 |  | 10.37 | 1191 |  | 10.74 | — |  | —
11000 | 1012 |  | 9.1 |  |  | 1040 |  | 9.47 | 1067 |  | 9.83 | 1094 |  | 10.2 |  |  | 1120 |  | 10.57 |  |  | 1145 |  |  | 10.95 |  |  | 1170 |  | 11.33 |  |  | 1195 |  | 11.71 | — |  | — | — |  | —
12000 | 1048 |  | 10.54 |  |  | 1075 |  | 10.91 | 1102 |  | 11.28 | 1127 |  | 11.66 |  |  | 1152 |  | 12.04 |  |  | 1177 |  |  | 12.42 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
13000 | 1087 |  | 12.17 |  |  | 1113 |  | 12.54 | 1138 |  | 12.91 | 1163 |  | 13.3 |  |  | 1187 |  | 13.68 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
14000 | 1128 |  | 13.98 |  |  | 1153 |  | 14.36 | 1177 |  | 14.74 | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
15000 | 1171 |  | 16 |  |  | 1194 |  | 16.38 | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet | [17 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
48A2,A3,A6,A7 035 (35 TONS)
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
7000 | 534 |  | 2.46 |  |  | 584 |  | 2.8 | 630 |  | 3.13 | 674 |  | 3.48 |  |  | 716 |  | 3.82 |  |  | 756 |  |  | 4.16 |  |  | 793 |  | 4.5 |  |  | 829 |  | 4.83 | 863 |  | 5.17 | 896 |  | 5.49
8000 | 590 |  | 3.27 |  |  | 635 |  | 3.63 | 677 |  | 3.99 | 718 |  | 4.35 |  |  | 757 |  | 4.72 |  |  | 794 |  |  | 5.08 |  |  | 830 |  | 5.45 |  |  | 864 |  | 5.81 | 897 |  | 6.18 | 929 |  | 6.54
9000 | 646 |  | 4.23 |  |  | 687 |  | 4.62 | 726 |  | 5 | 764 |  | 5.38 |  |  | 800 |  | 5.76 |  |  | 835 |  |  | 6.15 |  |  | 869 |  | 6.54 |  |  | 902 |  | 6.93 | 934 |  | 7.31 | 964 |  | 7.7
10000 | 704 |  | 5.35 |  |  | 742 |  | 5.77 | 778 |  | 6.17 | 812 |  | 6.57 |  |  | 846 |  | 6.97 |  |  | 879 |  |  | 7.38 |  |  | 911 |  | 7.78 |  |  | 942 |  | 8.19 | 972 |  | 8.6 | 1002 |  | 9.01
10500 | 733 |  | 5.97 |  |  | 769 |  | 6.4 | 804 |  | 6.82 | 837 |  | 7.23 |  |  | 870 |  | 7.64 |  |  | 902 |  |  | 8.05 |  |  | 933 |  | 8.46 |  |  | 963 |  | 8.88 | 992 |  | 9.3 | 1021 |  | 9.72
11000 | 762 |  | 6.63 |  |  | 797 |  | 7.08 | 830 |  | 7.51 | 863 |  | 7.93 |  |  | 894 |  | 8.35 |  |  | 925 |  |  | 8.77 |  |  | 955 |  | 9.19 |  |  | 984 |  | 9.62 | 1013 |  | 10.04 | 1041 |  | 10.47
12000 | 820 |  | 8.09 |  |  | 853 |  | 8.56 | 884 |  | 9.01 | 915 |  | 9.46 |  |  | 944 |  | 9.9 |  |  | 973 |  |  | 10.34 |  |  | 1001 |  | 10.78 |  |  | 1029 |  | 11.22 | 1056 |  | 11.66 | 1083 |  | 12.1
13000 | 879 |  | 9.72 |  |  | 909 |  | 10.22 | 939 |  | 10.7 | 968 |  | 11.17 |  |  | 996 |  | 11.63 |  |  | 1023 |  |  | 12.09 |  |  | 1050 |  | 12.55 |  |  | 1076 |  | 13.01 | 1102 |  | 13.46 | 1127 |  | 13.92
14000 | 938 |  | 11.54 |  |  | 967 |  | 12.07 | 995 |  | 12.58 | 1022 |  | 13.07 |  |  | 1048 |  | 13.55 |  |  | 1074 |  |  | 14.03 |  |  | 1099 |  | 14.51 |  |  | 1124 |  | 14.98 | 1149 |  | 15.46 | 1173 |  | 15.93
15000 | 997 |  | 13.56 |  |  | 1024 |  | 14.11 | 1051 |  | 14.64 | 1076 |  | 15.16 |  |  | 1102 |  | 15.67 |  |  | 1126 |  |  | 16.17 |  |  | 1150 |  | 16.66 |  |  | 1174 |  | 17.16 | 1197 |  | 17.65 | 1220 |  | 18.14
16000 | 1056 |  | 15.78 |  |  | 1082 |  | 16.35 | 1107 |  | 16.91 | 1132 |  | 17.45 |  |  | 1156 |  | 17.98 |  |  | 1179 |  |  | 18.5 |  |  | 1202 |  | 19.02 |  |  | 1225 |  | 19.53 | 1247 |  | 20.04 | 1269 |  | 20.55
17000 | 1116 |  | 18.2 |  |  | 1140 |  | 18.8 | 1164 |  | 19.38 | 1188 |  | 19.95 |  |  | 1210 |  | 20.5 |  |  | 1233 |  |  | 21.05 |  |  | 1255 |  | 21.58 |  |  | 1276 |  | 22.11 | 1298 |  | 22.64 | — |  | —
17500 | 1145 |  | 19.49 |  |  | 1170 |  | 20.1 | 1193 |  | 20.7 | 1216 |  | 21.28 |  |  | 1238 |  | 21.84 |  |  | 1260 |  |  | 22.4 |  |  | 1282 |  | 22.94 |  |  | — |  | — | — |  | — | — |  | —
48A2,A3,A6,A7 035 (35 TONS) (cont)
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
7000 | 927 |  | 5.81 |  |  | 956 |  | 6.13 | 985 |  | 6.45 | 1012 |  | 6.76 |  |  | 1039 |  | 7.06 |  |  | 1065 |  |  | 7.37 |  |  | 1090 |  | 7.67 |  |  | 1114 |  | 7.97 | 1138 |  | 8.26 | 1161 |  | 8.56
8000 | 960 |  | 6.89 |  |  | 989 |  | 7.25 | 1018 |  | 7.6 | 1045 |  | 7.94 |  |  | 1072 |  | 8.29 |  |  | 1098 |  |  | 8.63 |  |  | 1122 |  | 8.96 |  |  | 1147 |  | 9.29 | 1170 |  | 9.62 | 1193 |  | 9.95
9000 | 994 |  | 8.09 |  |  | 1023 |  | 8.47 | 1051 |  | 8.85 | 1078 |  | 9.23 |  |  | 1104 |  | 9.61 |  |  | 1130 |  |  | 9.98 |  |  | 1155 |  | 10.35 |  |  | 1179 |  | 10.71 | 1203 |  | 11.08 | 1226 |  | 11.44
10000 | 1030 |  | 9.42 |  |  | 1058 |  | 9.82 | 1085 |  | 10.23 | 1112 |  | 10.64 |  |  | 1138 |  | 11.04 |  |  | 1163 |  |  | 11.44 |  |  | 1188 |  | 11.84 |  |  | 1212 |  | 12.24 | 1235 |  | 12.64 | 1258 |  | 13.03
10500 | 1049 |  | 10.14 |  |  | 1077 |  | 10.56 | 1103 |  | 10.97 | 1129 |  | 11.39 |  |  | 1155 |  | 11.81 |  |  | 1180 |  |  | 12.23 |  |  | 1204 |  | 12.64 |  |  | 1228 |  | 13.05 | 1251 |  | 13.46 | 1274 |  | 13.87
11000 | 1069 |  | 10.9 |  |  | 1095 |  | 11.33 | 1122 |  | 11.76 | 1147 |  | 12.18 |  |  | 1173 |  | 12.61 |  |  | 1197 |  |  | 13.04 |  |  | 1221 |  | 13.47 |  |  | 1245 |  | 13.89 | 1268 |  | 14.31 | 1291 |  | 14.73
12000 | 1109 |  | 12.55 |  |  | 1135 |  | 13 | 1160 |  | 13.44 | 1185 |  | 13.89 |  |  | 1209 |  | 14.34 |  |  | 1233 |  |  | 14.79 |  |  | 1256 |  | 15.24 |  |  | 1279 |  | 15.69 | — |  | — | — |  | —
13000 | 1152 |  | 14.38 |  |  | 1176 |  | 14.84 | 1200 |  | 15.31 | 1224 |  | 15.77 |  |  | 1248 |  | 16.24 |  |  | 1271 |  |  | 16.7 |  |  | 1293 |  | 17.17 |  |  | — |  | — | — |  | — | — |  | —
14000 | 1196 |  | 16.41 |  |  | 1220 |  | 16.88 | 1243 |  | 17.36 | 1266 |  | 17.84 |  |  | 1288 |  | 18.32 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
15000 | 1243 |  | 18.63 |  |  | 1265 |  | 19.12 | 1287 |  | 19.61 | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
16000 | 1290 |  | 21.06 |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
17000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
17500 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
48A2,A3,A6,A7040 (40 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
8000 | 502 |  | 2.9 |  |  | 550 |  | 3.3 | 596 |  | 3.71 | 639 |  | 4.12 |  |  | 680 |  | 4.54 |  |  | 720 |  |  | 4.97 |  |  | 759 |  | 5.4 |  |  | 796 |  | 5.85 | 832 |  | 6.31 | 867 |  | 6.77
9000 | 552 |  | 3.81 |  |  | 595 |  | 4.24 | 637 |  | 4.67 | 677 |  | 5.11 |  |  | 715 |  | 5.55 |  |  | 752 |  |  | 6 |  |  | 788 |  | 6.45 |  |  | 823 |  | 6.92 | 857 |  | 7.39 | 890 |  | 7.87
10000 | 602 |  | 4.89 |  |  | 642 |  | 5.34 | 680 |  | 5.8 | 717 |  | 6.26 |  |  | 752 |  | 6.73 |  |  | 787 |  |  | 7.2 |  |  | 821 |  | 7.67 |  |  | 854 |  | 8.16 | 886 |  | 8.64 | 917 |  | 9.14
11000 | 653 |  | 6.15 |  |  | 689 |  | 6.62 | 725 |  | 7.11 | 759 |  | 7.59 |  |  | 792 |  | 8.08 |  |  | 825 |  |  | 8.58 |  |  | 856 |  | 9.07 |  |  | 887 |  | 9.57 | 918 |  | 10.08 | 947 |  | 10.59
12000 | 704 |  | 7.6 |  |  | 738 |  | 8.09 | 771 |  | 8.6 | 803 |  | 9.11 |  |  | 834 |  | 9.63 |  |  | 865 |  |  | 10.14 |  |  | 895 |  | 10.66 |  |  | 924 |  | 11.18 | 952 |  | 11.71 | 980 |  | 12.24
13000 | 756 |  | 9.24 |  |  | 788 |  | 9.76 | 818 |  | 10.29 | 848 |  | 10.83 |  |  | 878 |  | 11.36 |  |  | 906 |  |  | 11.9 |  |  | 935 |  | 12.44 |  |  | 962 |  | 12.99 | 989 |  | 13.53 | 1016 |  | 14.08
14000 | 808 |  | 11.1 |  |  | 838 |  | 11.64 | 867 |  | 12.19 | 895 |  | 12.74 |  |  | 922 |  | 13.3 |  |  | 950 |  |  | 13.87 |  |  | 976 |  | 14.43 |  |  | 1002 |  | 15 | 1028 |  | 15.57 | 1053 |  | 16.14
15000 | 861 |  | 13.18 |  |  | 888 |  | 13.74 | 915 |  | 14.31 | 942 |  | 14.88 |  |  | 968 |  | 15.46 |  |  | 994 |  |  | 16.05 |  |  | 1019 |  | 16.63 |  |  | 1044 |  | 17.22 | 1068 |  | 17.81 | 1093 |  | 18.4
16000 | 914 |  | 15.49 |  |  | 940 |  | 16.06 | 965 |  | 16.65 | 990 |  | 17.24 |  |  | 1015 |  | 17.85 |  |  | 1039 |  |  | 18.45 |  |  | 1063 |  | 19.06 |  |  | 1087 |  | 19.67 | 1110 |  | 20.28 | 1133 |  | 20.89
17000 | 967 |  | 18.03 |  |  | 991 |  | 18.62 | 1015 |  | 19.23 | 1039 |  | 19.85 |  |  | 1062 |  | 20.47 |  |  | 1086 |  |  | 21.09 |  |  | 1109 |  | 21.72 |  |  | 1131 |  | 22.35 | 1153 |  | 22.98 | 1175 |  | 23.61
18000 | 1020 |  | 20.82 |  |  | 1043 |  | 21.43 | 1066 |  | 22.06 | 1088 |  | 22.69 |  |  | 1111 |  | 23.33 |  |  | 1133 |  |  | 23.97 |  |  | 1155 |  | 24.62 |  |  | 1176 |  | 25.27 | 1197 |  | 25.92 | 1219 |  | 26.58
19000 | 1073 |  | 23.87 |  |  | 1095 |  | 24.5 | 1117 |  | 25.14 | 1138 |  | 25.79 |  |  | 1159 |  | 26.44 |  |  | 1180 |  |  | 27.11 |  |  | 1201 |  | 27.77 |  |  | 1222 |  | 28.45 | 1242 |  | 29.12 | — |  | —
20000 | 1127 |  | 27.18 |  |  | 1147 |  | 27.82 | 1168 |  | 28.48 | 1188 |  | 29.15 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
48A2,A3,A6,A7040 (40 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
8000 | 901 |  | 7.24 |  |  | 933 |  | 7.72 | 965 |  | 8.2 | 995 |  | 8.69 |  |  | 1024 |  | 9.19 |  |  | 1053 |  |  | 9.69 |  |  | 1081 |  | 10.19 |  |  | 1108 |  | 10.7 | 1134 |  | 11.21 | 1159 |  | 11.73
9000 | 923 |  | 8.35 |  |  | 954 |  | 8.85 | 985 |  | 9.35 | 1014 |  | 9.86 |  |  | 1043 |  | 10.37 |  |  | 1072 |  |  | 10.89 |  |  | 1099 |  | 11.41 |  |  | 1126 |  | 11.94 | 1152 |  | 12.47 | 1177 |  | 13
10000 | 948 |  | 9.64 |  |  | 978 |  | 10.15 | 1007 |  | 10.66 | 1036 |  | 11.19 |  |  | 1064 |  | 11.71 |  |  | 1092 |  |  | 12.25 |  |  | 1119 |  | 12.78 |  |  | 1145 |  | 13.33 | 1171 |  | 13.88 | 1196 |  | 14.43
11000 | 976 |  | 11.11 |  |  | 1005 |  | 11.63 | 1033 |  | 12.16 | 1061 |  | 12.7 |  |  | 1088 |  | 13.24 |  |  | 1114 |  |  | 13.79 |  |  | 1140 |  | 14.34 |  |  | 1166 |  | 14.9 | 1191 |  | 15.46 | 1216 |  | 16.03
12000 | 1008 |  | 12.77 |  |  | 1035 |  | 13.31 | 1062 |  | 13.86 | 1088 |  | 14.41 |  |  | 1114 |  | 14.97 |  |  | 1139 |  |  | 15.53 |  |  | 1164 |  | 16.09 |  |  | 1189 |  | 16.67 | 1213 |  | 17.24 | 1237 |  | 17.83
13000 | 1042 |  | 14.64 |  |  | 1068 |  | 15.19 | 1093 |  | 15.76 | 1118 |  | 16.32 |  |  | 1143 |  | 16.89 |  |  | 1167 |  |  | 17.47 |  |  | 1191 |  | 18.05 |  |  | 1215 |  | 18.64 | 1238 |  | 19.23 | 1262 |  | 19.82
14000 | 1078 |  | 16.71 |  |  | 1103 |  | 17.28 | 1127 |  | 17.86 | 1151 |  | 18.45 |  |  | 1174 |  | 19.03 |  |  | 1198 |  |  | 19.63 |  |  | 1221 |  | 20.22 |  |  | 1244 |  | 20.82 | 1266 |  | 21.43 | 1288 |  | 22.04
15000 | 1116 |  | 19 |  |  | 1140 |  | 19.59 | 1163 |  | 20.19 | 1186 |  | 20.79 |  |  | 1208 |  | 21.4 |  |  | 1230 |  |  | 22 |  |  | 1253 |  | 22.62 |  |  | 1274 |  | 23.23 | 1296 |  | 23.85 | — |  | —
16000 | 1156 |  | 21.51 |  |  | 1178 |  | 22.12 | 1200 |  | 22.74 | 1222 |  | 23.36 |  |  | 1244 |  | 23.98 |  |  | 1265 |  |  | 24.61 |  |  | 1286 |  | 25.24 |  |  | — |  | — | — |  | — | — |  | —
17000 | 1197 |  | 24.25 |  |  | 1218 |  | 24.89 | 1240 |  | 25.52 | 1261 |  | 26.17 |  |  | 1281 |  | 26.81 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
18000 | 1239 |  | 27.24 |  |  | 1260 |  | 27.89 | 1280 |  | 28.55 | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
19000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
20000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet | [17 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
48A2,A3,A6,A7050 (50 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
10000 | 611 |  | 5 |  |  | 651 |  | 5.45 | 689 |  | 5.91 | 725 |  | 6.37 |  |  | 761 |  | 6.84 |  |  | 795 |  |  | 7.31 |  |  | 829 |  | 7.79 |  |  | 861 |  | 8.27 | 893 |  | 8.76 | 925 |  | 9.26
11000 | 662 |  | 6.27 |  |  | 699 |  | 6.75 | 734 |  | 7.23 | 768 |  | 7.72 |  |  | 801 |  | 8.21 |  |  | 833 |  |  | 8.71 |  |  | 865 |  | 9.2 |  |  | 895 |  | 9.71 | 925 |  | 10.21 | 955 |  | 10.73
12000 | 714 |  | 7.74 |  |  | 748 |  | 8.24 | 780 |  | 8.75 | 812 |  | 9.26 |  |  | 843 |  | 9.77 |  |  | 873 |  |  | 10.29 |  |  | 903 |  | 10.81 |  |  | 932 |  | 11.33 | 960 |  | 11.86 | 988 |  | 12.39
13000 | 766 |  | 9.41 |  |  | 798 |  | 9.93 | 828 |  | 10.46 | 858 |  | 11 |  |  | 887 |  | 11.54 |  |  | 916 |  |  | 12.08 |  |  | 944 |  | 12.62 |  |  | 971 |  | 13.16 | 998 |  | 13.71 | 1024 |  | 14.26
14000 | 819 |  | 11.29 |  |  | 848 |  | 11.84 | 877 |  | 12.39 | 905 |  | 12.95 |  |  | 932 |  | 13.51 |  |  | 959 |  |  | 14.07 |  |  | 986 |  | 14.63 |  |  | 1012 |  | 15.2 | 1037 |  | 15.77 | 1062 |  | 16.34
15000 | 872 |  | 13.4 |  |  | 899 |  | 13.96 | 926 |  | 14.54 | 953 |  | 15.11 |  |  | 979 |  | 15.7 |  |  | 1004 |  |  | 16.28 |  |  | 1029 |  | 16.87 |  |  | 1054 |  | 17.46 | 1078 |  | 18.05 | 1102 |  | 18.64
16000 | 925 |  | 15.74 |  |  | 951 |  | 16.32 | 976 |  | 16.91 | 1001 |  | 17.51 |  |  | 1026 |  | 18.12 |  |  | 1050 |  |  | 18.72 |  |  | 1074 |  | 19.33 |  |  | 1097 |  | 19.94 | 1121 |  | 20.55 | 1143 |  | 21.17
17000 | 979 |  | 18.32 |  |  | 1003 |  | 18.92 | 1027 |  | 19.53 | 1051 |  | 20.15 |  |  | 1074 |  | 20.77 |  |  | 1097 |  |  | 21.4 |  |  | 1120 |  | 22.03 |  |  | 1142 |  | 22.66 | 1164 |  | 23.29 | 1186 |  | 23.93
18000 | 1032 |  | 21.15 |  |  | 1055 |  | 21.77 | 1078 |  | 22.4 | 1100 |  | 23.04 |  |  | 1123 |  | 23.68 |  |  | 1145 |  |  | 24.33 |  |  | 1166 |  | 24.98 |  |  | 1188 |  | 25.63 | 1209 |  | 26.28 | 1230 |  | 26.93
19000 | 1086 |  | 24.24 |  |  | 1108 |  | 24.88 | 1129 |  | 25.52 | 1151 |  | 26.18 |  |  | 1172 |  | 26.84 |  |  | 1193 |  |  | 27.51 |  |  | 1214 |  | 28.18 |  |  | 1234 |  | 28.85 | 1255 |  | 29.52 | 1275 |  | 30.19
20000 | 1140 |  | 27.6 |  |  | 1161 |  | 28.25 | 1181 |  | 28.92 | 1202 |  | 29.59 |  |  | 1222 |  | 30.27 |  |  | 1242 |  |  | 30.95 |  |  | 1262 |  | 31.64 |  |  | 1281 |  | 32.33 | — |  | — | — |  | —
48A2,A3,A6,A7050 (50 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
10000 | 955 |  | 9.76 |  |  | 985 |  | 10.27 | 1014 |  | 10.79 | 1043 |  | 11.31 |  |  | 1071 |  | 11.84 |  |  | 1098 |  |  | 12.37 |  |  | 1125 |  | 12.91 |  |  | 1151 |  | 13.46 | 1177 |  | 14.01 | 1202 |  | 14.56
11000 | 984 |  | 11.25 |  |  | 1012 |  | 11.77 | 1040 |  | 12.3 | 1068 |  | 12.84 |  |  | 1095 |  | 13.38 |  |  | 1121 |  |  | 13.93 |  |  | 1147 |  | 14.49 |  |  | 1172 |  | 15.05 | 1197 |  | 15.61 | 1222 |  | 16.18
12000 | 1016 |  | 12.93 |  |  | 1043 |  | 13.47 | 1069 |  | 14.02 | 1095 |  | 14.57 |  |  | 1121 |  | 15.13 |  |  | 1147 |  |  | 15.69 |  |  | 1172 |  | 16.26 |  |  | 1196 |  | 16.83 | 1220 |  | 17.41 | 1244 |  | 18
13000 | 1050 |  | 14.82 |  |  | 1076 |  | 15.38 | 1101 |  | 15.94 | 1126 |  | 16.51 |  |  | 1151 |  | 17.08 |  |  | 1175 |  |  | 17.66 |  |  | 1199 |  | 18.24 |  |  | 1223 |  | 18.83 | 1246 |  | 19.42 | 1269 |  | 20.02
14000 | 1087 |  | 16.92 |  |  | 1111 |  | 17.49 | 1136 |  | 18.07 | 1159 |  | 18.66 |  |  | 1183 |  | 19.25 |  |  | 1206 |  |  | 19.84 |  |  | 1229 |  | 20.44 |  |  | 1252 |  | 21.04 | 1274 |  | 21.64 | 1296 |  | 22.25
15000 | 1126 |  | 19.23 |  |  | 1149 |  | 19.83 | 1172 |  | 20.43 | 1195 |  | 21.03 |  |  | 1217 |  | 21.64 |  |  | 1239 |  |  | 22.25 |  |  | 1261 |  | 22.86 |  |  | 1283 |  | 23.48 | — |  | — | — |  | —
16000 | 1166 |  | 21.78 |  |  | 1188 |  | 22.4 | 1210 |  | 23.01 | 1232 |  | 23.64 |  |  | 1253 |  | 24.26 |  |  | 1275 |  |  | 24.89 |  |  | 1296 |  | 25.52 |  |  | — |  | — | — |  | — | — |  | —
17000 | 1208 |  | 24.56 |  |  | 1229 |  | 25.2 | 1250 |  | 25.84 | 1271 |  | 26.48 |  |  | 1291 |  | 27.12 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
18000 | 1250 |  | 27.59 |  |  | 1271 |  | 28.25 | 1291 |  | 28.91 | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
19000 | 1294 |  | 30.87 |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
20000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
48A2,A3,A6,A7060 (60 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
12000 | 476 |  | 4.33 |  |  | 534 |  | 5.04 | 585 |  | 5.78 | 632 |  | 6.56 |  |  | 674 |  | 7.39 |  |  | 714 |  |  | 8.24 |  |  | 751 |  | 9.12 |  |  | 786 |  | 10.02 | 819 |  | 10.93 | 851 |  | 11.85
14000 | 536 |  | 6.19 |  |  | 588 |  | 6.96 | 636 |  | 7.74 | 680 |  | 8.56 |  |  | 720 |  | 9.41 |  |  | 758 |  |  | 10.3 |  |  | 793 |  | 11.21 |  |  | 827 |  | 12.15 | 859 |  | 13.11 | 890 |  | 14.08
15000 | 566 |  | 7.28 |  |  | 617 |  | 8.09 | 662 |  | 8.9 | 704 |  | 9.73 |  |  | 744 |  | 10.59 |  |  | 781 |  |  | 11.5 |  |  | 816 |  | 12.42 |  |  | 849 |  | 13.38 | 881 |  | 14.36 | 911 |  | 15.35
16000 | 597 |  | 8.48 |  |  | 645 |  | 9.34 | 689 |  | 10.17 | 730 |  | 11.02 |  |  | 768 |  | 11.9 |  |  | 804 |  |  | 12.82 |  |  | 839 |  | 13.76 |  |  | 871 |  | 14.73 | 902 |  | 15.72 | 932 |  | 16.73
17000 | 628 |  | 9.8 |  |  | 674 |  | 10.71 | 717 |  | 11.58 | 756 |  | 12.45 |  |  | 793 |  | 13.34 |  |  | 829 |  |  | 14.27 |  |  | 862 |  | 15.23 |  |  | 894 |  | 16.21 | 925 |  | 17.21 | 954 |  | 18.24
18000 | 659 |  | 11.25 |  |  | 704 |  | 12.21 | 745 |  | 13.11 | 783 |  | 14 |  |  | 819 |  | 14.91 |  |  | 853 |  |  | 15.85 |  |  | 886 |  | 16.82 |  |  | 918 |  | 17.82 | 948 |  | 18.84 | 977 |  | 19.88
19000 | 691 |  | 12.82 |  |  | 734 |  | 13.84 | 773 |  | 14.77 | 810 |  | 15.69 |  |  | 845 |  | 16.62 |  |  | 879 |  |  | 17.58 |  |  | 911 |  | 18.56 |  |  | 942 |  | 19.57 | 971 |  | 20.6 | 1000 |  | 21.65
20000 | 723 |  | 14.53 |  |  | 764 |  | 15.6 | 802 |  | 16.57 | 838 |  | 17.52 |  |  | 872 |  | 18.47 |  |  | 905 |  |  | 19.44 |  |  | 936 |  | 20.44 |  |  | 966 |  | 21.45 | 995 |  | 22.5 | 1023 |  | 23.57
21000 | 755 |  | 16.37 |  |  | 794 |  | 17.49 | 831 |  | 18.51 | 866 |  | 19.49 |  |  | 899 |  | 20.47 |  |  | 931 |  |  | 21.46 |  |  | 961 |  | 22.47 |  |  | 991 |  | 23.5 | 1019 |  | 24.55 | 1047 |  | 25.63
22000 | 787 |  | 18.35 |  |  | 825 |  | 19.53 | 861 |  | 20.59 | 894 |  | 21.6 |  |  | 927 |  | 22.61 |  |  | 958 |  |  | 23.62 |  |  | 987 |  | 24.64 |  |  | 1016 |  | 25.69 | 1044 |  | 26.76 | 1071 |  | 27.84
23000 | 819 |  | 20.48 |  |  | 856 |  | 21.71 | 890 |  | 22.81 | 923 |  | 23.87 |  |  | 954 |  | 24.9 |  |  | 985 |  |  | 25.93 |  |  | 1014 |  | 26.97 |  |  | 1042 |  | 28.03 | 1069 |  | 29.11 | 1096 |  | 30.21
24000 | 851 |  | 22.75 |  |  | 887 |  | 24.04 | 920 |  | 25.19 | 952 |  | 26.28 |  |  | 983 |  | 27.34 |  |  | 1012 |  |  | 28.4 |  |  | 1041 |  | 29.46 |  |  | 1068 |  | 30.54 | 1095 |  | 31.63 | 1121 |  | 32.74
25000 | 883 |  | 25.17 |  |  | 918 |  | 26.52 | 951 |  | 27.72 | 982 |  | 28.84 |  |  | 1011 |  | 29.94 |  |  | 1040 |  |  | 31.02 |  |  | 1068 |  | 32.11 |  |  | 1095 |  | 33.21 | 1121 |  | 34.31 | 1147 |  | 35.44
26000 | 916 |  | 27.76 |  |  | 950 |  | 29.15 | 981 |  | 30.4 | 1011 |  | 31.57 |  |  | 1040 |  | 32.7 |  |  | 1068 |  |  | 33.81 |  |  | 1095 |  | 34.92 |  |  | 1122 |  | 36.04 | 1147 |  | 37.16 | 1172 |  | 38.3
27000 | 948 |  | 30.49 |  |  | 981 |  | 31.95 | 1012 |  | 33.24 | 1041 |  | 34.46 |  |  | 1070 |  | 35.62 |  |  | 1097 |  |  | 36.76 |  |  | 1123 |  | 37.9 |  |  | 1149 |  | 39.04 | 1174 |  | 40.18 | 1199 |  | 41.34
48A2,A3,A6,A7060 (60 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
12000 | 881 |  | 12.78 |  |  | 911 |  | 13.72 | 939 |  | 14.67 | 967 |  | 15.62 |  |  | 993 |  | 16.58 |  |  | 1019 |  |  | 17.54 |  |  | 1045 |  | 18.51 |  |  | 1069 |  | 19.48 | 1093 |  | 20.45 | 1117 |  | 21.43
14000 | 920 |  | 15.06 |  |  | 948 |  | 16.06 | 976 |  | 17.07 | 1003 |  | 18.08 |  |  | 1029 |  | 19.11 |  |  | 1054 |  |  | 20.13 |  |  | 1079 |  | 21.17 |  |  | 1103 |  | 22.21 | 1126 |  | 23.26 | 1149 |  | 24.31
15000 | 940 |  | 16.36 |  |  | 968 |  | 17.38 | 996 |  | 18.41 | 1022 |  | 19.45 |  |  | 1048 |  | 20.5 |  |  | 1073 |  |  | 21.56 |  |  | 1097 |  | 22.63 |  |  | 1121 |  | 23.7 | 1144 |  | 24.78 | 1167 |  | 25.86
16000 | 961 |  | 17.76 |  |  | 989 |  | 18.8 | 1016 |  | 19.86 | 1042 |  | 20.92 |  |  | 1067 |  | 22 |  |  | 1092 |  |  | 23.08 |  |  | 1116 |  | 24.17 |  |  | 1140 |  | 25.28 | 1162 |  | 26.38 | 1185 |  | 27.49
17000 | 983 |  | 19.28 |  |  | 1010 |  | 20.34 | 1036 |  | 21.42 | 1062 |  | 22.51 |  |  | 1087 |  | 23.6 |  |  | 1112 |  |  | 24.71 |  |  | 1135 |  | 25.83 |  |  | 1159 |  | 26.95 | 1181 |  | 28.09 | — |  | —
18000 | 1005 |  | 20.94 |  |  | 1032 |  | 22.01 | 1058 |  | 23.11 | 1083 |  | 24.21 |  |  | 1108 |  | 25.33 |  |  | 1132 |  |  | 26.46 |  |  | 1156 |  | 27.6 |  |  | 1178 |  | 28.74 | — |  | — | — |  | —
19000 | 1027 |  | 22.72 |  |  | 1054 |  | 23.81 | 1080 |  | 24.92 | 1105 |  | 26.04 |  |  | 1129 |  | 27.18 |  |  | 1153 |  |  | 28.33 |  |  | 1176 |  | 29.48 |  |  | 1199 |  | 30.65 | — |  | — | — |  | —
20000 | 1050 |  | 24.65 |  |  | 1076 |  | 25.76 | 1102 |  | 26.88 | 1126 |  | 28.01 |  |  | 1151 |  | 29.17 |  |  | 1174 |  |  | 30.33 |  |  | 1197 |  | 31.5 |  |  | — |  | — | — |  | — | — |  | —
21000 | 1073 |  | 26.73 |  |  | 1099 |  | 27.84 | 1124 |  | 28.97 | 1149 |  | 30.13 |  |  | 1173 |  | 31.29 |  |  | 1196 |  |  | 32.47 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
22000 | 1097 |  | 28.95 |  |  | 1123 |  | 30.08 | 1147 |  | 31.22 | 1172 |  | 32.39 |  |  | 1195 |  | 33.56 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
23000 | 1122 |  | 31.33 |  |  | 1147 |  | 32.47 | 1171 |  | 33.63 | 1195 |  | 34.8 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
24000 | 1146 |  | 33.87 |  |  | 1171 |  | 35.02 | 1195 |  | 36.19 | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
25000 | 1171 |  | 36.58 |  |  | 1196 |  | 37.74 | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
26000 | 1197 |  | 39.46 |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
27000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet
[18 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
50A2,A3,A6,A7 020 (20 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
4000 | 311 |  | 0.54 |  |  | 390 |  | 0.71 | 457 |  | 0.88 | 515 |  | 1.05 |  |  | 567 |  | 1.21 |  |  | 613 |  |  | 1.38 |  |  | 656 |  | 1.55 |  |  | 696 |  | 1.71 | 733 |  | 1.88 | 768 |  | 2.04
5000 | 347 |  | 0.84 |  |  | 417 |  | 1.02 | 480 |  | 1.21 | 536 |  | 1.4 |  |  | 587 |  | 1.59 |  |  | 633 |  |  | 1.78 |  |  | 676 |  | 1.97 |  |  | 716 |  | 2.16 | 753 |  | 2.34 | 788 |  | 2.52
6000 | 387 |  | 1.25 |  |  | 450 |  | 1.43 | 507 |  | 1.63 | 560 |  | 1.84 |  |  | 609 |  | 2.05 |  |  | 654 |  |  | 2.26 |  |  | 696 |  | 2.47 |  |  | 735 |  | 2.68 | 773 |  | 2.88 | 808 |  | 3.09
7000 | 430 |  | 1.77 |  |  | 488 |  | 1.96 | 540 |  | 2.17 | 588 |  | 2.38 |  |  | 634 |  | 2.61 |  |  | 677 |  |  | 2.83 |  |  | 718 |  | 3.06 |  |  | 756 |  | 3.29 | 793 |  | 3.51 | 828 |  | 3.74
7500 | 452 |  | 2.07 |  |  | 507 |  | 2.27 | 557 |  | 2.48 | 604 |  | 2.7 |  |  | 648 |  | 2.93 |  |  | 690 |  |  | 3.16 |  |  | 730 |  | 3.4 |  |  | 768 |  | 3.63 | 804 |  | 3.87 | 839 |  | 4.1
8000 | 474 |  | 2.41 |  |  | 528 |  | 2.61 | 576 |  | 2.82 | 620 |  | 3.04 |  |  | 663 |  | 3.28 |  |  | 704 |  |  | 3.52 |  |  | 743 |  | 3.76 |  |  | 780 |  | 4 | 816 |  | 4.24 | 850 |  | 4.48
9000 | 519 |  | 3.19 |  |  | 570 |  | 3.39 | 614 |  | 3.6 | 656 |  | 3.83 |  |  | 696 |  | 4.07 |  |  | 734 |  |  | 4.32 |  |  | 771 |  | 4.57 |  |  | 806 |  | 4.82 | 840 |  | 5.08 | 873 |  | 5.34
10000 | 565 |  | 4.1 |  |  | 613 |  | 4.31 | 655 |  | 4.53 | 694 |  | 4.76 |  |  | 731 |  | 5 |  |  | 767 |  |  | 5.26 |  |  | 802 |  | 5.51 |  |  | 835 |  | 5.78 | 868 |  | 6.04 | 900 |  | 6.31
50A2,A3,A6,A7 020 (20 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
4000 | 802 |  | 2.21 |  |  | 833 |  | 2.38 | 864 |  | 2.55 | 893 |  | 2.71 |  |  | 921 |  | 2.88 |  |  | 949 |  |  | 3.06 |  |  | 975 |  | 3.23 |  |  | 1001 |  | 3.4 | 1026 |  | 3.58 | 1050 |  | 3.75
5000 | 822 |  | 2.71 |  |  | 854 |  | 2.89 | 885 |  | 3.08 | 914 |  | 3.26 |  |  | 943 |  | 3.45 |  |  | 970 |  |  | 3.64 |  |  | 997 |  | 3.82 |  |  | 1023 |  | 4.01 | 1048 |  | 4.2 | 1072 |  | 4.39
6000 | 842 |  | 3.29 |  |  | 874 |  | 3.5 | 905 |  | 3.7 | 934 |  | 3.9 |  |  | 963 |  | 4.1 |  |  | 991 |  |  | 4.31 |  |  | 1017 |  | 4.51 |  |  | 1043 |  | 4.71 | 1069 |  | 4.91 | 1093 |  | 5.12
7000 | 862 |  | 3.96 |  |  | 894 |  | 4.19 | 924 |  | 4.41 | 954 |  | 4.63 |  |  | 983 |  | 4.85 |  |  | 1010 |  |  | 5.07 |  |  | 1037 |  | 5.29 |  |  | 1063 |  | 5.51 | 1089 |  | 5.72 | 1113 |  | 5.94
7500 | 872 |  | 4.33 |  |  | 904 |  | 4.56 | 934 |  | 4.79 | 964 |  | 5.02 |  |  | 993 |  | 5.25 |  |  | 1020 |  |  | 5.48 |  |  | 1047 |  | 5.71 |  |  | 1073 |  | 5.94 | 1099 |  | 6.16 | 1123 |  | 6.39
8000 | 883 |  | 4.73 |  |  | 914 |  | 4.97 | 945 |  | 5.21 | 974 |  | 5.45 |  |  | 1003 |  | 5.68 |  |  | 1030 |  |  | 5.92 |  |  | 1057 |  | 6.16 |  |  | 1083 |  | 6.39 | 1108 |  | 6.63 | 1133 |  | 6.87
9000 | 905 |  | 5.6 |  |  | 936 |  | 5.85 | 966 |  | 6.11 | 995 |  | 6.37 |  |  | 1023 |  | 6.62 |  |  | 1051 |  |  | 6.88 |  |  | 1077 |  | 7.13 |  |  | 1103 |  | 7.38 | 1129 |  | 7.64 | 1153 |  | 7.89
10000 | 931 |  | 6.58 |  |  | 961 |  | 6.85 | 990 |  | 7.13 | 1018 |  | 7.4 |  |  | 1046 |  | 7.67 |  |  | 1073 |  |  | 7.94 |  |  | 1099 |  | 8.21 |  |  | 1124 |  | 8.48 | 1149 |  | 8.75 | 1174 |  | 9.02
50A2,A3,A6,A7 025-030 (25 THRU 30 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
5000 | 352 |  | 0.85 |  |  | 422 |  | 1.03 | 484 |  | 1.22 | 540 |  | 1.42 |  |  | 590 |  | 1.61 |  |  | 636 |  |  | 1.79 |  |  | 678 |  | 1.98 |  |  | 718 |  | 2.17 | 755 |  | 2.35 | 791 |  | 2.54
6000 | 394 |  | 1.26 |  |  | 456 |  | 1.45 | 513 |  | 1.65 | 565 |  | 1.86 |  |  | 613 |  | 2.07 |  |  | 658 |  |  | 2.28 |  |  | 700 |  | 2.49 |  |  | 739 |  | 2.7 | 776 |  | 2.9 | 811 |  | 3.11
7000 | 438 |  | 1.79 |  |  | 495 |  | 1.98 | 546 |  | 2.19 | 594 |  | 2.41 |  |  | 640 |  | 2.64 |  |  | 682 |  |  | 2.86 |  |  | 723 |  | 3.09 |  |  | 761 |  | 3.32 | 798 |  | 3.54 | 833 |  | 3.77
8000 | 483 |  | 2.44 |  |  | 536 |  | 2.64 | 583 |  | 2.85 | 628 |  | 3.08 |  |  | 670 |  | 3.32 |  |  | 710 |  |  | 3.55 |  |  | 749 |  | 3.8 |  |  | 786 |  | 4.04 | 821 |  | 4.28 | 855 |  | 4.52
9000 | 530 |  | 3.23 |  |  | 579 |  | 3.43 | 623 |  | 3.65 | 664 |  | 3.88 |  |  | 704 |  | 4.12 |  |  | 741 |  |  | 4.37 |  |  | 778 |  | 4.62 |  |  | 813 |  | 4.88 | 847 |  | 5.13 | 880 |  | 5.39
10000 | 577 |  | 4.15 |  |  | 624 |  | 4.36 | 665 |  | 4.58 | 703 |  | 4.82 |  |  | 740 |  | 5.06 |  |  | 776 |  |  | 5.32 |  |  | 810 |  | 5.58 |  |  | 843 |  | 5.84 | 876 |  | 6.11 | 907 |  | 6.38
11000 | 625 |  | 5.22 |  |  | 669 |  | 5.44 | 708 |  | 5.67 | 744 |  | 5.91 |  |  | 779 |  | 6.16 |  |  | 813 |  |  | 6.41 |  |  | 845 |  | 6.68 |  |  | 877 |  | 6.95 | 907 |  | 7.22 | 937 |  | 7.5
12000 | 674 |  | 6.45 |  |  | 715 |  | 6.67 | 753 |  | 6.9 | 787 |  | 7.15 |  |  | 820 |  | 7.4 |  |  | 851 |  |  | 7.67 |  |  | 882 |  | 7.93 |  |  | 912 |  | 8.21 | 941 |  | 8.49 | 970 |  | 8.78
13000 | 722 |  | 7.85 |  |  | 762 |  | 8.07 | 798 |  | 8.3 | 831 |  | 8.55 |  |  | 862 |  | 8.81 |  |  | 892 |  |  | 9.08 |  |  | 921 |  | 9.35 |  |  | 950 |  | 9.63 | 977 |  | 9.92 | 1005 |  | 10.21
14000 | 771 |  | 9.41 |  |  | 810 |  | 9.64 | 844 |  | 9.88 | 875 |  | 10.13 |  |  | 905 |  | 10.39 |  |  | 934 |  |  | 10.66 |  |  | 962 |  | 10.94 |  |  | 989 |  | 11.22 | 1015 |  | 11.51 | 1041 |  | 11.81
15000 | 821 |  | 11.15 |  |  | 857 |  | 11.38 | 890 |  | 11.62 | 921 |  | 11.88 |  |  | 949 |  | 12.14 |  |  | 977 |  |  | 12.42 |  |  | 1004 |  | 12.7 |  |  | 1030 |  | 12.99 | 1055 |  | 13.28 | 1080 |  | 13.58
50A2,A3,A6,A7 025-030 (25 THRU 30 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
5000 | 824 |  | 2.72 |  |  | 856 |  | 2.91 | 887 |  | 3.09 | 916 |  | 3.28 |  |  | 945 |  | 3.46 |  |  | 972 |  |  | 3.65 |  |  | 999 |  | 3.83 |  |  | 1024 |  | 4.02 | 1049 |  | 4.21 | 1074 |  | 4.4
6000 | 845 |  | 3.31 |  |  | 877 |  | 3.52 | 908 |  | 3.72 | 937 |  | 3.92 |  |  | 966 |  | 4.12 |  |  | 993 |  |  | 4.32 |  |  | 1020 |  | 4.53 |  |  | 1046 |  | 4.73 | 1071 |  | 4.93 | 1096 |  | 5.14
7000 | 866 |  | 3.99 |  |  | 898 |  | 4.21 | 928 |  | 4.43 | 958 |  | 4.66 |  |  | 986 |  | 4.88 |  |  | 1014 |  |  | 5.1 |  |  | 1041 |  | 5.31 |  |  | 1067 |  | 5.53 | 1092 |  | 5.75 | 1116 |  | 5.97
8000 | 888 |  | 4.77 |  |  | 919 |  | 5.01 | 950 |  | 5.25 | 979 |  | 5.49 |  |  | 1007 |  | 5.72 |  |  | 1035 |  |  | 5.96 |  |  | 1061 |  | 6.2 |  |  | 1087 |  | 6.43 | 1113 |  | 6.67 | 1137 |  | 6.9
9000 | 912 |  | 5.65 |  |  | 942 |  | 5.9 | 972 |  | 6.16 | 1001 |  | 6.42 |  |  | 1029 |  | 6.67 |  |  | 1056 |  |  | 6.93 |  |  | 1083 |  | 7.18 |  |  | 1108 |  | 7.43 | 1134 |  | 7.69 | 1158 |  | 7.94
10000 | 938 |  | 6.65 |  |  | 968 |  | 6.92 | 997 |  | 7.19 | 1025 |  | 7.46 |  |  | 1052 |  | 7.73 |  |  | 1079 |  |  | 8 |  |  | 1105 |  | 8.27 |  |  | 1130 |  | 8.54 | 1155 |  | 8.81 | 1180 |  | 9.08
11000 | 967 |  | 7.78 |  |  | 995 |  | 8.07 | 1023 |  | 8.35 | 1051 |  | 8.63 |  |  | 1077 |  | 8.92 |  |  | 1103 |  |  | 9.2 |  |  | 1129 |  | 9.49 |  |  | 1154 |  | 9.77 | 1178 |  | 10.06 | — |  | —
12000 | 998 |  | 9.07 |  |  | 1025 |  | 9.35 | 1052 |  | 9.65 | 1078 |  | 9.94 |  |  | 1104 |  | 10.24 |  |  | 1130 |  |  | 10.54 |  |  | 1154 |  | 10.83 |  |  | 1179 |  | 11.13 | — |  | — | — |  | —
13000 | 1031 |  | 10.5 |  |  | 1058 |  | 10.8 | 1083 |  | 11.1 | 1109 |  | 11.4 |  |  | 1133 |  | 11.71 |  |  | 1158 |  |  | 12.01 |  |  | 1182 |  | 12.32 |  |  | — |  | — | — |  | — | — |  | —
14000 | 1067 |  | 12.1 |  |  | 1092 |  | 12.41 | 1117 |  | 12.71 | 1141 |  | 13.02 |  |  | 1165 |  | 13.33 |  |  | 1188 |  |  | 13.65 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
15000 | 1104 |  | 13.88 |  |  | 1128 |  | 14.19 | 1152 |  | 14.5 | 1175 |  | 14.81 |  |  | 1198 |  | 15.13 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet | [17 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
50A2,A3,A6,A7035 (35 TONS)
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
7000 | 503 |  | 1.96 |  |  | 553 |  | 2.22 | 601 |  | 2.47 | 646 |  | 2.72 |  |  | 689 |  | 2.97 |  |  | 730 |  |  | 3.22 |  |  | 768 |  | 3.46 |  |  | 804 |  | 3.7 | 839 |  | 3.94 | 872 |  | 4.17
8000 | 553 |  | 2.62 |  |  | 599 |  | 2.89 | 643 |  | 3.16 | 684 |  | 3.43 |  |  | 724 |  | 3.7 |  |  | 763 |  |  | 3.97 |  |  | 799 |  | 4.23 |  |  | 834 |  | 4.5 | 868 |  | 4.76 | 901 |  | 5.02
9000 | 605 |  | 3.39 |  |  | 647 |  | 3.68 | 687 |  | 3.97 | 726 |  | 4.26 |  |  | 763 |  | 4.55 |  |  | 798 |  |  | 4.83 |  |  | 833 |  | 5.12 |  |  | 867 |  | 5.4 | 899 |  | 5.68 | 930 |  | 5.96
10000 | 657 |  | 4.29 |  |  | 696 |  | 4.61 | 733 |  | 4.91 | 769 |  | 5.22 |  |  | 803 |  | 5.52 |  |  | 837 |  |  | 5.82 |  |  | 870 |  | 6.12 |  |  | 901 |  | 6.42 | 932 |  | 6.72 | 962 |  | 7.02
10500 | 684 |  | 4.8 |  |  | 721 |  | 5.12 | 757 |  | 5.43 | 791 |  | 5.75 |  |  | 825 |  | 6.06 |  |  | 857 |  |  | 6.37 |  |  | 889 |  | 6.68 |  |  | 920 |  | 6.98 | 950 |  | 7.29 | 979 |  | 7.6
11000 | 710 |  | 5.33 |  |  | 747 |  | 5.66 | 781 |  | 5.99 | 814 |  | 6.31 |  |  | 847 |  | 6.63 |  |  | 878 |  |  | 6.95 |  |  | 909 |  | 7.26 |  |  | 939 |  | 7.58 | 968 |  | 7.89 | 997 |  | 8.21
12000 | 764 |  | 6.52 |  |  | 798 |  | 6.86 | 830 |  | 7.21 | 861 |  | 7.54 |  |  | 891 |  | 7.88 |  |  | 921 |  |  | 8.21 |  |  | 950 |  | 8.54 |  |  | 978 |  | 8.87 | 1006 |  | 9.2 | 1033 |  | 9.53
13000 | 818 |  | 7.85 |  |  | 849 |  | 8.21 | 880 |  | 8.57 | 909 |  | 8.92 |  |  | 938 |  | 9.27 |  |  | 966 |  |  | 9.62 |  |  | 993 |  | 9.97 |  |  | 1020 |  | 10.31 | 1046 |  | 10.66 | 1072 |  | 11
14000 | 872 |  | 9.33 |  |  | 901 |  | 9.71 | 930 |  | 10.09 | 958 |  | 10.45 |  |  | 985 |  | 10.82 |  |  | 1012 |  |  | 11.19 |  |  | 1037 |  | 11.55 |  |  | 1063 |  | 11.91 | 1088 |  | 12.27 | 1113 |  | 12.63
15000 | 926 |  | 10.98 |  |  | 954 |  | 11.37 | 981 |  | 11.76 | 1008 |  | 12.15 |  |  | 1033 |  | 12.53 |  |  | 1059 |  |  | 12.91 |  |  | 1083 |  | 13.28 |  |  | 1108 |  | 13.66 | 1131 |  | 14.03 | 1155 |  | 14.4
16000 | 980 |  | 12.79 |  |  | 1007 |  | 13.2 | 1033 |  | 13.6 | 1058 |  | 14 |  |  | 1082 |  | 14.4 |  |  | 1106 |  |  | 14.79 |  |  | 1130 |  | 15.18 |  |  | 1153 |  | 15.57 | 1176 |  | 15.96 | 1199 |  | 16.35
17000 | 1035 |  | 14.77 |  |  | 1060 |  | 15.19 | 1085 |  | 15.61 | 1109 |  | 16.03 |  |  | 1132 |  | 16.44 |  |  | 1155 |  |  | 16.84 |  |  | 1178 |  | 17.25 |  |  | 1200 |  | 17.65 | 1222 |  | 18.05 | 1243 |  | 18.46
17500 | 1062 |  | 15.83 |  |  | 1087 |  | 16.25 | 1111 |  | 16.68 | 1134 |  | 17.1 |  |  | 1157 |  | 17.52 |  |  | 1180 |  |  | 17.94 |  |  | 1202 |  | 18.35 |  |  | 1224 |  | 18.76 | 1245 |  | 19.17 | 1266 |  | 19.58
50A2,A3,A6,A7035 (35 TONS) (cont)
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
7000 | 903 |  | 4.4 |  |  | 933 |  | 4.62 | 962 |  | 4.84 | 990 |  | 5.06 |  |  | 1017 |  | 5.27 |  |  | 1043 |  |  | 5.48 |  |  | 1068 |  | 5.69 |  |  | 1092 |  | 5.89 | 1116 |  | 6.09 | 1139 |  | 6.28
8000 | 932 |  | 5.27 |  |  | 962 |  | 5.52 | 991 |  | 5.77 | 1019 |  | 6.02 |  |  | 1045 |  | 6.26 |  |  | 1071 |  |  | 6.5 |  |  | 1097 |  | 6.73 |  |  | 1121 |  | 6.96 | 1145 |  | 7.19 | 1168 |  | 7.42
9000 | 961 |  | 6.24 |  |  | 990 |  | 6.52 | 1019 |  | 6.79 | 1047 |  | 7.06 |  |  | 1073 |  | 7.33 |  |  | 1099 |  |  | 7.59 |  |  | 1125 |  | 7.85 |  |  | 1149 |  | 8.11 | 1173 |  | 8.37 | 1196 |  | 8.62
10000 | 992 |  | 7.32 |  |  | 1020 |  | 7.62 | 1048 |  | 7.91 | 1075 |  | 8.2 |  |  | 1102 |  | 8.49 |  |  | 1127 |  |  | 8.78 |  |  | 1152 |  | 9.07 |  |  | 1177 |  | 9.35 | 1201 |  | 9.63 | 1224 |  | 9.91
10500 | 1008 |  | 7.9 |  |  | 1036 |  | 8.21 | 1063 |  | 8.51 | 1090 |  | 8.82 |  |  | 1116 |  | 9.12 |  |  | 1142 |  |  | 9.41 |  |  | 1166 |  | 9.71 |  |  | 1191 |  | 10.01 | 1214 |  | 10.3 | 1238 |  | 10.59
11000 | 1025 |  | 8.52 |  |  | 1052 |  | 8.84 | 1079 |  | 9.15 | 1105 |  | 9.46 |  |  | 1131 |  | 9.77 |  |  | 1156 |  |  | 10.08 |  |  | 1181 |  | 10.39 |  |  | 1205 |  | 10.69 | 1228 |  | 10.99 | 1252 |  | 11.29
12000 | 1060 |  | 9.86 |  |  | 1086 |  | 10.19 | 1112 |  | 10.52 | 1137 |  | 10.85 |  |  | 1162 |  | 11.17 |  |  | 1187 |  |  | 11.5 |  |  | 1211 |  | 11.82 |  |  | 1234 |  | 12.15 | 1257 |  | 12.47 | 1280 |  | 12.79
13000 | 1097 |  | 11.35 |  |  | 1122 |  | 11.69 | 1147 |  | 12.03 | 1171 |  | 12.37 |  |  | 1195 |  | 12.72 |  |  | 1219 |  |  | 13.06 |  |  | 1242 |  | 13.4 |  |  | 1265 |  | 13.74 | 1287 |  | 14.08 | — |  | —
14000 | 1137 |  | 12.98 |  |  | 1161 |  | 13.34 | 1184 |  | 13.69 | 1208 |  | 14.05 |  |  | 1231 |  | 14.41 |  |  | 1253 |  |  | 14.76 |  |  | 1276 |  | 15.12 |  |  | 1298 |  | 15.47 | — |  | — | — |  | —
15000 | 1178 |  | 14.77 |  |  | 1201 |  | 15.15 | 1223 |  | 15.51 | 1246 |  | 15.88 |  |  | 1268 |  | 16.25 |  |  | 1289 |  |  | 16.62 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
16000 | 1221 |  | 16.73 |  |  | 1243 |  | 17.11 | 1264 |  | 17.5 | 1286 |  | 17.88 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
17000 | 1265 |  | 18.85 |  |  | 1286 |  | 19.25 | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
17500 | 1287 |  | 19.98 |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
50A2,A3,A6,A7040 (40 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
8000 | 475 |  | 2.69 |  |  | 523 |  | 3.08 | 569 |  | 3.47 | 612 |  | 3.86 |  |  | 653 |  | 4.26 |  |  | 692 |  |  | 4.66 |  |  | 730 |  | 5.07 |  |  | 767 |  | 5.49 | 802 |  | 5.92 | 836 |  | 6.36
9000 | 521 |  | 3.53 |  |  | 565 |  | 3.94 | 606 |  | 4.36 | 646 |  | 4.78 |  |  | 684 |  | 5.2 |  |  | 721 |  |  | 5.63 |  |  | 757 |  | 6.06 |  |  | 791 |  | 6.49 | 825 |  | 6.94 | 857 |  | 7.39
10000 | 568 |  | 4.52 |  |  | 608 |  | 4.96 | 646 |  | 5.4 | 683 |  | 5.84 |  |  | 719 |  | 6.29 |  |  | 753 |  |  | 6.74 |  |  | 787 |  | 7.2 |  |  | 819 |  | 7.65 | 851 |  | 8.11 | 882 |  | 8.58
11000 | 615 |  | 5.68 |  |  | 652 |  | 6.14 | 687 |  | 6.6 | 722 |  | 7.07 |  |  | 755 |  | 7.55 |  |  | 788 |  |  | 8.02 |  |  | 819 |  | 8.5 |  |  | 850 |  | 8.97 | 880 |  | 9.46 | 909 |  | 9.94
12000 | 663 |  | 7.01 |  |  | 697 |  | 7.49 | 730 |  | 7.98 | 762 |  | 8.47 |  |  | 794 |  | 8.97 |  |  | 824 |  |  | 9.47 |  |  | 854 |  | 9.96 |  |  | 883 |  | 10.47 | 912 |  | 10.97 | 939 |  | 11.48
13000 | 712 |  | 8.53 |  |  | 743 |  | 9.03 | 774 |  | 9.54 | 804 |  | 10.05 |  |  | 834 |  | 10.57 |  |  | 862 |  |  | 11.09 |  |  | 891 |  | 11.61 |  |  | 918 |  | 12.13 | 945 |  | 12.66 | 972 |  | 13.19
14000 | 760 |  | 10.24 |  |  | 790 |  | 10.76 | 819 |  | 11.29 | 847 |  | 11.82 |  |  | 875 |  | 12.36 |  |  | 902 |  |  | 12.9 |  |  | 929 |  | 13.45 |  |  | 955 |  | 13.99 | 981 |  | 14.54 | 1006 |  | 15.09
15000 | 809 |  | 12.15 |  |  | 837 |  | 12.69 | 864 |  | 13.24 | 891 |  | 13.79 |  |  | 917 |  | 14.35 |  |  | 943 |  |  | 14.91 |  |  | 968 |  | 15.48 |  |  | 993 |  | 16.04 | 1018 |  | 16.62 | 1042 |  | 17.18
16000 | 859 |  | 14.27 |  |  | 885 |  | 14.83 | 910 |  | 15.4 | 936 |  | 15.97 |  |  | 960 |  | 16.55 |  |  | 985 |  |  | 17.13 |  |  | 1009 |  | 17.71 |  |  | 1033 |  | 18.3 | 1056 |  | 18.89 | 1079 |  | 19.48
17000 | 908 |  | 16.61 |  |  | 933 |  | 17.19 | 957 |  | 17.77 | 981 |  | 18.36 |  |  | 1004 |  | 18.96 |  |  | 1028 |  |  | 19.56 |  |  | 1051 |  | 20.16 |  |  | 1073 |  | 20.77 | 1096 |  | 21.38 | 1118 |  | 21.99
18000 | 958 |  | 19.18 |  |  | 981 |  | 19.77 | 1004 |  | 20.37 | 1027 |  | 20.98 |  |  | 1049 |  | 21.6 |  |  | 1071 |  |  | 22.22 |  |  | 1093 |  | 22.84 |  |  | 1115 |  | 23.46 | 1136 |  | 24.09 | 1157 |  | 24.72
19000 | 1007 |  | 21.98 |  |  | 1030 |  | 22.59 | 1052 |  | 23.21 | 1073 |  | 23.84 |  |  | 1095 |  | 24.47 |  |  | 1116 |  |  | 25.1 |  |  | 1137 |  | 25.74 |  |  | 1157 |  | 26.39 | 1178 |  | 27.04 | 1198 |  | 27.68
20000 | 1057 |  | 25.02 |  |  | 1079 |  | 25.65 | 1099 |  | 26.29 | 1120 |  | 26.93 |  |  | 1140 |  | 27.58 |  |  | 1161 |  |  | 28.23 |  |  | 1181 |  | 28.89 |  |  | — |  | — | — |  | — | — |  | —
50A2,A3,A6,A7040 (40 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
8000 | 870 |  | 6.81 |  |  | 902 |  | 7.26 | 933 |  | 7.73 | 964 |  | 8.2 |  |  | 993 |  | 8.67 |  |  | 1022 |  |  | 9.16 |  |  | 1050 |  | 9.65 |  |  | 1077 |  | 10.14 | 1104 |  | 10.64 | 1129 |  | 11.15
9000 | 889 |  | 7.85 |  |  | 920 |  | 8.31 | 950 |  | 8.79 | 979 |  | 9.27 |  |  | 1008 |  | 9.75 |  |  | 1036 |  |  | 10.25 |  |  | 1064 |  | 10.75 |  |  | 1090 |  | 11.26 | 1117 |  | 11.77 | 1142 |  | 12.29
10000 | 912 |  | 9.05 |  |  | 941 |  | 9.53 | 970 |  | 10.02 | 998 |  | 10.51 |  |  | 1026 |  | 11 |  |  | 1053 |  |  | 11.51 |  |  | 1080 |  | 12.02 |  |  | 1106 |  | 12.54 | 1131 |  | 13.06 | 1157 |  | 13.59
11000 | 938 |  | 10.43 |  |  | 966 |  | 10.92 | 993 |  | 11.42 | 1020 |  | 11.93 |  |  | 1047 |  | 12.44 |  |  | 1073 |  |  | 12.95 |  |  | 1099 |  | 13.47 |  |  | 1124 |  | 14 | 1149 |  | 14.53 | 1173 |  | 15.07
12000 | 967 |  | 11.98 |  |  | 993 |  | 12.49 | 1020 |  | 13.01 | 1046 |  | 13.53 |  |  | 1071 |  | 14.05 |  |  | 1096 |  |  | 14.58 |  |  | 1121 |  | 15.11 |  |  | 1145 |  | 15.65 | 1169 |  | 16.19 | 1192 |  | 16.74
13000 | 998 |  | 13.72 |  |  | 1023 |  | 14.25 | 1049 |  | 14.78 | 1073 |  | 15.32 |  |  | 1098 |  | 15.86 |  |  | 1121 |  |  | 16.4 |  |  | 1145 |  | 16.95 |  |  | 1168 |  | 17.5 | 1191 |  | 18.06 | 1214 |  | 18.62
14000 | 1031 |  | 15.64 |  |  | 1055 |  | 16.19 | 1079 |  | 16.75 | 1103 |  | 17.3 |  |  | 1126 |  | 17.86 |  |  | 1149 |  |  | 18.42 |  |  | 1172 |  | 18.98 |  |  | 1195 |  | 19.55 | 1217 |  | 20.12 | 1239 |  | 20.69
15000 | 1066 |  | 17.76 |  |  | 1089 |  | 18.33 | 1112 |  | 18.9 | 1135 |  | 19.48 |  |  | 1157 |  | 20.06 |  |  | 1179 |  |  | 20.63 |  |  | 1201 |  | 21.21 |  |  | 1223 |  | 21.8 | 1244 |  | 22.38 | 1265 |  | 22.97
16000 | 1102 |  | 20.08 |  |  | 1124 |  | 20.67 | 1147 |  | 21.26 | 1168 |  | 21.86 |  |  | 1190 |  | 22.46 |  |  | 1211 |  |  | 23.06 |  |  | 1232 |  | 23.66 |  |  | 1253 |  | 24.26 | 1274 |  | 24.86 | 1294 |  | 25.46
17000 | 1140 |  | 22.61 |  |  | 1161 |  | 23.22 | 1182 |  | 23.84 | 1203 |  | 24.45 |  |  | 1224 |  | 25.07 |  |  | 1245 |  |  | 25.69 |  |  | 1265 |  | 26.31 |  |  | 1285 |  | 26.93 | — |  | — | — |  | —
18000 | 1178 |  | 25.36 |  |  | 1199 |  | 25.99 | 1219 |  | 26.63 | 1240 |  | 27.26 |  |  | 1260 |  | 27.9 |  |  | 1279 |  |  | 28.54 |  |  | 1299 |  | 29.18 |  |  | — |  | — | — |  | — | — |  | —
19000 | 1218 |  | 28.34 |  |  | 1238 |  | 28.99 | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
20000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet | [17 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
50A2,A3,A6,A7050 (50 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
10000 | 577 |  | 4.62 |  |  | 617 |  | 5.06 | 655 |  | 5.5 | 692 |  | 5.95 |  |  | 727 |  | 6.4 |  |  | 761 |  |  | 6.85 |  |  | 794 |  | 7.3 |  |  | 827 |  | 7.76 | 858 |  | 8.22 | 889 |  | 8.69
11000 | 625 |  | 5.8 |  |  | 661 |  | 6.26 | 697 |  | 6.73 | 731 |  | 7.2 |  |  | 764 |  | 7.67 |  |  | 796 |  |  | 8.14 |  |  | 827 |  | 8.62 |  |  | 858 |  | 9.1 | 888 |  | 9.58 | 917 |  | 10.07
12000 | 673 |  | 7.15 |  |  | 707 |  | 7.63 | 740 |  | 8.12 | 772 |  | 8.62 |  |  | 803 |  | 9.11 |  |  | 833 |  |  | 9.61 |  |  | 863 |  | 10.11 |  |  | 891 |  | 10.61 | 920 |  | 11.12 | 947 |  | 11.62
13000 | 722 |  | 8.69 |  |  | 753 |  | 9.19 | 784 |  | 9.7 | 814 |  | 10.22 |  |  | 843 |  | 10.74 |  |  | 872 |  |  | 11.26 |  |  | 900 |  | 11.78 |  |  | 927 |  | 12.31 | 954 |  | 12.83 | 980 |  | 13.36
14000 | 771 |  | 10.43 |  |  | 800 |  | 10.95 | 829 |  | 11.48 | 857 |  | 12.01 |  |  | 885 |  | 12.55 |  |  | 912 |  |  | 13.1 |  |  | 938 |  | 13.64 |  |  | 964 |  | 14.19 | 990 |  | 14.74 | 1015 |  | 15.29
15000 | 821 |  | 12.37 |  |  | 848 |  | 12.91 | 875 |  | 13.46 | 901 |  | 14.01 |  |  | 928 |  | 14.57 |  |  | 953 |  |  | 15.14 |  |  | 978 |  | 15.7 |  |  | 1003 |  | 16.27 | 1028 |  | 16.84 | 1052 |  | 17.41
16000 | 870 |  | 14.52 |  |  | 896 |  | 15.08 | 922 |  | 15.65 | 947 |  | 16.22 |  |  | 971 |  | 16.8 |  |  | 996 |  |  | 17.39 |  |  | 1020 |  | 17.97 |  |  | 1043 |  | 18.56 | 1066 |  | 19.15 | 1089 |  | 19.75
17000 | 920 |  | 16.89 |  |  | 945 |  | 17.48 | 969 |  | 18.06 | 993 |  | 18.65 |  |  | 1016 |  | 19.25 |  |  | 1039 |  |  | 19.86 |  |  | 1062 |  | 20.46 |  |  | 1084 |  | 21.07 | 1107 |  | 21.68 | 1129 |  | 22.3
18000 | 971 |  | 19.5 |  |  | 994 |  | 20.1 | 1017 |  | 20.71 | 1039 |  | 21.32 |  |  | 1061 |  | 21.93 |  |  | 1083 |  |  | 22.55 |  |  | 1105 |  | 23.18 |  |  | 1126 |  | 23.8 | 1148 |  | 24.44 | 1169 |  | 25.07
19000 | 1021 |  | 22.35 |  |  | 1043 |  | 22.96 | 1065 |  | 23.59 | 1086 |  | 24.21 |  |  | 1107 |  | 24.85 |  |  | 1128 |  |  | 25.49 |  |  | 1149 |  | 26.13 |  |  | 1170 |  | 26.78 | 1190 |  | 27.42 | 1210 |  | 28.08
20000 | 1071 |  | 25.43 |  |  | 1092 |  | 26.07 | 1113 |  | 26.71 | 1133 |  | 27.36 |  |  | 1154 |  | 28.01 |  |  | 1174 |  |  | 28.66 |  |  | 1194 |  | 29.33 |  |  | 1213 |  | 29.99 | 1233 |  | 30.65 | 1252 |  | 31.33
50A2,A3,A6,A7050 (50 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
10000 | 919 |  | 9.17 |  |  | 948 |  | 9.64 | 977 |  | 10.13 | 1005 |  | 10.62 |  |  | 1032 |  | 11.12 |  |  | 1059 |  |  | 11.63 |  |  | 1086 |  | 12.14 |  |  | 1112 |  | 12.66 | 1137 |  | 13.18 | 1162 |  | 13.71
11000 | 945 |  | 10.56 |  |  | 973 |  | 11.05 | 1001 |  | 11.55 | 1027 |  | 12.06 |  |  | 1054 |  | 12.57 |  |  | 1080 |  |  | 13.09 |  |  | 1105 |  | 13.61 |  |  | 1130 |  | 14.14 | 1155 |  | 14.67 | 1179 |  | 15.21
12000 | 975 |  | 12.13 |  |  | 1001 |  | 12.64 | 1027 |  | 13.16 | 1053 |  | 13.68 |  |  | 1078 |  | 14.21 |  |  | 1103 |  |  | 14.74 |  |  | 1128 |  | 15.27 |  |  | 1152 |  | 15.81 | 1176 |  | 16.35 | 1199 |  | 16.9
13000 | 1006 |  | 13.89 |  |  | 1032 |  | 14.42 | 1057 |  | 14.96 | 1081 |  | 15.49 |  |  | 1105 |  | 16.03 |  |  | 1129 |  |  | 16.58 |  |  | 1153 |  | 17.12 |  |  | 1176 |  | 17.68 | 1199 |  | 18.23 | 1221 |  | 18.8
14000 | 1040 |  | 15.84 |  |  | 1064 |  | 16.39 | 1088 |  | 16.94 | 1112 |  | 17.5 |  |  | 1135 |  | 18.06 |  |  | 1158 |  |  | 18.62 |  |  | 1180 |  | 19.18 |  |  | 1203 |  | 19.75 | 1225 |  | 20.32 | 1246 |  | 20.9
15000 | 1075 |  | 17.99 |  |  | 1098 |  | 18.56 | 1121 |  | 19.13 | 1144 |  | 19.71 |  |  | 1166 |  | 20.29 |  |  | 1188 |  |  | 20.86 |  |  | 1210 |  | 21.45 |  |  | 1231 |  | 22.03 | 1253 |  | 22.62 | 1274 |  | 23.21
16000 | 1112 |  | 20.34 |  |  | 1134 |  | 20.93 | 1156 |  | 21.53 | 1178 |  | 22.12 |  |  | 1199 |  | 22.72 |  |  | 1221 |  |  | 23.32 |  |  | 1241 |  | 23.92 |  |  | 1262 |  | 24.52 | 1283 |  | 25.13 | — |  | —
17000 | 1150 |  | 22.91 |  |  | 1172 |  | 23.52 | 1193 |  | 24.14 | 1214 |  | 24.76 |  |  | 1234 |  | 25.37 |  |  | 1255 |  |  | 25.99 |  |  | 1275 |  | 26.61 |  |  | 1295 |  | 27.23 | — |  | — | — |  | —
18000 | 1190 |  | 25.7 |  |  | 1210 |  | 26.34 | 1230 |  | 26.97 | 1250 |  | 27.61 |  |  | 1270 |  | 28.25 |  |  | 1290 |  |  | 28.89 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
19000 | 1230 |  | 28.73 |  |  | 1250 |  | 29.38 | 1269 |  | 30.04 | 1289 |  | 30.7 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
20000 | 1271 |  | 31.99 |  |  | 1290 |  | 32.67 | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
50A2,A3,A6,A7060 (60 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
12000 | 450 |  | 4.02 |  |  | 509 |  | 4.71 | 560 |  | 5.41 | 605 |  | 6.12 |  |  | 647 |  | 6.86 |  |  | 686 |  |  | 7.62 |  |  | 723 |  | 8.4 |  |  | 757 |  | 9.21 | 790 |  | 10.04 | 821 |  | 10.89
14000 | 505 |  | 5.74 |  |  | 558 |  | 6.49 | 606 |  | 7.24 | 649 |  | 8.01 |  |  | 689 |  | 8.79 |  |  | 727 |  |  | 9.59 |  |  | 762 |  | 10.4 |  |  | 795 |  | 11.24 | 827 |  | 12.09 | 857 |  | 12.96
15000 | 533 |  | 6.75 |  |  | 584 |  | 7.53 | 630 |  | 8.32 | 672 |  | 9.11 |  |  | 711 |  | 9.91 |  |  | 748 |  |  | 10.73 |  |  | 782 |  | 11.56 |  |  | 815 |  | 12.41 | 846 |  | 13.28 | 876 |  | 14.17
16000 | 561 |  | 7.88 |  |  | 610 |  | 8.68 | 655 |  | 9.5 | 696 |  | 10.32 |  |  | 734 |  | 11.14 |  |  | 770 |  |  | 11.98 |  |  | 803 |  | 12.84 |  |  | 836 |  | 13.71 | 866 |  | 14.59 | 896 |  | 15.49
17000 | 590 |  | 9.12 |  |  | 637 |  | 9.95 | 680 |  | 10.79 | 720 |  | 11.64 |  |  | 757 |  | 12.49 |  |  | 792 |  |  | 13.35 |  |  | 825 |  | 14.23 |  |  | 857 |  | 15.12 | 887 |  | 16.02 | 916 |  | 16.94
18000 | 619 |  | 10.48 |  |  | 664 |  | 11.33 | 706 |  | 12.2 | 744 |  | 13.07 |  |  | 781 |  | 13.96 |  |  | 815 |  |  | 14.84 |  |  | 847 |  | 15.74 |  |  | 878 |  | 16.65 | 908 |  | 17.57 | 937 |  | 18.5
19000 | 648 |  | 11.96 |  |  | 692 |  | 12.84 | 732 |  | 13.74 | 769 |  | 14.64 |  |  | 805 |  | 15.54 |  |  | 838 |  |  | 16.45 |  |  | 870 |  | 17.37 |  |  | 900 |  | 18.3 | 930 |  | 19.24 | 958 |  | 20.19
20000 | 678 |  | 13.57 |  |  | 719 |  | 14.47 | 758 |  | 15.4 | 795 |  | 16.32 |  |  | 829 |  | 17.25 |  |  | 862 |  |  | 18.19 |  |  | 893 |  | 19.13 |  |  | 923 |  | 20.08 | 952 |  | 21.04 | 979 |  | 22.01
21000 | 707 |  | 15.3 |  |  | 748 |  | 16.24 | 785 |  | 17.19 | 821 |  | 18.14 |  |  | 854 |  | 19.09 |  |  | 886 |  |  | 20.05 |  |  | 917 |  | 21.02 |  |  | 946 |  | 22 | 974 |  | 22.98 | 1001 |  | 23.97
22000 | 737 |  | 17.18 |  |  | 776 |  | 18.14 | 812 |  | 19.11 | 847 |  | 20.09 |  |  | 879 |  | 21.07 |  |  | 911 |  |  | 22.06 |  |  | 940 |  | 23.05 |  |  | 969 |  | 24.04 | 997 |  | 25.05 | 1024 |  | 26.06
23000 | 767 |  | 19.2 |  |  | 804 |  | 20.18 | 840 |  | 21.17 | 873 |  | 22.17 |  |  | 905 |  | 23.18 |  |  | 935 |  |  | 24.19 |  |  | 965 |  | 25.21 |  |  | 993 |  | 26.23 | 1020 |  | 27.25 | 1046 |  | 28.28
24000 | 797 |  | 21.35 |  |  | 833 |  | 22.36 | 867 |  | 23.38 | 900 |  | 24.4 |  |  | 931 |  | 25.43 |  |  | 961 |  |  | 26.47 |  |  | 989 |  | 27.51 |  |  | 1017 |  | 28.55 | 1044 |  | 29.6 | 1070 |  | 30.65
25000 | 827 |  | 23.66 |  |  | 862 |  | 24.68 | 895 |  | 25.72 | 927 |  | 26.78 |  |  | 957 |  | 27.83 |  |  | 986 |  |  | 28.89 |  |  | 1014 |  | 29.95 |  |  | 1041 |  | 31.02 | 1068 |  | 32.09 | 1093 |  | 33.17
26000 | 857 |  | 26.11 |  |  | 891 |  | 27.16 | 923 |  | 28.23 | 954 |  | 29.3 |  |  | 984 |  | 30.38 |  |  | 1012 |  |  | 31.46 |  |  | 1040 |  | 32.55 |  |  | 1066 |  | 33.64 | 1092 |  | 34.73 | 1117 |  | 35.83
27000 | 888 |  | 28.72 |  |  | 920 |  | 29.79 | 952 |  | 30.88 | 982 |  | 31.97 |  |  | 1011 |  | 33.08 |  |  | 1038 |  |  | 34.19 |  |  | 1065 |  | 35.29 |  |  | 1091 |  | 36.4 | 1117 |  | 37.52 | 1141 |  | 38.64
50A2,A3,A6,A7060 (60 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
12000 | 851 |  | 11.75 |  |  | 880 |  | 12.63 | 907 |  | 13.53 | 934 |  | 14.45 |  |  | 960 |  | 15.38 |  |  | 985 |  |  | 16.32 |  |  | 1010 |  | 17.28 |  |  | 1033 |  | 18.24 | 1057 |  | 19.22 | 1079 |  | 20.22
14000 | 886 |  | 13.85 |  |  | 915 |  | 14.76 | 942 |  | 15.68 | 968 |  | 16.62 |  |  | 993 |  | 17.57 |  |  | 1018 |  |  | 18.54 |  |  | 1042 |  | 19.52 |  |  | 1066 |  | 20.51 | 1088 |  | 21.52 | 1111 |  | 22.53
15000 | 905 |  | 15.07 |  |  | 933 |  | 15.99 | 960 |  | 16.92 | 986 |  | 17.87 |  |  | 1011 |  | 18.83 |  |  | 1035 |  |  | 19.81 |  |  | 1059 |  | 20.81 |  |  | 1082 |  | 21.81 | 1105 |  | 22.82 | 1127 |  | 23.85
16000 | 924 |  | 16.41 |  |  | 952 |  | 17.34 | 978 |  | 18.28 | 1004 |  | 19.25 |  |  | 1029 |  | 20.22 |  |  | 1053 |  |  | 21.21 |  |  | 1077 |  | 22.21 |  |  | 1100 |  | 23.22 | 1122 |  | 24.25 | 1144 |  | 25.29
17000 | 944 |  | 17.86 |  |  | 971 |  | 18.81 | 997 |  | 19.77 | 1023 |  | 20.74 |  |  | 1047 |  | 21.73 |  |  | 1071 |  |  | 22.73 |  |  | 1095 |  | 23.74 |  |  | 1117 |  | 24.76 | 1140 |  | 25.8 | 1161 |  | 26.85
18000 | 964 |  | 19.45 |  |  | 991 |  | 20.41 | 1017 |  | 21.38 | 1042 |  | 22.36 |  |  | 1066 |  | 23.36 |  |  | 1090 |  |  | 24.37 |  |  | 1113 |  | 25.4 |  |  | 1136 |  | 26.43 | 1158 |  | 27.48 | 1179 |  | 28.54
19000 | 985 |  | 21.15 |  |  | 1011 |  | 22.13 | 1037 |  | 23.12 | 1061 |  | 24.11 |  |  | 1085 |  | 25.13 |  |  | 1109 |  |  | 26.15 |  |  | 1132 |  | 27.19 |  |  | 1154 |  | 28.24 | 1176 |  | 29.29 | 1197 |  | 30.36
20000 | 1006 |  | 22.99 |  |  | 1032 |  | 23.98 | 1057 |  | 24.99 | 1081 |  | 26 |  |  | 1105 |  | 27.03 |  |  | 1128 |  |  | 28.06 |  |  | 1151 |  | 29.11 |  |  | 1173 |  | 30.17 | 1195 |  | 31.24 | — |  | —
21000 | 1028 |  | 24.97 |  |  | 1053 |  | 25.97 | 1078 |  | 26.99 | 1102 |  | 28.02 |  |  | 1126 |  | 29.06 |  |  | 1148 |  |  | 30.11 |  |  | 1171 |  | 31.17 |  |  | 1193 |  | 32.25 | — |  | — | — |  | —
22000 | 1050 |  | 27.08 |  |  | 1075 |  | 28.1 | 1099 |  | 29.14 | 1123 |  | 30.18 |  |  | 1146 |  | 31.24 |  |  | 1169 |  |  | 32.3 |  |  | 1191 |  | 33.38 |  |  | — |  | — | — |  | — | — |  | —
23000 | 1072 |  | 29.32 |  |  | 1097 |  | 30.37 | 1121 |  | 31.42 | 1144 |  | 32.48 |  |  | 1167 |  | 33.55 |  |  | 1190 |  |  | 34.64 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
24000 | 1095 |  | 31.71 |  |  | 1119 |  | 32.78 | 1143 |  | 33.85 | 1166 |  | 34.93 |  |  | 1189 |  | 36.02 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
25000 | 1118 |  | 34.25 |  |  | 1142 |  | 35.33 | 1165 |  | 36.42 | 1188 |  | 37.52 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
26000 | 1141 |  | 36.93 |  |  | 1165 |  | 38.04 | 1188 |  | 39.15 | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
27000 | 1165 |  | 39.76 |  |  | 1188 |  | 40.89 | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet
[18 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
Fan Performance — Horizontal Discharge Units
48A4,A5,A8,A9 020 (20 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
4000 | 339 |  | 0.71 |  |  | 414 |  | 0.97 | 478 |  | 1.25 | 534 |  | 1.54 |  |  | 585 |  | 1.84 |  |  | 631 |  |  | 2.14 |  |  | 674 |  | 2.44 |  |  | 714 |  | 2.75 | 751 |  | 3.06 | 787 |  | 3.37
5000 | 384 |  | 1.1 |  |  | 452 |  | 1.37 | 510 |  | 1.66 | 563 |  | 1.96 |  |  | 611 |  | 2.28 |  |  | 656 |  |  | 2.6 |  |  | 698 |  | 2.93 |  |  | 738 |  | 3.27 | 775 |  | 3.6 | 811 |  | 3.94
6000 | 433 |  | 1.61 |  |  | 494 |  | 1.89 | 548 |  | 2.19 | 597 |  | 2.51 |  |  | 643 |  | 2.84 |  |  | 686 |  |  | 3.18 |  |  | 726 |  | 3.52 |  |  | 764 |  | 3.88 | 800 |  | 4.23 | 835 |  | 4.6
7000 | 484 |  | 2.27 |  |  | 540 |  | 2.56 | 590 |  | 2.87 | 636 |  | 3.19 |  |  | 679 |  | 3.53 |  |  | 719 |  |  | 3.88 |  |  | 757 |  | 4.24 |  |  | 794 |  | 4.61 | 829 |  | 4.98 | 863 |  | 5.36
7500 | 511 |  | 2.66 |  |  | 563 |  | 2.95 | 612 |  | 3.26 | 656 |  | 3.59 |  |  | 698 |  | 3.94 |  |  | 737 |  |  | 4.29 |  |  | 775 |  | 4.66 |  |  | 810 |  | 5.03 | 845 |  | 5.41 | 877 |  | 5.79
8000 | 538 |  | 3.09 |  |  | 588 |  | 3.38 | 634 |  | 3.7 | 678 |  | 4.03 |  |  | 718 |  | 4.38 |  |  | 756 |  |  | 4.74 |  |  | 793 |  | 5.11 |  |  | 827 |  | 5.49 | 861 |  | 5.87 | 893 |  | 6.26
9000 | 593 |  | 4.07 |  |  | 639 |  | 4.37 | 682 |  | 4.69 | 722 |  | 5.03 |  |  | 760 |  | 5.39 |  |  | 796 |  |  | 5.76 |  |  | 831 |  | 6.13 |  |  | 864 |  | 6.52 | 896 |  | 6.91 | 927 |  | 7.32
10000 | 649 |  | 5.23 |  |  | 691 |  | 5.54 | 731 |  | 5.87 | 769 |  | 6.21 |  |  | 805 |  | 6.58 |  |  | 839 |  |  | 6.95 |  |  | 872 |  | 7.34 |  |  | 904 |  | 7.73 | 934 |  | 8.13 | 964 |  | 8.54
48A4,A5,A8,A9 020 (20 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
4000 | 820 |  | 3.68 |  |  | 852 |  | 3.99 | 883 |  | 4.3 | 912 |  | 4.62 |  |  | 940 |  | 4.93 |  |  | 967 |  |  | 5.25 |  |  | 993 |  | 5.57 |  |  | 1019 |  | 5.89 | 1043 |  | 6.21 | 1067 |  | 6.53
5000 | 844 |  | 4.28 |  |  | 877 |  | 4.63 | 907 |  | 4.97 | 937 |  | 5.31 |  |  | 966 |  | 5.66 |  |  | 993 |  |  | 6.01 |  |  | 1020 |  | 6.35 |  |  | 1046 |  | 6.7 | 1071 |  | 7.05 | 1095 |  | 7.4
6000 | 869 |  | 4.96 |  |  | 901 |  | 5.33 | 931 |  | 5.7 | 961 |  | 6.07 |  |  | 990 |  | 6.44 |  |  | 1017 |  |  | 6.81 |  |  | 1044 |  | 7.19 |  |  | 1070 |  | 7.57 | 1096 |  | 7.94 | 1121 |  | 8.32
7000 | 895 |  | 5.74 |  |  | 926 |  | 6.13 | 956 |  | 6.52 | 986 |  | 6.91 |  |  | 1014 |  | 7.3 |  |  | 1042 |  |  | 7.7 |  |  | 1068 |  | 8.1 |  |  | 1094 |  | 8.5 | 1120 |  | 8.9 | 1145 |  | 9.3
7500 | 909 |  | 6.18 |  |  | 940 |  | 6.57 | 970 |  | 6.97 | 999 |  | 7.37 |  |  | 1027 |  | 7.78 |  |  | 1054 |  |  | 8.18 |  |  | 1081 |  | 8.59 |  |  | 1107 |  | 9 | 1132 |  | 9.41 | 1157 |  | 9.82
8000 | 925 |  | 6.66 |  |  | 955 |  | 7.06 | 984 |  | 7.46 | 1013 |  | 7.87 |  |  | 1040 |  | 8.28 |  |  | 1067 |  |  | 8.69 |  |  | 1094 |  | 9.11 |  |  | 1119 |  | 9.53 | 1144 |  | 9.95 | 1169 |  | 10.37
9000 | 957 |  | 7.72 |  |  | 986 |  | 8.13 | 1015 |  | 8.55 | 1042 |  | 8.97 |  |  | 1069 |  | 9.39 |  |  | 1096 |  |  | 9.82 |  |  | 1121 |  | 10.25 |  |  | 1146 |  | 10.69 | 1171 |  | 11.12 | 1195 |  | 11.56
10000 | 993 |  | 8.96 |  |  | 1021 |  | 9.38 | 1048 |  | 9.8 | 1075 |  | 10.23 |  |  | 1101 |  | 10.67 |  |  | 1126 |  |  | 11.11 |  |  | 1151 |  | 11.55 |  |  | 1176 |  | 12 | 1200 |  | 12.45 | — |  | —
48A4,A5,A8,A9 025-030 (25 THRU 30 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
5000 | 389 |  | 1.11 |  |  | 456 |  | 1.38 | 514 |  | 1.68 | 566 |  | 1.98 |  |  | 614 |  | 2.3 |  |  | 659 |  |  | 2.62 |  |  | 701 |  | 2.95 |  |  | 740 |  | 3.29 | 777 |  | 3.62 | 813 |  | 3.96
6000 | 439 |  | 1.64 |  |  | 499 |  | 1.92 | 553 |  | 2.22 | 602 |  | 2.54 |  |  | 647 |  | 2.87 |  |  | 689 |  |  | 3.21 |  |  | 730 |  | 3.56 |  |  | 768 |  | 3.91 | 804 |  | 4.27 | 838 |  | 4.63
7000 | 492 |  | 2.31 |  |  | 546 |  | 2.6 | 596 |  | 2.91 | 641 |  | 3.24 |  |  | 684 |  | 3.58 |  |  | 724 |  |  | 3.93 |  |  | 762 |  | 4.29 |  |  | 798 |  | 4.66 | 833 |  | 5.03 | 867 |  | 5.41
8000 | 546 |  | 3.14 |  |  | 596 |  | 3.43 | 642 |  | 3.75 | 684 |  | 4.09 |  |  | 724 |  | 4.44 |  |  | 762 |  |  | 4.8 |  |  | 798 |  | 5.17 |  |  | 833 |  | 5.55 | 866 |  | 5.93 | 898 |  | 6.32
9000 | 602 |  | 4.13 |  |  | 647 |  | 4.43 | 690 |  | 4.76 | 730 |  | 5.1 |  |  | 768 |  | 5.46 |  |  | 803 |  |  | 5.83 |  |  | 838 |  | 6.21 |  |  | 871 |  | 6.6 | 903 |  | 7 | 933 |  | 7.4
10000 | 659 |  | 5.31 |  |  | 701 |  | 5.62 | 740 |  | 5.95 | 777 |  | 6.3 |  |  | 813 |  | 6.67 |  |  | 847 |  |  | 7.04 |  |  | 880 |  | 7.43 |  |  | 911 |  | 7.83 | 942 |  | 8.23 | 971 |  | 8.64
11000 | 717 |  | 6.67 |  |  | 755 |  | 6.99 | 792 |  | 7.33 | 827 |  | 7.68 |  |  | 860 |  | 8.06 |  |  | 893 |  |  | 8.44 |  |  | 924 |  | 8.83 |  |  | 954 |  | 9.24 | 983 |  | 9.65 | 1011 |  | 10.07
12000 | 775 |  | 8.23 |  |  | 811 |  | 8.56 | 845 |  | 8.9 | 878 |  | 9.27 |  |  | 909 |  | 9.64 |  |  | 940 |  |  | 10.03 |  |  | 970 |  | 10.43 |  |  | 999 |  | 10.84 | 1026 |  | 11.26 | 1054 |  | 11.69
13000 | 834 |  | 9.99 |  |  | 867 |  | 10.33 | 899 |  | 10.68 | 930 |  | 11.05 |  |  | 960 |  | 11.44 |  |  | 989 |  |  | 11.83 |  |  | 1017 |  | 12.24 |  |  | 1045 |  | 12.65 | 1072 |  | 13.08 | 1098 |  | 13.51
14000 | 893 |  | 11.97 |  |  | 924 |  | 12.32 | 954 |  | 12.68 | 983 |  | 13.06 |  |  | 1012 |  | 13.44 |  |  | 1039 |  |  | 13.85 |  |  | 1066 |  | 14.26 |  |  | 1093 |  | 14.68 | 1118 |  | 15.11 | 1143 |  | 15.54
15000 | 953 |  | 14.17 |  |  | 982 |  | 14.53 | 1010 |  | 14.9 | 1037 |  | 15.28 |  |  | 1064 |  | 15.68 |  |  | 1091 |  |  | 16.08 |  |  | 1116 |  | 16.5 |  |  | 1142 |  | 16.93 | 1166 |  | 17.36 | 1190 |  | 17.8
48A4,A5,A8,A9 025-030 (25 THRU 30 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
5000 | 846 |  | 4.31 |  |  | 879 |  | 4.65 | 909 |  | 4.99 | 939 |  | 5.34 |  |  | 968 |  | 5.68 |  |  | 995 |  |  | 6.03 |  |  | 1022 |  | 6.38 |  |  | 1048 |  | 6.73 | 1073 |  | 7.08 | 1097 |  | 7.43
6000 | 872 |  | 5 |  |  | 903 |  | 5.36 | 934 |  | 5.73 | 964 |  | 6.1 |  |  | 992 |  | 6.48 |  |  | 1020 |  |  | 6.85 |  |  | 1047 |  | 7.22 |  |  | 1073 |  | 7.6 | 1098 |  | 7.98 | 1123 |  | 8.36
7000 | 899 |  | 5.79 |  |  | 930 |  | 6.18 | 960 |  | 6.57 | 989 |  | 6.96 |  |  | 1018 |  | 7.36 |  |  | 1045 |  |  | 7.75 |  |  | 1072 |  | 8.15 |  |  | 1098 |  | 8.55 | 1123 |  | 8.95 | 1148 |  | 9.35
8000 | 930 |  | 6.72 |  |  | 960 |  | 7.12 | 989 |  | 7.53 | 1017 |  | 7.94 |  |  | 1045 |  | 8.35 |  |  | 1072 |  |  | 8.76 |  |  | 1098 |  | 9.18 |  |  | 1124 |  | 9.6 | 1148 |  | 10.02 | 1173 |  | 10.44
9000 | 963 |  | 7.8 |  |  | 992 |  | 8.22 | 1020 |  | 8.63 | 1048 |  | 9.06 |  |  | 1075 |  | 9.48 |  |  | 1101 |  |  | 9.91 |  |  | 1126 |  | 10.34 |  |  | 1151 |  | 10.78 | 1176 |  | 11.21 | 1200 |  | 11.65
10000 | 1000 |  | 9.06 |  |  | 1028 |  | 9.48 | 1055 |  | 9.91 | 1081 |  | 10.34 |  |  | 1107 |  | 10.77 |  |  | 1133 |  |  | 11.22 |  |  | 1157 |  | 11.66 |  |  | 1182 |  | 12.11 | — |  | — | — |  | —
11000 | 1039 |  | 10.49 |  |  | 1066 |  | 10.92 | 1092 |  | 11.36 | 1117 |  | 11.8 |  |  | 1142 |  | 12.24 |  |  | 1167 |  |  | 12.69 |  |  | 1191 |  | 13.15 |  |  | — |  | — | — |  | — | — |  | —
12000 | 1080 |  | 12.12 |  |  | 1106 |  | 12.56 | 1131 |  | 13 | 1156 |  | 13.45 |  |  | 1180 |  | 13.9 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
13000 | 1123 |  | 13.95 |  |  | 1148 |  | 14.39 | 1172 |  | 14.84 | 1196 |  | 15.3 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
14000 | 1168 |  | 15.99 |  |  | 1192 |  | 16.44 | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
15000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet
[18 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
48A4,A5,A8,A9 035 (35 TONS)
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
7000 | 553 |  | 2.59 |  |  | 602 |  | 2.92 | 648 |  | 3.26 | 691 |  | 3.61 |  |  | 732 |  | 3.95 |  |  | 770 |  |  | 4.29 |  |  | 807 |  | 4.63 |  |  | 842 |  | 4.96 | 875 |  | 5.29 | 907 |  | 5.62
8000 | 612 |  | 3.45 |  |  | 656 |  | 3.81 | 698 |  | 4.17 | 738 |  | 4.53 |  |  | 776 |  | 4.9 |  |  | 812 |  |  | 5.27 |  |  | 847 |  | 5.63 |  |  | 881 |  | 6 | 913 |  | 6.36 | 944 |  | 6.72
9000 | 672 |  | 4.47 |  |  | 712 |  | 4.86 | 750 |  | 5.24 | 787 |  | 5.62 |  |  | 823 |  | 6.01 |  |  | 857 |  |  | 6.39 |  |  | 890 |  | 6.78 |  |  | 922 |  | 7.17 | 953 |  | 7.56 | 983 |  | 7.95
10000 | 733 |  | 5.67 |  |  | 769 |  | 6.08 | 805 |  | 6.48 | 839 |  | 6.88 |  |  | 872 |  | 7.28 |  |  | 904 |  |  | 7.69 |  |  | 935 |  | 8.1 |  |  | 966 |  | 8.51 | 995 |  | 8.92 | 1024 |  | 9.33
10500 | 763 |  | 6.33 |  |  | 798 |  | 6.75 | 832 |  | 7.17 | 865 |  | 7.58 |  |  | 897 |  | 7.99 |  |  | 929 |  |  | 8.4 |  |  | 959 |  | 8.82 |  |  | 989 |  | 9.24 | 1017 |  | 9.66 | 1046 |  | 10.08
11000 | 794 |  | 7.04 |  |  | 828 |  | 7.47 | 861 |  | 7.9 | 892 |  | 8.32 |  |  | 923 |  | 8.74 |  |  | 954 |  |  | 9.16 |  |  | 983 |  | 9.59 |  |  | 1012 |  | 10.01 | 1040 |  | 10.44 | 1067 |  | 10.87
12000 | 855 |  | 8.6 |  |  | 887 |  | 9.06 | 918 |  | 9.51 | 948 |  | 9.95 |  |  | 977 |  | 10.39 |  |  | 1005 |  |  | 10.83 |  |  | 1033 |  | 11.27 |  |  | 1060 |  | 11.71 | 1087 |  | 12.16 | 1113 |  | 12.6
13000 | 917 |  | 10.36 |  |  | 947 |  | 10.84 | 976 |  | 11.31 | 1004 |  | 11.77 |  |  | 1031 |  | 12.23 |  |  | 1058 |  |  | 12.69 |  |  | 1084 |  | 13.14 |  |  | 1110 |  | 13.6 | 1135 |  | 14.06 | 1160 |  | 14.52
14000 | 980 |  | 12.32 |  |  | 1008 |  | 12.82 | 1035 |  | 13.31 | 1061 |  | 13.79 |  |  | 1087 |  | 14.27 |  |  | 1112 |  |  | 14.75 |  |  | 1137 |  | 15.22 |  |  | 1161 |  | 15.7 | 1185 |  | 16.17 | 1209 |  | 16.65
15000 | 1042 |  | 14.49 |  |  | 1069 |  | 15.01 | 1094 |  | 15.52 | 1119 |  | 16.03 |  |  | 1143 |  | 16.53 |  |  | 1167 |  |  | 17.02 |  |  | 1191 |  | 17.51 |  |  | 1214 |  | 18.01 | 1237 |  | 18.5 | 1260 |  | 18.99
16000 | 1105 |  | 16.88 |  |  | 1130 |  | 17.42 | 1154 |  | 17.96 | 1178 |  | 18.48 |  |  | 1201 |  | 19 |  |  | 1224 |  |  | 19.51 |  |  | 1246 |  | 20.02 |  |  | 1268 |  | 20.53 | 1290 |  | 21.04 | — |  | —
17000 | 1168 |  | 19.49 |  |  | 1191 |  | 20.06 | 1214 |  | 20.61 | 1237 |  | 21.16 |  |  | 1259 |  | 21.69 |  |  | 1281 |  |  | 22.23 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
17500 | 1200 |  | 20.88 |  |  | 1222 |  | 21.46 | 1245 |  | 22.03 | 1267 |  | 22.58 |  |  | 1288 |  | 23.13 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
48A4,A5,A8,A9 035 (35 TONS) (cont)
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
7000 | 937 |  | 5.94 |  |  | 967 |  | 6.26 | 995 |  | 6.57 | 1022 |  | 6.87 |  |  | 1048 |  | 7.18 |  |  | 1073 |  |  | 7.48 |  |  | 1098 |  | 7.78 |  |  | 1122 |  | 8.07 | 1145 |  | 8.36 | 1168 |  | 8.66
8000 | 974 |  | 7.08 |  |  | 1003 |  | 7.43 | 1031 |  | 7.77 | 1058 |  | 8.12 |  |  | 1084 |  | 8.46 |  |  | 1109 |  |  | 8.79 |  |  | 1134 |  | 9.13 |  |  | 1158 |  | 9.46 | 1181 |  | 9.78 | 1204 |  | 10.11
9000 | 1012 |  | 8.33 |  |  | 1041 |  | 8.72 | 1068 |  | 9.1 | 1094 |  | 9.47 |  |  | 1120 |  | 9.85 |  |  | 1145 |  |  | 10.22 |  |  | 1169 |  | 10.58 |  |  | 1193 |  | 10.95 | 1216 |  | 11.31 | 1239 |  | 11.66
10000 | 1052 |  | 9.74 |  |  | 1080 |  | 10.15 | 1106 |  | 10.55 | 1132 |  | 10.96 |  |  | 1157 |  | 11.36 |  |  | 1182 |  |  | 11.76 |  |  | 1206 |  | 12.16 |  |  | 1229 |  | 12.55 | 1252 |  | 12.95 | 1275 |  | 13.34
10500 | 1073 |  | 10.5 |  |  | 1100 |  | 10.92 | 1126 |  | 11.34 | 1151 |  | 11.75 |  |  | 1176 |  | 12.17 |  |  | 1201 |  |  | 12.59 |  |  | 1224 |  | 13 |  |  | 1248 |  | 13.41 | 1271 |  | 13.82 | 1293 |  | 14.22
11000 | 1094 |  | 11.3 |  |  | 1120 |  | 11.73 | 1146 |  | 12.16 | 1171 |  | 12.59 |  |  | 1196 |  | 13.02 |  |  | 1220 |  |  | 13.45 |  |  | 1243 |  | 13.87 |  |  | 1266 |  | 14.3 | 1289 |  | 14.72 | — |  | —
12000 | 1138 |  | 13.05 |  |  | 1163 |  | 13.5 | 1188 |  | 13.95 | 1212 |  | 14.4 |  |  | 1236 |  | 14.84 |  |  | 1259 |  |  | 15.3 |  |  | 1282 |  | 15.74 |  |  | — |  | — | — |  | — | — |  | —
13000 | 1184 |  | 14.99 |  |  | 1208 |  | 15.45 | 1232 |  | 15.92 | 1255 |  | 16.39 |  |  | 1278 |  | 16.85 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
14000 | 1232 |  | 17.13 |  |  | 1255 |  | 17.61 | 1278 |  | 18.09 | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
15000 | 1282 |  | 19.48 |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
16000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
17000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
17500 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
48A4,A5,A8,A9 040 (40 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
8000 | 526 |  | 3.1 |  |  | 573 |  | 3.5 | 617 |  | 3.91 | 660 |  | 4.33 |  |  | 700 |  | 4.75 |  |  | 740 |  |  | 5.18 |  |  | 778 |  | 5.62 |  |  | 814 |  | 6.07 | 850 |  | 6.53 | 884 |  | 7
9000 | 579 |  | 4.08 |  |  | 621 |  | 4.51 | 662 |  | 4.95 | 701 |  | 5.39 |  |  | 738 |  | 5.83 |  |  | 775 |  |  | 6.28 |  |  | 810 |  | 6.74 |  |  | 845 |  | 7.21 | 878 |  | 7.69 | 911 |  | 8.17
10000 | 633 |  | 5.24 |  |  | 671 |  | 5.7 | 709 |  | 6.16 | 744 |  | 6.62 |  |  | 779 |  | 7.09 |  |  | 813 |  |  | 7.57 |  |  | 846 |  | 8.05 |  |  | 879 |  | 8.53 | 910 |  | 9.03 | 941 |  | 9.53
11000 | 687 |  | 6.59 |  |  | 723 |  | 7.07 | 757 |  | 7.56 | 790 |  | 8.05 |  |  | 823 |  | 8.54 |  |  | 854 |  |  | 9.04 |  |  | 885 |  | 9.54 |  |  | 916 |  | 10.05 | 945 |  | 10.56 | 974 |  | 11.08
12000 | 742 |  | 8.15 |  |  | 775 |  | 8.65 | 807 |  | 9.17 | 838 |  | 9.68 |  |  | 868 |  | 10.2 |  |  | 898 |  |  | 10.72 |  |  | 927 |  | 11.24 |  |  | 955 |  | 11.77 | 983 |  | 12.3 | 1011 |  | 12.84
13000 | 797 |  | 9.92 |  |  | 827 |  | 10.45 | 857 |  | 10.98 | 887 |  | 11.52 |  |  | 915 |  | 12.07 |  |  | 943 |  |  | 12.61 |  |  | 970 |  | 13.15 |  |  | 997 |  | 13.7 | 1024 |  | 14.25 | 1050 |  | 14.81
14000 | 852 |  | 11.92 |  |  | 881 |  | 12.47 | 909 |  | 13.03 | 936 |  | 13.59 |  |  | 963 |  | 14.15 |  |  | 990 |  |  | 14.72 |  |  | 1016 |  | 15.29 |  |  | 1041 |  | 15.86 | 1066 |  | 16.43 | 1091 |  | 17.01
15000 | 908 |  | 14.15 |  |  | 935 |  | 14.72 | 961 |  | 15.31 | 987 |  | 15.89 |  |  | 1013 |  | 16.48 |  |  | 1038 |  |  | 17.06 |  |  | 1062 |  | 17.65 |  |  | 1086 |  | 18.25 | 1110 |  | 18.84 | 1134 |  | 19.44
16000 | 964 |  | 16.63 |  |  | 989 |  | 17.23 | 1014 |  | 17.83 | 1039 |  | 18.43 |  |  | 1063 |  | 19.04 |  |  | 1086 |  |  | 19.65 |  |  | 1110 |  | 20.26 |  |  | 1133 |  | 20.88 | 1156 |  | 21.49 | 1178 |  | 22.11
17000 | 1021 |  | 19.37 |  |  | 1044 |  | 19.98 | 1068 |  | 20.6 | 1091 |  | 21.23 |  |  | 1114 |  | 21.86 |  |  | 1136 |  |  | 22.49 |  |  | 1158 |  | 23.12 |  |  | 1180 |  | 23.76 | 1202 |  | 24.39 | 1223 |  | 25.03
18000 | 1077 |  | 22.37 |  |  | 1099 |  | 23.01 | 1122 |  | 23.64 | 1144 |  | 24.29 |  |  | 1165 |  | 24.94 |  |  | 1187 |  |  | 25.59 |  |  | 1208 |  | 26.25 |  |  | 1229 |  | 26.9 | 1250 |  | 27.56 | 1270 |  | 28.22
19000 | 1133 |  | 25.65 |  |  | 1155 |  | 26.3 | 1176 |  | 26.96 | 1197 |  | 27.62 |  |  | 1217 |  | 28.29 |  |  | 1238 |  |  | 28.96 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
20000 | 1190 |  | 29.21 |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
48A4,A5,A8,A9 040 (40 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
8000 | 917 |  | 7.48 |  |  | 949 |  | 7.96 | 980 |  | 8.44 | 1010 |  | 8.94 |  |  | 1039 |  | 9.43 |  |  | 1067 |  |  | 9.93 |  |  | 1094 |  | 10.44 |  |  | 1121 |  | 10.95 | 1147 |  | 11.46 | 1172 |  | 11.98
9000 | 942 |  | 8.66 |  |  | 973 |  | 9.16 | 1003 |  | 9.66 | 1033 |  | 10.17 |  |  | 1061 |  | 10.69 |  |  | 1089 |  |  | 11.21 |  |  | 1116 |  | 11.73 |  |  | 1142 |  | 12.26 | 1168 |  | 12.8 | 1193 |  | 13.33
10000 | 971 |  | 10.03 |  |  | 1001 |  | 10.55 | 1030 |  | 11.06 | 1058 |  | 11.59 |  |  | 1086 |  | 12.12 |  |  | 1113 |  |  | 12.66 |  |  | 1139 |  | 13.2 |  |  | 1165 |  | 13.75 | 1190 |  | 14.3 | 1215 |  | 14.86
11000 | 1003 |  | 11.6 |  |  | 1031 |  | 12.13 | 1059 |  | 12.67 | 1086 |  | 13.21 |  |  | 1112 |  | 13.75 |  |  | 1139 |  |  | 14.31 |  |  | 1164 |  | 14.86 |  |  | 1189 |  | 15.43 | 1214 |  | 15.99 | 1238 |  | 16.56
12000 | 1038 |  | 13.38 |  |  | 1065 |  | 13.92 | 1091 |  | 14.47 | 1117 |  | 15.03 |  |  | 1142 |  | 15.59 |  |  | 1167 |  |  | 16.16 |  |  | 1192 |  | 16.73 |  |  | 1216 |  | 17.31 | 1240 |  | 17.89 | 1264 |  | 18.48
13000 | 1075 |  | 15.37 |  |  | 1101 |  | 15.93 | 1126 |  | 16.5 | 1150 |  | 17.07 |  |  | 1175 |  | 17.65 |  |  | 1199 |  |  | 18.23 |  |  | 1222 |  | 18.82 |  |  | 1246 |  | 19.41 | 1269 |  | 20 | 1291 |  | 20.61
14000 | 1115 |  | 17.59 |  |  | 1139 |  | 18.17 | 1163 |  | 18.75 | 1186 |  | 19.34 |  |  | 1210 |  | 19.94 |  |  | 1232 |  |  | 20.53 |  |  | 1255 |  | 21.14 |  |  | 1277 |  | 21.74 | 1300 |  | 22.35 | — |  | —
15000 | 1157 |  | 20.04 |  |  | 1180 |  | 20.64 | 1202 |  | 21.24 | 1225 |  | 21.85 |  |  | 1247 |  | 22.46 |  |  | 1269 |  |  | 23.07 |  |  | 1290 |  | 23.69 |  |  | — |  | — | — |  | — | — |  | —
16000 | 1200 |  | 22.73 |  |  | 1222 |  | 23.35 | 1243 |  | 23.97 | 1265 |  | 24.6 |  |  | 1286 |  | 25.23 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
17000 | 1245 |  | 25.67 |  |  | 1266 |  | 26.32 | 1286 |  | 26.96 | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
18000 | 1290 |  | 28.88 |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
19000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
20000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet
[18 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
48A4,A5,A8,A9 050 (50 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
10000 | 642 |  | 5.35 |  |  | 680 |  | 5.8 | 717 |  | 6.27 | 753 |  | 6.73 |  |  | 787 |  | 7.2 |  |  | 821 |  |  | 7.68 |  |  | 854 |  | 8.16 |  |  | 886 |  | 8.65 | 917 |  | 9.14 | 948 |  | 9.65
11000 | 696 |  | 6.72 |  |  | 732 |  | 7.2 | 766 |  | 7.69 | 799 |  | 8.18 |  |  | 831 |  | 8.67 |  |  | 863 |  |  | 9.17 |  |  | 893 |  | 9.68 |  |  | 923 |  | 10.18 | 953 |  | 10.7 | 982 |  | 11.21
12000 | 751 |  | 8.29 |  |  | 784 |  | 8.8 | 816 |  | 9.32 | 847 |  | 9.83 |  |  | 877 |  | 10.35 |  |  | 906 |  |  | 10.87 |  |  | 935 |  | 11.4 |  |  | 964 |  | 11.92 | 991 |  | 12.46 | 1019 |  | 12.99
13000 | 807 |  | 10.09 |  |  | 837 |  | 10.62 | 867 |  | 11.16 | 896 |  | 11.7 |  |  | 924 |  | 12.24 |  |  | 952 |  |  | 12.78 |  |  | 979 |  | 13.33 |  |  | 1006 |  | 13.88 | 1032 |  | 14.43 | 1058 |  | 14.99
14000 | 863 |  | 12.12 |  |  | 891 |  | 12.67 | 919 |  | 13.23 | 946 |  | 13.79 |  |  | 973 |  | 14.36 |  |  | 999 |  |  | 14.92 |  |  | 1025 |  | 15.49 |  |  | 1050 |  | 16.06 | 1075 |  | 16.64 | 1100 |  | 17.21
15000 | 919 |  | 14.38 |  |  | 946 |  | 14.96 | 972 |  | 15.54 | 997 |  | 16.12 |  |  | 1023 |  | 16.71 |  |  | 1047 |  |  | 17.3 |  |  | 1072 |  | 17.89 |  |  | 1096 |  | 18.48 | 1120 |  | 19.08 | 1143 |  | 19.68
16000 | 975 |  | 16.9 |  |  | 1000 |  | 17.49 | 1025 |  | 18.09 | 1049 |  | 18.7 |  |  | 1073 |  | 19.31 |  |  | 1097 |  |  | 19.92 |  |  | 1120 |  | 20.53 |  |  | 1143 |  | 21.15 | 1165 |  | 21.76 | 1188 |  | 22.38
17000 | 1032 |  | 19.67 |  |  | 1056 |  | 20.29 | 1079 |  | 20.91 | 1102 |  | 21.54 |  |  | 1125 |  | 22.17 |  |  | 1147 |  |  | 22.8 |  |  | 1169 |  | 23.44 |  |  | 1191 |  | 24.07 | 1213 |  | 24.71 | 1234 |  | 25.35
18000 | 1089 |  | 22.71 |  |  | 1111 |  | 23.35 | 1134 |  | 23.99 | 1155 |  | 24.64 |  |  | 1177 |  | 25.29 |  |  | 1198 |  |  | 25.95 |  |  | 1219 |  | 26.6 |  |  | 1240 |  | 27.26 | 1261 |  | 27.92 | 1281 |  | 28.58
19000 | 1146 |  | 26.04 |  |  | 1167 |  | 26.69 | 1188 |  | 27.35 | 1209 |  | 28.02 |  |  | 1230 |  | 28.69 |  |  | 1250 |  |  | 29.37 |  |  | 1270 |  | 30.04 |  |  | 1290 |  | 30.72 | — |  | — | — |  | —
20000 | 1203 |  | 29.65 |  |  | 1224 |  | 30.32 | 1244 |  | 31 | 1263 |  | 31.69 |  |  | 1283 |  | 32.38 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
48A4,A5,A8,A9 050 (50 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
10000 | 978 |  | 10.15 |  |  | 1008 |  | 10.67 | 1036 |  | 11.19 | 1064 |  | 11.72 |  |  | 1092 |  | 12.25 |  |  | 1119 |  |  | 12.79 |  |  | 1145 |  | 13.33 |  |  | 1171 |  | 13.88 | 1196 |  | 14.43 | 1221 |  | 14.99
11000 | 1010 |  | 11.74 |  |  | 1038 |  | 12.27 | 1066 |  | 12.81 | 1093 |  | 13.35 |  |  | 1119 |  | 13.9 |  |  | 1145 |  |  | 14.45 |  |  | 1171 |  | 15.01 |  |  | 1196 |  | 15.57 | 1220 |  | 16.14 | 1245 |  | 16.72
12000 | 1046 |  | 13.53 |  |  | 1072 |  | 14.08 | 1098 |  | 14.63 | 1124 |  | 15.19 |  |  | 1149 |  | 15.76 |  |  | 1174 |  |  | 16.32 |  |  | 1199 |  | 16.9 |  |  | 1223 |  | 17.48 | 1247 |  | 18.06 | 1270 |  | 18.65
13000 | 1084 |  | 15.55 |  |  | 1109 |  | 16.11 | 1134 |  | 16.68 | 1158 |  | 17.26 |  |  | 1182 |  | 17.84 |  |  | 1206 |  |  | 18.42 |  |  | 1230 |  | 19.01 |  |  | 1253 |  | 19.6 | 1276 |  | 20.2 | 1299 |  | 20.8
14000 | 1124 |  | 17.79 |  |  | 1148 |  | 18.38 | 1171 |  | 18.97 | 1195 |  | 19.55 |  |  | 1218 |  | 20.15 |  |  | 1241 |  |  | 20.75 |  |  | 1263 |  | 21.35 |  |  | 1285 |  | 21.96 | — |  | — | — |  | —
15000 | 1166 |  | 20.27 |  |  | 1189 |  | 20.88 | 1211 |  | 21.49 | 1234 |  | 22.09 |  |  | 1256 |  | 22.71 |  |  | 1277 |  |  | 23.32 |  |  | 1299 |  | 23.94 |  |  | — |  | — | — |  | — | — |  | —
16000 | 1210 |  | 23 |  |  | 1231 |  | 23.62 | 1253 |  | 24.25 | 1274 |  | 24.88 |  |  | 1295 |  | 25.51 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
17000 | 1255 |  | 25.99 |  |  | 1276 |  | 26.63 | 1296 |  | 27.27 | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
18000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
19000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
20000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
48A4,A5,A8,A9 060 (60 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
12000 | 516 |  | 4.81 |  |  | 569 |  | 5.54 | 617 |  | 6.3 | 660 |  | 7.1 |  |  | 701 |  | 7.93 |  |  | 739 |  |  | 8.79 |  |  | 774 |  | 9.68 |  |  | 808 |  | 10.59 | 841 |  | 11.52 | 872 |  | 12.46
14000 | 584 |  | 6.9 |  |  | 632 |  | 7.69 | 676 |  | 8.5 | 716 |  | 9.33 |  |  | 754 |  | 10.2 |  |  | 790 |  |  | 11.1 |  |  | 824 |  | 12.02 |  |  | 857 |  | 12.97 | 888 |  | 13.94 | 917 |  | 14.92
15000 | 619 |  | 8.13 |  |  | 664 |  | 8.96 | 706 |  | 9.79 | 745 |  | 10.65 |  |  | 782 |  | 11.53 |  |  | 817 |  |  | 12.44 |  |  | 850 |  | 13.38 |  |  | 882 |  | 14.35 | 912 |  | 15.33 | 941 |  | 16.34
16000 | 654 |  | 9.49 |  |  | 697 |  | 10.36 | 737 |  | 11.22 | 775 |  | 12.1 |  |  | 811 |  | 13 |  |  | 845 |  |  | 13.93 |  |  | 877 |  | 14.88 |  |  | 908 |  | 15.86 | 938 |  | 16.86 | 966 |  | 17.88
17000 | 689 |  | 10.99 |  |  | 730 |  | 11.9 | 769 |  | 12.79 | 806 |  | 13.69 |  |  | 840 |  | 14.61 |  |  | 873 |  |  | 15.56 |  |  | 904 |  | 16.53 |  |  | 935 |  | 17.52 | 964 |  | 18.54 | 992 |  | 19.58
18000 | 725 |  | 12.64 |  |  | 764 |  | 13.58 | 801 |  | 14.51 | 837 |  | 15.43 |  |  | 870 |  | 16.38 |  |  | 902 |  |  | 17.34 |  |  | 933 |  | 18.32 |  |  | 962 |  | 19.33 | 990 |  | 20.36 | 1018 |  | 21.41
19000 | 760 |  | 14.43 |  |  | 798 |  | 15.41 | 834 |  | 16.37 | 868 |  | 17.32 |  |  | 900 |  | 18.29 |  |  | 932 |  |  | 19.27 |  |  | 961 |  | 20.27 |  |  | 990 |  | 21.29 | 1018 |  | 22.34 | 1045 |  | 23.4
20000 | 796 |  | 16.37 |  |  | 833 |  | 17.39 | 867 |  | 18.39 | 900 |  | 19.37 |  |  | 931 |  | 20.36 |  |  | 962 |  |  | 21.36 |  |  | 991 |  | 22.38 |  |  | 1019 |  | 23.42 | 1046 |  | 24.48 | 1072 |  | 25.56
21000 | 832 |  | 18.47 |  |  | 867 |  | 19.54 | 901 |  | 20.56 | 932 |  | 21.57 |  |  | 963 |  | 22.59 |  |  | 992 |  |  | 23.61 |  |  | 1020 |  | 24.65 |  |  | 1048 |  | 25.71 | 1074 |  | 26.78 | 1100 |  | 27.87
22000 | 869 |  | 20.74 |  |  | 902 |  | 21.84 | 934 |  | 22.9 | 965 |  | 23.94 |  |  | 995 |  | 24.98 |  |  | 1023 |  |  | 26.03 |  |  | 1051 |  | 27.09 |  |  | 1077 |  | 28.17 | 1103 |  | 29.26 | 1129 |  | 30.36
23000 | 905 |  | 23.17 |  |  | 937 |  | 24.31 | 968 |  | 25.4 | 998 |  | 26.48 |  |  | 1027 |  | 27.55 |  |  | 1055 |  |  | 28.62 |  |  | 1081 |  | 29.7 |  |  | 1107 |  | 30.79 | 1133 |  | 31.9 | 1157 |  | 33.02
24000 | 942 |  | 25.78 |  |  | 973 |  | 26.95 | 1003 |  | 28.08 | 1032 |  | 29.18 |  |  | 1059 |  | 30.28 |  |  | 1086 |  |  | 31.38 |  |  | 1113 |  | 32.48 |  |  | 1138 |  | 33.59 | 1163 |  | 34.72 | 1187 |  | 35.86
25000 | 978 |  | 28.56 |  |  | 1008 |  | 29.77 | 1037 |  | 30.93 | 1065 |  | 32.07 |  |  | 1092 |  | 33.2 |  |  | 1119 |  |  | 34.32 |  |  | 1144 |  | 35.44 |  |  | 1169 |  | 36.58 | 1193 |  | 37.72 | — |  | —
26000 | 1015 |  | 31.52 |  |  | 1044 |  | 32.76 | 1072 |  | 33.96 | 1099 |  | 35.13 |  |  | 1125 |  | 36.29 |  |  | 1151 |  |  | 37.44 |  |  | 1176 |  | 38.59 |  |  | — |  | — | — |  | — | — |  | —
27000 | 1052 |  | 34.66 |  |  | 1080 |  | 35.94 | 1107 |  | 37.18 | 1133 |  | 38.38 |  |  | 1159 |  | 39.57 |  |  | 1184 |  |  | 40.75 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
48A4,A5,A8,A9 060 (60 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
12000 | 901 |  | 13.42 |  |  | 930 |  | 14.38 | 958 |  | 15.36 | 985 |  | 16.34 |  |  | 1011 |  | 17.33 |  |  | 1036 |  |  | 18.33 |  |  | 1061 |  | 19.33 |  |  | 1085 |  | 20.34 | 1108 |  | 21.35 | 1131 |  | 22.36
14000 | 946 |  | 15.92 |  |  | 974 |  | 16.94 | 1001 |  | 17.97 | 1027 |  | 19.01 |  |  | 1052 |  | 20.06 |  |  | 1077 |  |  | 21.12 |  |  | 1101 |  | 22.18 |  |  | 1125 |  | 23.25 | 1148 |  | 24.33 | 1170 |  | 25.42
15000 | 970 |  | 17.36 |  |  | 997 |  | 18.4 | 1024 |  | 19.45 | 1049 |  | 20.51 |  |  | 1074 |  | 21.58 |  |  | 1099 |  |  | 22.67 |  |  | 1122 |  | 23.76 |  |  | 1146 |  | 24.86 | 1168 |  | 25.97 | 1191 |  | 27.08
16000 | 994 |  | 18.93 |  |  | 1021 |  | 19.98 | 1047 |  | 21.05 | 1072 |  | 22.14 |  |  | 1097 |  | 23.23 |  |  | 1121 |  |  | 24.34 |  |  | 1144 |  | 25.45 |  |  | 1167 |  | 26.58 | 1190 |  | 27.71 | — |  | —
17000 | 1019 |  | 20.63 |  |  | 1045 |  | 21.7 | 1071 |  | 22.79 | 1096 |  | 23.89 |  |  | 1120 |  | 25.01 |  |  | 1144 |  |  | 26.13 |  |  | 1167 |  | 27.27 |  |  | 1190 |  | 28.42 | — |  | — | — |  | —
18000 | 1045 |  | 22.48 |  |  | 1070 |  | 23.57 | 1096 |  | 24.67 | 1120 |  | 25.79 |  |  | 1144 |  | 26.93 |  |  | 1167 |  |  | 28.07 |  |  | 1190 |  | 29.23 |  |  | — |  | — | — |  | — | — |  | —
19000 | 1071 |  | 24.49 |  |  | 1096 |  | 25.59 | 1121 |  | 26.71 | 1145 |  | 27.84 |  |  | 1169 |  | 28.99 |  |  | 1192 |  |  | 30.16 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
20000 | 1098 |  | 26.66 |  |  | 1123 |  | 27.77 | 1147 |  | 28.9 | 1171 |  | 30.05 |  |  | 1194 |  | 31.21 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
21000 | 1125 |  | 28.99 |  |  | 1150 |  | 30.12 | 1173 |  | 31.26 | 1197 |  | 32.42 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
22000 | 1153 |  | 31.49 |  |  | 1177 |  | 32.63 | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
23000 | 1181 |  | 34.16 |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
24000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
25000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
26000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
27000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet | [17 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
50A4,A5,A8,A9 020 (20 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
4000 | 322 |  | 0.62 |  |  | 399 |  | 0.82 | 464 |  | 1.04 | 521 |  | 1.26 |  |  | 572 |  | 1.48 |  |  | 619 |  |  | 1.71 |  |  | 662 |  | 1.93 |  |  | 702 |  | 2.16 | 739 |  | 2.38 | 774 |  | 2.61
5000 | 361 |  | 0.95 |  |  | 431 |  | 1.17 | 491 |  | 1.41 | 545 |  | 1.65 |  |  | 594 |  | 1.89 |  |  | 640 |  |  | 2.14 |  |  | 682 |  | 2.39 |  |  | 722 |  | 2.64 | 759 |  | 2.89 | 795 |  | 3.14
6000 | 405 |  | 1.41 |  |  | 467 |  | 1.64 | 524 |  | 1.88 | 574 |  | 2.14 |  |  | 621 |  | 2.4 |  |  | 664 |  |  | 2.67 |  |  | 705 |  | 2.93 |  |  | 744 |  | 3.2 | 780 |  | 3.47 | 816 |  | 3.75
7000 | 451 |  | 2 |  |  | 508 |  | 2.22 | 559 |  | 2.48 | 607 |  | 2.75 |  |  | 651 |  | 3.02 |  |  | 693 |  |  | 3.3 |  |  | 732 |  | 3.58 |  |  | 769 |  | 3.87 | 804 |  | 4.16 | 839 |  | 4.45
7500 | 475 |  | 2.34 |  |  | 529 |  | 2.57 | 579 |  | 2.82 | 625 |  | 3.1 |  |  | 668 |  | 3.38 |  |  | 708 |  |  | 3.66 |  |  | 746 |  | 3.96 |  |  | 783 |  | 4.25 | 818 |  | 4.55 | 851 |  | 4.84
8000 | 500 |  | 2.72 |  |  | 551 |  | 2.95 | 598 |  | 3.21 | 643 |  | 3.48 |  |  | 685 |  | 3.77 |  |  | 724 |  |  | 4.06 |  |  | 762 |  | 4.36 |  |  | 797 |  | 4.66 | 832 |  | 4.96 | 864 |  | 5.27
9000 | 550 |  | 3.6 |  |  | 596 |  | 3.83 | 640 |  | 4.09 | 682 |  | 4.36 |  |  | 721 |  | 4.66 |  |  | 759 |  |  | 4.96 |  |  | 795 |  | 5.27 |  |  | 829 |  | 5.58 | 862 |  | 5.9 | 893 |  | 6.22
10000 | 601 |  | 4.63 |  |  | 644 |  | 4.86 | 684 |  | 5.12 | 723 |  | 5.4 |  |  | 760 |  | 5.7 |  |  | 796 |  |  | 6.01 |  |  | 830 |  | 6.33 |  |  | 863 |  | 6.65 | 894 |  | 6.98 | 925 |  | 7.31
50A4,A5,A8,A9 020 (20 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
4000 | 808 |  | 2.84 |  |  | 840 |  | 3.06 | 870 |  | 3.29 | 900 |  | 3.52 |  |  | 928 |  | 3.75 |  |  | 955 |  |  | 3.98 |  |  | 981 |  | 4.21 |  |  | 1007 |  | 4.44 | 1031 |  | 4.67 | 1055 |  | 4.91
5000 | 829 |  | 3.39 |  |  | 861 |  | 3.64 | 892 |  | 3.89 | 922 |  | 4.14 |  |  | 950 |  | 4.4 |  |  | 978 |  |  | 4.65 |  |  | 1005 |  | 4.9 |  |  | 1031 |  | 5.16 | 1056 |  | 5.41 | 1080 |  | 5.67
6000 | 849 |  | 4.02 |  |  | 881 |  | 4.29 | 912 |  | 4.57 | 942 |  | 4.84 |  |  | 971 |  | 5.12 |  |  | 999 |  |  | 5.39 |  |  | 1026 |  | 5.67 |  |  | 1052 |  | 5.94 | 1077 |  | 6.22 | 1102 |  | 6.49
7000 | 871 |  | 4.74 |  |  | 903 |  | 5.03 | 933 |  | 5.33 | 963 |  | 5.62 |  |  | 991 |  | 5.92 |  |  | 1019 |  |  | 6.21 |  |  | 1046 |  | 6.51 |  |  | 1072 |  | 6.8 | 1098 |  | 7.1 | 1123 |  | 7.4
7500 | 883 |  | 5.14 |  |  | 915 |  | 5.44 | 945 |  | 5.75 | 974 |  | 6.05 |  |  | 1002 |  | 6.35 |  |  | 1030 |  |  | 6.66 |  |  | 1057 |  | 6.96 |  |  | 1083 |  | 7.27 | 1108 |  | 7.58 | 1133 |  | 7.88
8000 | 896 |  | 5.58 |  |  | 927 |  | 5.89 | 957 |  | 6.2 | 985 |  | 6.51 |  |  | 1014 |  | 6.82 |  |  | 1041 |  |  | 7.13 |  |  | 1067 |  | 7.45 |  |  | 1093 |  | 7.76 | 1118 |  | 8.08 | 1143 |  | 8.39
9000 | 924 |  | 6.54 |  |  | 954 |  | 6.86 | 983 |  | 7.19 | 1011 |  | 7.51 |  |  | 1038 |  | 7.84 |  |  | 1064 |  |  | 8.17 |  |  | 1090 |  | 8.5 |  |  | 1116 |  | 8.83 | 1141 |  | 9.16 | 1165 |  | 9.49
10000 | 954 |  | 7.64 |  |  | 983 |  | 7.98 | 1011 |  | 8.31 | 1038 |  | 8.65 |  |  | 1065 |  | 8.99 |  |  | 1091 |  |  | 9.34 |  |  | 1116 |  | 9.68 |  |  | 1141 |  | 10.02 | 1165 |  | 10.37 | 1189 |  | 10.72
50A4,A5,A8,A9 025-030 (25 THRU 30 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
5000 | 366 |  | 0.97 |  |  | 435 |  | 1.19 | 495 |  | 1.42 | 548 |  | 1.67 |  |  | 597 |  | 1.91 |  |  | 642 |  |  | 2.16 |  |  | 685 |  | 2.41 |  |  | 724 |  | 2.65 | 762 |  | 2.9 | 797 |  | 3.16
6000 | 411 |  | 1.43 |  |  | 473 |  | 1.66 | 529 |  | 1.91 | 579 |  | 2.16 |  |  | 625 |  | 2.43 |  |  | 668 |  |  | 2.69 |  |  | 709 |  | 2.96 |  |  | 747 |  | 3.23 | 784 |  | 3.5 | 819 |  | 3.77
7000 | 459 |  | 2.02 |  |  | 515 |  | 2.25 | 566 |  | 2.51 | 613 |  | 2.78 |  |  | 657 |  | 3.06 |  |  | 698 |  |  | 3.34 |  |  | 737 |  | 3.62 |  |  | 774 |  | 3.91 | 809 |  | 4.2 | 843 |  | 4.49
8000 | 508 |  | 2.76 |  |  | 559 |  | 2.99 | 606 |  | 3.25 | 650 |  | 3.53 |  |  | 691 |  | 3.82 |  |  | 731 |  |  | 4.11 |  |  | 768 |  | 4.41 |  |  | 803 |  | 4.71 | 837 |  | 5.01 | 870 |  | 5.32
9000 | 560 |  | 3.64 |  |  | 605 |  | 3.88 | 649 |  | 4.14 | 690 |  | 4.42 |  |  | 729 |  | 4.72 |  |  | 766 |  |  | 5.02 |  |  | 802 |  | 5.33 |  |  | 835 |  | 5.64 | 868 |  | 5.96 | 900 |  | 6.28
10000 | 612 |  | 4.68 |  |  | 654 |  | 4.92 | 694 |  | 5.19 | 732 |  | 5.47 |  |  | 769 |  | 5.77 |  |  | 804 |  |  | 6.09 |  |  | 838 |  | 6.4 |  |  | 870 |  | 6.73 | 902 |  | 7.06 | 932 |  | 7.39
11000 | 665 |  | 5.89 |  |  | 703 |  | 6.14 | 740 |  | 6.41 | 776 |  | 6.69 |  |  | 811 |  | 7 |  |  | 844 |  |  | 7.31 |  |  | 876 |  | 7.64 |  |  | 907 |  | 7.97 | 937 |  | 8.31 | 967 |  | 8.65
12000 | 718 |  | 7.28 |  |  | 754 |  | 7.53 | 788 |  | 7.8 | 822 |  | 8.09 |  |  | 854 |  | 8.39 |  |  | 886 |  |  | 8.71 |  |  | 916 |  | 9.04 |  |  | 946 |  | 9.38 | 975 |  | 9.72 | 1003 |  | 10.07
13000 | 772 |  | 8.85 |  |  | 806 |  | 9.11 | 838 |  | 9.38 | 869 |  | 9.67 |  |  | 899 |  | 9.98 |  |  | 929 |  |  | 10.3 |  |  | 958 |  | 10.63 |  |  | 987 |  | 10.97 | 1014 |  | 11.32 | 1041 |  | 11.68
14000 | 826 |  | 10.61 |  |  | 858 |  | 10.87 | 888 |  | 11.15 | 917 |  | 11.44 |  |  | 946 |  | 11.75 |  |  | 974 |  |  | 12.07 |  |  | 1002 |  | 12.41 |  |  | 1029 |  | 12.75 | 1055 |  | 13.1 | 1081 |  | 13.46
15000 | 881 |  | 12.57 |  |  | 910 |  | 12.84 | 939 |  | 13.12 | 967 |  | 13.41 |  |  | 994 |  | 13.72 |  |  | 1021 |  |  | 14.05 |  |  | 1047 |  | 14.38 |  |  | 1073 |  | 14.73 | 1098 |  | 15.08 | 1123 |  | 15.45
50A4,A5,A8,A9 025-030 (25 THRU 30 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
5000 | 831 |  | 3.41 |  |  | 863 |  | 3.66 | 894 |  | 3.91 | 924 |  | 4.16 |  |  | 952 |  | 4.41 |  |  | 980 |  |  | 4.67 |  |  | 1007 |  | 4.92 |  |  | 1032 |  | 5.17 | 1057 |  | 5.43 | 1082 |  | 5.68
6000 | 852 |  | 4.05 |  |  | 884 |  | 4.32 | 915 |  | 4.59 | 945 |  | 4.87 |  |  | 974 |  | 5.14 |  |  | 1001 |  |  | 5.42 |  |  | 1028 |  | 5.69 |  |  | 1054 |  | 5.97 | 1080 |  | 6.24 | 1105 |  | 6.52
7000 | 875 |  | 4.78 |  |  | 907 |  | 5.07 | 937 |  | 5.37 | 967 |  | 5.66 |  |  | 995 |  | 5.95 |  |  | 1023 |  |  | 6.25 |  |  | 1049 |  | 6.55 |  |  | 1076 |  | 6.84 | 1101 |  | 7.14 | 1126 |  | 7.44
8000 | 901 |  | 5.63 |  |  | 932 |  | 5.94 | 961 |  | 6.25 | 990 |  | 6.56 |  |  | 1018 |  | 6.87 |  |  | 1045 |  |  | 7.18 |  |  | 1072 |  | 7.5 |  |  | 1097 |  | 7.81 | 1123 |  | 8.13 | 1147 |  | 8.44
9000 | 930 |  | 6.6 |  |  | 960 |  | 6.93 | 988 |  | 7.25 | 1016 |  | 7.58 |  |  | 1043 |  | 7.91 |  |  | 1070 |  |  | 8.23 |  |  | 1096 |  | 8.57 |  |  | 1121 |  | 8.9 | 1146 |  | 9.23 | 1170 |  | 9.56
10000 | 961 |  | 7.72 |  |  | 990 |  | 8.06 | 1018 |  | 8.4 | 1045 |  | 8.74 |  |  | 1071 |  | 9.08 |  |  | 1097 |  |  | 9.42 |  |  | 1122 |  | 9.76 |  |  | 1147 |  | 10.11 | 1171 |  | 10.46 | 1194 |  | 10.8
11000 | 995 |  | 8.99 |  |  | 1022 |  | 9.34 | 1049 |  | 9.69 | 1075 |  | 10.04 |  |  | 1101 |  | 10.39 |  |  | 1126 |  |  | 10.75 |  |  | 1151 |  | 11.11 |  |  | 1175 |  | 11.47 | 1198 |  | 11.82 | — |  | —
12000 | 1030 |  | 10.43 |  |  | 1057 |  | 10.78 | 1083 |  | 11.14 | 1108 |  | 11.51 |  |  | 1133 |  | 11.87 |  |  | 1157 |  |  | 12.24 |  |  | 1181 |  | 12.61 |  |  | — |  | — | — |  | — | — |  | —
13000 | 1068 |  | 12.04 |  |  | 1093 |  | 12.4 | 1119 |  | 12.77 | 1143 |  | 13.14 |  |  | 1167 |  | 13.52 |  |  | 1191 |  |  | 13.89 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
14000 | 1107 |  | 13.83 |  |  | 1131 |  | 14.2 | 1156 |  | 14.58 | 1179 |  | 14.96 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
15000 | 1147 |  | 15.82 |  |  | 1171 |  | 16.19 | 1194 |  | 16.58 | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet
[18 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
50A4,A5,A8,A9 035 (35 TONS)
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
7000 | 522 |  | 2.06 |  |  | 573 |  | 2.32 | 620 |  | 2.57 | 664 |  | 2.82 |  |  | 705 |  | 3.06 |  |  | 744 |  |  | 3.3 |  |  | 780 |  | 3.54 |  |  | 815 |  | 3.78 | 849 |  | 4.01 | 881 |  | 4.24
8000 | 576 |  | 2.75 |  |  | 622 |  | 3.03 | 665 |  | 3.3 | 706 |  | 3.57 |  |  | 745 |  | 3.84 |  |  | 782 |  |  | 4.1 |  |  | 817 |  | 4.36 |  |  | 850 |  | 4.62 | 883 |  | 4.87 | 914 |  | 5.12
9000 | 630 |  | 3.57 |  |  | 672 |  | 3.86 | 712 |  | 4.16 | 750 |  | 4.45 |  |  | 787 |  | 4.74 |  |  | 822 |  |  | 5.02 |  |  | 855 |  | 5.3 |  |  | 888 |  | 5.58 | 919 |  | 5.86 | 949 |  | 6.13
10000 | 686 |  | 4.52 |  |  | 724 |  | 4.84 | 761 |  | 5.15 | 797 |  | 5.46 |  |  | 831 |  | 5.77 |  |  | 864 |  |  | 6.07 |  |  | 896 |  | 6.37 |  |  | 927 |  | 6.67 | 957 |  | 6.97 | 986 |  | 7.26
10500 | 714 |  | 5.05 |  |  | 750 |  | 5.38 | 786 |  | 5.7 | 821 |  | 6.02 |  |  | 854 |  | 6.34 |  |  | 886 |  |  | 6.65 |  |  | 917 |  | 6.96 |  |  | 947 |  | 7.27 | 977 |  | 7.57 | 1005 |  | 7.87
11000 | 742 |  | 5.62 |  |  | 777 |  | 5.95 | 811 |  | 6.28 | 845 |  | 6.61 |  |  | 877 |  | 6.94 |  |  | 909 |  |  | 7.26 |  |  | 939 |  | 7.58 |  |  | 968 |  | 7.9 | 997 |  | 8.21 | 1025 |  | 8.52
12000 | 799 |  | 6.88 |  |  | 831 |  | 7.22 | 863 |  | 7.57 | 894 |  | 7.91 |  |  | 925 |  | 8.25 |  |  | 954 |  |  | 8.6 |  |  | 983 |  | 8.93 |  |  | 1011 |  | 9.27 | 1039 |  | 9.6 | 1065 |  | 9.93
13000 | 856 |  | 8.29 |  |  | 886 |  | 8.65 | 916 |  | 9.01 | 945 |  | 9.37 |  |  | 974 |  | 9.72 |  |  | 1002 |  |  | 10.08 |  |  | 1029 |  | 10.44 |  |  | 1056 |  | 10.79 | 1082 |  | 11.14 | 1108 |  | 11.49
14000 | 914 |  | 9.87 |  |  | 942 |  | 10.24 | 969 |  | 10.61 | 997 |  | 10.98 |  |  | 1024 |  | 11.36 |  |  | 1050 |  |  | 11.73 |  |  | 1076 |  | 12.1 |  |  | 1102 |  | 12.47 | 1127 |  | 12.84 | 1152 |  | 13.2
15000 | 971 |  | 11.62 |  |  | 998 |  | 12 | 1024 |  | 12.39 | 1050 |  | 12.77 |  |  | 1075 |  | 13.16 |  |  | 1100 |  |  | 13.54 |  |  | 1125 |  | 13.93 |  |  | 1149 |  | 14.31 | 1173 |  | 14.7 | 1197 |  | 15.08
16000 | 1029 |  | 13.55 |  |  | 1054 |  | 13.94 | 1079 |  | 14.34 | 1103 |  | 14.74 |  |  | 1127 |  | 15.13 |  |  | 1151 |  |  | 15.53 |  |  | 1174 |  | 15.93 |  |  | 1198 |  | 16.33 | 1220 |  | 16.73 | 1243 |  | 17.12
17000 | 1088 |  | 15.66 |  |  | 1111 |  | 16.07 | 1134 |  | 16.47 | 1157 |  | 16.88 |  |  | 1180 |  | 17.29 |  |  | 1203 |  |  | 17.7 |  |  | 1225 |  | 18.11 |  |  | 1247 |  | 18.53 | 1269 |  | 18.93 | 1290 |  | 19.34
17500 | 1117 |  | 16.79 |  |  | 1140 |  | 17.2 | 1162 |  | 17.61 | 1184 |  | 18.02 |  |  | 1207 |  | 18.44 |  |  | 1229 |  |  | 18.86 |  |  | 1250 |  | 19.27 |  |  | 1272 |  | 19.69 | 1293 |  | 20.11 | — |  | —
50A4,A5,A8,A9 035 (35 TONS) (cont)
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
7000 | 912 |  | 4.46 |  |  | 942 |  | 4.68 | 970 |  | 4.9 | 998 |  | 5.12 |  |  | 1025 |  | 5.33 |  |  | 1051 |  |  | 5.54 |  |  | 1076 |  | 5.75 |  |  | 1101 |  | 5.96 | 1124 |  | 6.16 | 1148 |  | 6.36
8000 | 944 |  | 5.37 |  |  | 973 |  | 5.62 | 1001 |  | 5.86 | 1029 |  | 6.11 |  |  | 1055 |  | 6.35 |  |  | 1081 |  |  | 6.58 |  |  | 1106 |  | 6.82 |  |  | 1130 |  | 7.05 | 1154 |  | 7.28 | 1177 |  | 7.51
9000 | 978 |  | 6.4 |  |  | 1006 |  | 6.67 | 1034 |  | 6.93 | 1060 |  | 7.2 |  |  | 1086 |  | 7.46 |  |  | 1112 |  |  | 7.72 |  |  | 1136 |  | 7.98 |  |  | 1160 |  | 8.23 | 1184 |  | 8.49 | 1207 |  | 8.74
10000 | 1014 |  | 7.55 |  |  | 1041 |  | 7.84 | 1068 |  | 8.12 | 1094 |  | 8.41 |  |  | 1119 |  | 8.69 |  |  | 1144 |  |  | 8.97 |  |  | 1168 |  | 9.25 |  |  | 1192 |  | 9.52 | 1215 |  | 9.8 | 1238 |  | 10.07
10500 | 1033 |  | 8.17 |  |  | 1059 |  | 8.47 | 1086 |  | 8.77 | 1111 |  | 9.06 |  |  | 1136 |  | 9.35 |  |  | 1161 |  |  | 9.64 |  |  | 1184 |  | 9.93 |  |  | 1208 |  | 10.22 | 1231 |  | 10.5 | 1253 |  | 10.79
11000 | 1052 |  | 8.83 |  |  | 1078 |  | 9.14 | 1104 |  | 9.44 | 1129 |  | 9.75 |  |  | 1154 |  | 10.05 |  |  | 1178 |  |  | 10.35 |  |  | 1201 |  | 10.64 |  |  | 1224 |  | 10.94 | 1247 |  | 11.23 | 1269 |  | 11.53
12000 | 1091 |  | 10.26 |  |  | 1117 |  | 10.58 | 1142 |  | 10.9 | 1166 |  | 11.23 |  |  | 1190 |  | 11.54 |  |  | 1213 |  |  | 11.86 |  |  | 1236 |  | 12.18 |  |  | 1259 |  | 12.49 | 1281 |  | 12.8 | — |  | —
13000 | 1133 |  | 11.83 |  |  | 1157 |  | 12.17 | 1181 |  | 12.51 | 1205 |  | 12.85 |  |  | 1228 |  | 13.19 |  |  | 1251 |  |  | 13.52 |  |  | 1273 |  | 13.86 |  |  | 1295 |  | 14.19 | — |  | — | — |  | —
14000 | 1176 |  | 13.56 |  |  | 1199 |  | 13.92 | 1222 |  | 14.28 | 1245 |  | 14.63 |  |  | 1268 |  | 14.99 |  |  | 1290 |  |  | 15.34 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
15000 | 1220 |  | 15.45 |  |  | 1243 |  | 15.83 | 1265 |  | 16.2 | 1287 |  | 16.58 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
16000 | 1265 |  | 17.52 |  |  | 1287 |  | 17.91 | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
17000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
17500 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
50A4,A5,A8,A9 040 (40 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
8000 | 499 |  | 2.88 |  |  | 546 |  | 3.27 | 590 |  | 3.66 | 632 |  | 4.06 |  |  | 672 |  | 4.46 |  |  | 711 |  |  | 4.87 |  |  | 748 |  | 5.28 |  |  | 784 |  | 5.7 | 819 |  | 6.14 | 853 |  | 6.58
9000 | 548 |  | 3.78 |  |  | 591 |  | 4.2 | 631 |  | 4.62 | 670 |  | 5.04 |  |  | 708 |  | 5.47 |  |  | 744 |  |  | 5.9 |  |  | 778 |  | 6.33 |  |  | 812 |  | 6.77 | 845 |  | 7.22 | 877 |  | 7.67
10000 | 599 |  | 4.86 |  |  | 637 |  | 5.3 | 675 |  | 5.74 | 711 |  | 6.19 |  |  | 746 |  | 6.64 |  |  | 779 |  |  | 7.09 |  |  | 812 |  | 7.55 |  |  | 844 |  | 8.01 | 875 |  | 8.47 | 905 |  | 8.94
11000 | 649 |  | 6.11 |  |  | 685 |  | 6.57 | 720 |  | 7.04 | 753 |  | 7.51 |  |  | 786 |  | 7.99 |  |  | 817 |  |  | 8.47 |  |  | 848 |  | 8.94 |  |  | 878 |  | 9.43 | 907 |  | 9.91 | 936 |  | 10.4
12000 | 701 |  | 7.54 |  |  | 734 |  | 8.03 | 766 |  | 8.52 | 797 |  | 9.02 |  |  | 828 |  | 9.52 |  |  | 857 |  |  | 10.02 |  |  | 886 |  | 10.52 |  |  | 915 |  | 11.03 | 943 |  | 11.53 | 970 |  | 12.04
13000 | 753 |  | 9.18 |  |  | 783 |  | 9.69 | 813 |  | 10.21 | 842 |  | 10.72 |  |  | 871 |  | 11.25 |  |  | 899 |  |  | 11.77 |  |  | 927 |  | 12.3 |  |  | 953 |  | 12.82 | 980 |  | 13.35 | 1006 |  | 13.88
14000 | 805 |  | 11.03 |  |  | 833 |  | 11.56 | 861 |  | 12.09 | 889 |  | 12.63 |  |  | 916 |  | 13.18 |  |  | 942 |  |  | 13.73 |  |  | 968 |  | 14.27 |  |  | 994 |  | 14.82 | 1019 |  | 15.37 | 1044 |  | 15.92
15000 | 857 |  | 13.09 |  |  | 884 |  | 13.64 | 910 |  | 14.2 | 936 |  | 14.76 |  |  | 962 |  | 15.32 |  |  | 987 |  |  | 15.89 |  |  | 1011 |  | 16.46 |  |  | 1036 |  | 17.03 | 1060 |  | 17.61 | 1083 |  | 18.18
16000 | 910 |  | 15.38 |  |  | 935 |  | 15.95 | 960 |  | 16.53 | 984 |  | 17.11 |  |  | 1008 |  | 17.69 |  |  | 1032 |  |  | 18.28 |  |  | 1056 |  | 18.87 |  |  | 1079 |  | 19.47 | 1101 |  | 20.06 | 1124 |  | 20.66
17000 | 963 |  | 17.91 |  |  | 986 |  | 18.5 | 1010 |  | 19.09 | 1033 |  | 19.69 |  |  | 1056 |  | 20.3 |  |  | 1078 |  |  | 20.91 |  |  | 1101 |  | 21.52 |  |  | 1123 |  | 22.13 | 1145 |  | 22.75 | 1166 |  | 23.36
18000 | 1016 |  | 20.68 |  |  | 1038 |  | 21.29 | 1060 |  | 21.9 | 1082 |  | 22.52 |  |  | 1104 |  | 23.15 |  |  | 1126 |  |  | 23.77 |  |  | 1147 |  | 24.41 |  |  | 1168 |  | 25.04 | 1189 |  | 25.67 | 1209 |  | 26.31
19000 | 1069 |  | 23.71 |  |  | 1090 |  | 24.33 | 1111 |  | 24.96 | 1132 |  | 25.6 |  |  | 1153 |  | 26.25 |  |  | 1173 |  |  | 26.89 |  |  | 1194 |  | 27.54 |  |  | 1214 |  | 28.19 | 1234 |  | 28.85 | — |  | —
20000 | 1122 |  | 26.99 |  |  | 1142 |  | 27.64 | 1162 |  | 28.29 | 1182 |  | 28.95 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
50A4,A5,A8,A9 040 (40 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
8000 | 885 |  | 7.03 |  |  | 917 |  | 7.48 | 948 |  | 7.95 | 978 |  | 8.42 |  |  | 1007 |  | 8.9 |  |  | 1036 |  |  | 9.39 |  |  | 1063 |  | 9.88 |  |  | 1090 |  | 10.38 | 1116 |  | 10.88 | 1142 |  | 11.39
9000 | 908 |  | 8.13 |  |  | 939 |  | 8.6 | 968 |  | 9.08 | 997 |  | 9.56 |  |  | 1026 |  | 10.05 |  |  | 1053 |  |  | 10.55 |  |  | 1080 |  | 11.05 |  |  | 1107 |  | 11.56 | 1133 |  | 12.08 | 1158 |  | 12.6
10000 | 934 |  | 9.42 |  |  | 963 |  | 9.9 | 992 |  | 10.39 | 1020 |  | 10.89 |  |  | 1047 |  | 11.39 |  |  | 1073 |  |  | 11.89 |  |  | 1100 |  | 12.41 |  |  | 1125 |  | 12.93 | 1151 |  | 13.45 | 1175 |  | 13.99
11000 | 964 |  | 10.89 |  |  | 992 |  | 11.39 | 1019 |  | 11.89 | 1045 |  | 12.4 |  |  | 1071 |  | 12.91 |  |  | 1097 |  |  | 13.43 |  |  | 1122 |  | 13.96 |  |  | 1147 |  | 14.49 | 1171 |  | 15.02 | 1195 |  | 15.56
12000 | 996 |  | 12.55 |  |  | 1023 |  | 13.07 | 1048 |  | 13.59 | 1074 |  | 14.11 |  |  | 1099 |  | 14.64 |  |  | 1123 |  |  | 15.17 |  |  | 1147 |  | 15.71 |  |  | 1171 |  | 16.25 | 1195 |  | 16.8 | 1218 |  | 17.35
13000 | 1031 |  | 14.41 |  |  | 1056 |  | 14.95 | 1081 |  | 15.48 | 1105 |  | 16.03 |  |  | 1129 |  | 16.57 |  |  | 1152 |  |  | 17.12 |  |  | 1175 |  | 17.67 |  |  | 1198 |  | 18.22 | 1221 |  | 18.78 | 1243 |  | 19.35
14000 | 1068 |  | 16.48 |  |  | 1092 |  | 17.03 | 1115 |  | 17.59 | 1138 |  | 18.15 |  |  | 1161 |  | 18.71 |  |  | 1184 |  |  | 19.27 |  |  | 1206 |  | 19.84 |  |  | 1228 |  | 20.41 | 1250 |  | 20.99 | 1271 |  | 21.56
15000 | 1106 |  | 18.75 |  |  | 1129 |  | 19.33 | 1151 |  | 19.91 | 1174 |  | 20.48 |  |  | 1196 |  | 21.07 |  |  | 1217 |  |  | 21.65 |  |  | 1239 |  | 22.23 |  |  | 1260 |  | 22.82 | 1280 |  | 23.41 | — |  | —
16000 | 1146 |  | 21.25 |  |  | 1168 |  | 21.85 | 1189 |  | 22.45 | 1211 |  | 23.04 |  |  | 1232 |  | 23.64 |  |  | 1253 |  |  | 24.25 |  |  | 1273 |  | 24.85 |  |  | 1293 |  | 25.45 | — |  | — | — |  | —
17000 | 1187 |  | 23.98 |  |  | 1208 |  | 24.6 | 1229 |  | 25.21 | 1249 |  | 25.83 |  |  | 1270 |  | 26.46 |  |  | 1289 |  |  | 27.07 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
18000 | 1230 |  | 26.95 |  |  | 1250 |  | 27.58 | 1269 |  | 28.22 | 1289 |  | 28.86 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
19000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
20000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet
[18 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
50A4,A5,A8,A9 050 (50 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
10000 | 608 |  | 4.96 |  |  | 646 |  | 5.4 | 683 |  | 5.85 | 719 |  | 6.3 |  |  | 754 |  | 6.75 |  |  | 787 |  |  | 7.2 |  |  | 819 |  | 7.66 |  |  | 851 |  | 8.12 | 882 |  | 8.58 | 912 |  | 9.06
11000 | 659 |  | 6.23 |  |  | 694 |  | 6.69 | 728 |  | 7.16 | 762 |  | 7.64 |  |  | 794 |  | 8.11 |  |  | 825 |  |  | 8.59 |  |  | 856 |  | 9.07 |  |  | 886 |  | 9.55 | 915 |  | 10.04 | 943 |  | 10.53
12000 | 710 |  | 7.68 |  |  | 743 |  | 8.17 | 775 |  | 8.67 | 806 |  | 9.17 |  |  | 836 |  | 9.67 |  |  | 866 |  |  | 10.17 |  |  | 895 |  | 10.67 |  |  | 923 |  | 11.17 | 950 |  | 11.68 | 978 |  | 12.19
13000 | 763 |  | 9.35 |  |  | 793 |  | 9.86 | 823 |  | 10.37 | 852 |  | 10.89 |  |  | 880 |  | 11.42 |  |  | 908 |  |  | 11.94 |  |  | 935 |  | 12.47 |  |  | 962 |  | 12.99 | 988 |  | 13.52 | 1014 |  | 14.05
14000 | 815 |  | 11.22 |  |  | 843 |  | 11.75 | 871 |  | 12.29 | 899 |  | 12.83 |  |  | 925 |  | 13.38 |  |  | 952 |  |  | 13.92 |  |  | 978 |  | 14.47 |  |  | 1003 |  | 15.02 | 1028 |  | 15.57 | 1052 |  | 16.12
15000 | 868 |  | 13.31 |  |  | 895 |  | 13.86 | 921 |  | 14.42 | 946 |  | 14.98 |  |  | 972 |  | 15.55 |  |  | 997 |  |  | 16.12 |  |  | 1021 |  | 16.69 |  |  | 1045 |  | 17.26 | 1069 |  | 17.83 | 1092 |  | 18.41
16000 | 921 |  | 15.64 |  |  | 946 |  | 16.21 | 971 |  | 16.78 | 995 |  | 17.37 |  |  | 1019 |  | 17.96 |  |  | 1043 |  |  | 18.54 |  |  | 1066 |  | 19.14 |  |  | 1089 |  | 19.73 | 1111 |  | 20.32 | 1134 |  | 20.92
17000 | 974 |  | 18.2 |  |  | 998 |  | 18.79 | 1021 |  | 19.39 | 1044 |  | 19.99 |  |  | 1067 |  | 20.6 |  |  | 1089 |  |  | 21.21 |  |  | 1112 |  | 21.82 |  |  | 1134 |  | 22.43 | 1155 |  | 23.05 | 1176 |  | 23.66
18000 | 1028 |  | 21.01 |  |  | 1050 |  | 21.62 | 1072 |  | 22.24 | 1094 |  | 22.86 |  |  | 1116 |  | 23.49 |  |  | 1137 |  |  | 24.12 |  |  | 1158 |  | 24.75 |  |  | 1179 |  | 25.38 | 1200 |  | 26.02 | 1220 |  | 26.65
19000 | 1081 |  | 24.08 |  |  | 1103 |  | 24.71 | 1124 |  | 25.35 | 1145 |  | 25.99 |  |  | 1165 |  | 26.63 |  |  | 1185 |  |  | 27.28 |  |  | 1206 |  | 27.93 |  |  | 1226 |  | 28.58 | 1245 |  | 29.24 | 1265 |  | 29.9
20000 | 1135 |  | 27.42 |  |  | 1155 |  | 28.06 | 1175 |  | 28.72 | 1195 |  | 29.38 |  |  | 1215 |  | 30.04 |  |  | 1234 |  |  | 30.71 |  |  | 1254 |  | 31.38 |  |  | 1273 |  | 32.05 | 1292 |  | 32.72 | — |  | —
50A4,A5,A8,A9 050 (50 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
10000 | 941 |  | 9.53 |  |  | 970 |  | 10.02 | 998 |  | 10.51 | 1026 |  | 11 |  |  | 1053 |  | 11.51 |  |  | 1080 |  |  | 12.01 |  |  | 1106 |  | 12.53 |  |  | 1131 |  | 13.05 | 1156 |  | 13.58 | 1181 |  | 14.11
11000 | 971 |  | 11.02 |  |  | 999 |  | 11.52 | 1026 |  | 12.02 | 1052 |  | 12.53 |  |  | 1078 |  | 13.05 |  |  | 1103 |  |  | 13.57 |  |  | 1128 |  | 14.09 |  |  | 1153 |  | 14.63 | 1177 |  | 15.16 | 1201 |  | 15.71
12000 | 1004 |  | 12.7 |  |  | 1030 |  | 13.22 | 1056 |  | 13.74 | 1081 |  | 14.26 |  |  | 1106 |  | 14.79 |  |  | 1130 |  |  | 15.33 |  |  | 1154 |  | 15.86 |  |  | 1178 |  | 16.41 | 1201 |  | 16.96 | 1224 |  | 17.51
13000 | 1039 |  | 14.59 |  |  | 1064 |  | 15.12 | 1088 |  | 15.66 | 1113 |  | 16.2 |  |  | 1136 |  | 16.74 |  |  | 1160 |  |  | 17.29 |  |  | 1183 |  | 17.85 |  |  | 1206 |  | 18.4 | 1228 |  | 18.96 | 1250 |  | 19.53
14000 | 1076 |  | 16.68 |  |  | 1100 |  | 17.23 | 1123 |  | 17.79 | 1147 |  | 18.35 |  |  | 1169 |  | 18.91 |  |  | 1192 |  |  | 19.48 |  |  | 1214 |  | 20.04 |  |  | 1236 |  | 20.62 | 1257 |  | 21.19 | 1279 |  | 21.77
15000 | 1115 |  | 18.98 |  |  | 1138 |  | 19.56 | 1160 |  | 20.14 | 1182 |  | 20.72 |  |  | 1204 |  | 21.3 |  |  | 1226 |  |  | 21.88 |  |  | 1247 |  | 22.47 |  |  | 1268 |  | 23.05 | 1289 |  | 23.65 | — |  | —
16000 | 1156 |  | 21.52 |  |  | 1178 |  | 22.11 | 1199 |  | 22.71 | 1220 |  | 23.31 |  |  | 1241 |  | 23.91 |  |  | 1262 |  |  | 24.51 |  |  | 1282 |  | 25.12 |  |  | — |  | — | — |  | — | — |  | —
17000 | 1198 |  | 24.28 |  |  | 1218 |  | 24.9 | 1239 |  | 25.52 | 1259 |  | 26.14 |  |  | 1279 |  | 26.76 |  |  | 1299 |  |  | 27.38 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
18000 | 1240 |  | 27.29 |  |  | 1260 |  | 27.93 | 1280 |  | 28.57 | 1300 |  | 29.21 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
19000 | 1284 |  | 30.55 |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
20000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
50A4,A5,A8,A9 060 (60 TONS)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 0.2 |  |  |  |  | 0.4 |  |  | 0.6 |  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 1.2 | [5 empty] | 1.4 |  |  |  |  | 1.6 |  |  | 1.8 |  |  | 2
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
12000 | 490 |  | 4.48 |  |  | 543 |  | 5.17 | 591 |  | 5.88 | 634 |  | 6.61 |  |  | 674 |  | 7.37 |  |  | 711 |  |  | 8.14 |  |  | 746 |  | 8.94 |  |  | 779 |  | 9.76 | 811 |  | 10.6 | 841 |  | 11.45
14000 | 554 |  | 6.41 |  |  | 602 |  | 7.17 | 645 |  | 7.94 | 686 |  | 8.72 |  |  | 723 |  | 9.51 |  |  | 759 |  |  | 10.33 |  |  | 792 |  | 11.16 |  |  | 824 |  | 12.01 | 855 |  | 12.88 | 884 |  | 13.76
15000 | 586 |  | 7.56 |  |  | 632 |  | 8.34 | 674 |  | 9.14 | 713 |  | 9.94 |  |  | 749 |  | 10.77 |  |  | 784 |  |  | 11.6 |  |  | 816 |  | 12.45 |  |  | 848 |  | 13.32 | 878 |  | 14.21 | 906 |  | 15.11
16000 | 619 |  | 8.83 |  |  | 663 |  | 9.64 | 703 |  | 10.46 | 741 |  | 11.3 |  |  | 776 |  | 12.14 |  |  | 810 |  |  | 13 |  |  | 841 |  | 13.87 |  |  | 872 |  | 14.76 | 901 |  | 15.66 | 929 |  | 16.58
17000 | 652 |  | 10.23 |  |  | 694 |  | 11.07 | 733 |  | 11.92 | 769 |  | 12.78 |  |  | 803 |  | 13.65 |  |  | 836 |  |  | 14.53 |  |  | 867 |  | 15.42 |  |  | 897 |  | 16.33 | 926 |  | 17.25 | 953 |  | 18.19
18000 | 685 |  | 11.76 |  |  | 725 |  | 12.63 | 763 |  | 13.51 | 798 |  | 14.39 |  |  | 831 |  | 15.29 |  |  | 863 |  |  | 16.2 |  |  | 893 |  | 17.11 |  |  | 922 |  | 18.04 | 950 |  | 18.98 | 978 |  | 19.93
19000 | 719 |  | 13.44 |  |  | 757 |  | 14.33 | 793 |  | 15.23 | 827 |  | 16.14 |  |  | 860 |  | 17.07 |  |  | 890 |  |  | 18 |  |  | 920 |  | 18.94 |  |  | 949 |  | 19.88 | 976 |  | 20.84 | 1003 |  | 21.81
20000 | 753 |  | 15.26 |  |  | 789 |  | 16.18 | 824 |  | 17.1 | 857 |  | 18.04 |  |  | 888 |  | 18.99 |  |  | 918 |  |  | 19.94 |  |  | 947 |  | 20.9 |  |  | 975 |  | 21.87 | 1002 |  | 22.85 | 1028 |  | 23.84
21000 | 787 |  | 17.23 |  |  | 822 |  | 18.17 | 855 |  | 19.12 | 887 |  | 20.08 |  |  | 918 |  | 21.05 |  |  | 947 |  |  | 22.03 |  |  | 975 |  | 23.02 |  |  | 1002 |  | 24.01 | 1029 |  | 25.01 | 1054 |  | 26.02
22000 | 821 |  | 19.35 |  |  | 855 |  | 20.32 | 887 |  | 21.29 | 918 |  | 22.28 |  |  | 947 |  | 23.28 |  |  | 976 |  |  | 24.28 |  |  | 1003 |  | 25.28 |  |  | 1030 |  | 26.3 | 1056 |  | 27.32 | 1081 |  | 28.35
23000 | 855 |  | 21.63 |  |  | 888 |  | 22.62 | 919 |  | 23.62 | 949 |  | 24.63 |  |  | 977 |  | 25.65 |  |  | 1005 |  |  | 26.68 |  |  | 1032 |  | 27.71 |  |  | 1058 |  | 28.75 | 1083 |  | 29.79 | 1108 |  | 30.85
24000 | 889 |  | 24.07 |  |  | 921 |  | 25.08 | 951 |  | 26.11 | 980 |  | 27.14 |  |  | 1008 |  | 28.19 |  |  | 1035 |  |  | 29.24 |  |  | 1061 |  | 30.29 |  |  | 1086 |  | 31.35 | 1111 |  | 32.42 | 1135 |  | 33.49
25000 | 924 |  | 26.67 |  |  | 954 |  | 27.71 | 983 |  | 28.76 | 1011 |  | 29.82 |  |  | 1038 |  | 30.89 |  |  | 1065 |  |  | 31.96 |  |  | 1090 |  | 33.04 |  |  | 1115 |  | 34.12 | 1139 |  | 35.21 | 1163 |  | 36.31
26000 | 958 |  | 29.45 |  |  | 987 |  | 30.51 | 1016 |  | 31.59 | 1043 |  | 32.67 |  |  | 1069 |  | 33.76 |  |  | 1095 |  |  | 34.85 |  |  | 1120 |  | 35.95 |  |  | 1144 |  | 37.06 | 1168 |  | 38.17 | 1191 |  | 39.29
27000 | 993 |  | 32.4 |  |  | 1021 |  | 33.49 | 1048 |  | 34.58 | 1075 |  | 35.69 |  |  | 1101 |  | 36.8 |  |  | 1126 |  |  | 37.92 |  |  | 1150 |  | 39.04 |  |  | 1174 |  | 40.17 | 1197 |  | 41.3 | — |  | —
50A4,A5,A8,A9 060 (60 TONS) (cont)
Airflow (Cfm) | Available External Static Pressure (in. wg)
| 2.2 |  |  |  |  | 2.4 |  |  | 2.6 |  |  | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2 | [5 empty] | 3.4 |  |  |  |  | 3.6 |  |  | 3.8 |  |  | 4
| rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp | rpm |  | bhp | rpm |  | bhp
12000 | 870 |  | 12.33 |  |  | 898 |  | 13.22 | 925 |  | 14.13 | 951 |  | 15.06 |  |  | 977 |  | 16 |  |  | 1002 |  |  | 16.96 |  |  | 1026 |  | 17.92 |  |  | 1049 |  | 18.9 | 1072 |  | 19.89 | 1094 |  | 20.89
14000 | 912 |  | 14.67 |  |  | 939 |  | 15.59 | 965 |  | 16.52 | 991 |  | 17.47 |  |  | 1016 |  | 18.44 |  |  | 1040 |  |  | 19.42 |  |  | 1063 |  | 20.41 |  |  | 1086 |  | 21.41 | 1109 |  | 22.43 | 1131 |  | 23.46
15000 | 934 |  | 16.02 |  |  | 961 |  | 16.96 | 987 |  | 17.9 | 1012 |  | 18.87 |  |  | 1036 |  | 19.84 |  |  | 1060 |  |  | 20.83 |  |  | 1083 |  | 21.84 |  |  | 1106 |  | 22.85 | 1128 |  | 23.88 | 1150 |  | 24.92
16000 | 957 |  | 17.51 |  |  | 983 |  | 18.46 | 1008 |  | 19.42 | 1033 |  | 20.39 |  |  | 1057 |  | 21.38 |  |  | 1081 |  |  | 22.39 |  |  | 1104 |  | 23.4 |  |  | 1126 |  | 24.43 | 1148 |  | 25.47 | 1170 |  | 26.52
17000 | 980 |  | 19.13 |  |  | 1006 |  | 20.1 | 1031 |  | 21.07 | 1055 |  | 22.06 |  |  | 1079 |  | 23.06 |  |  | 1102 |  |  | 24.07 |  |  | 1125 |  | 25.1 |  |  | 1147 |  | 26.14 | 1169 |  | 27.19 | 1190 |  | 28.26
18000 | 1004 |  | 20.89 |  |  | 1029 |  | 21.87 | 1054 |  | 22.86 | 1078 |  | 23.86 |  |  | 1101 |  | 24.88 |  |  | 1124 |  |  | 25.91 |  |  | 1147 |  | 26.94 |  |  | 1169 |  | 28 | 1190 |  | 29.06 | — |  | —
19000 | 1028 |  | 22.8 |  |  | 1053 |  | 23.79 | 1078 |  | 24.8 | 1101 |  | 25.81 |  |  | 1124 |  | 26.84 |  |  | 1147 |  |  | 27.89 |  |  | 1169 |  | 28.94 |  |  | 1190 |  | 30 | — |  | — | — |  | —
20000 | 1053 |  | 24.85 |  |  | 1078 |  | 25.86 | 1102 |  | 26.88 | 1125 |  | 27.91 |  |  | 1148 |  | 28.96 |  |  | 1170 |  |  | 30.01 |  |  | 1192 |  | 31.08 |  |  | — |  | — | — |  | — | — |  | —
21000 | 1079 |  | 27.04 |  |  | 1103 |  | 28.07 | 1126 |  | 29.11 | 1149 |  | 30.16 |  |  | 1172 |  | 31.22 |  |  | 1194 |  |  | 32.3 |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
22000 | 1105 |  | 29.39 |  |  | 1129 |  | 30.44 | 1152 |  | 31.5 | 1174 |  | 32.57 |  |  | 1196 |  | 33.65 |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
23000 | 1131 |  | 31.9 |  |  | 1155 |  | 32.97 | 1177 |  | 34.05 | 1199 |  | 35.13 |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
24000 | 1158 |  | 34.57 |  |  | 1181 |  | 35.66 | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
25000 | 1186 |  | 37.41 |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
26000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
27000 | — |  | — |  |  | — |  | — | — |  | — | — |  | — |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  | — | — |  | — | — |  | —
LEGEND Bhp — Brake Horsepower | [21 empty] | 2. Conversion — Bhp to watts: Bhp x 746
NOTES: 1. Fan performance is based on wet coils, economizer, roof curb, cabinet
[18 empty] | Watts = | [7 empty] | Motor efficiency
losses, and clean 2-in. filters. | [6 empty] | 3. VAV units with variable capacity compressor can operate down to 100 cfm/ton. VAV units with standard scroll compressor or Humidi-MiZer are limited to 200 cfm/ton. Operation may be additionally limited by entering coil conditions.
48/50A020-050 (20 to 50 Tons) | [7 empty] | Fan Performance — Standard and Modulating Power Exhaust 48/50A060 (60 Tons)
Airflow (Cfm) |  | 208 V | [7 empty] | 230, 460, 575 V | [10 empty] | Airflow (Cfm) | [5 empty] | 208 V | [8 empty] | 230, 460, 575 V
|  | ESP |  |  | Bhp |  |  | Watts |  | ESP |  | Bhp |  |  | Watts | [11 empty] | ESP |  |  |  | Bhp |  |  | Watts |  | ESP |  | Bhp |  | Watts
7700 |  | 0.6 |  |  | 3.69 |  |  | 4140 |  | 0.73 |  | 3.98 |  |  | 4460 | [5 empty] | 11550 | [5 empty] | 0.6 |  |  |  | 5.54 |  |  | 6210 |  | 0.73 |  | 5.97 |  | 6690
7900 |  | 0.56 |  |  | 3.74 |  |  | 4190 |  | 0.69 |  | 4.02 |  |  | 4510 | [5 empty] | 11850 | [5 empty] | 0.56 |  |  |  | 5.61 |  |  | 6285 |  | 0.69 |  | 6.03 |  | 6765
8100 |  | 0.51 |  |  | 3.78 |  |  | 4240 |  | 0.65 |  | 4.07 |  |  | 4560 | [5 empty] | 12150 | [5 empty] | 0.51 |  |  |  | 5.67 |  |  | 6360 |  | 0.65 |  | 6.1 |  | 6840
8500 |  | 0.41 |  |  | 3.83 |  |  | 4290 |  | 0.56 |  | 4.12 |  |  | 4620 | [5 empty] | 12750 | [5 empty] | 0.41 |  |  |  | 5.74 |  |  | 6435 |  | 0.56 |  | 6.18 |  | 6930
8900 |  | 0.31 |  |  | 3.93 |  |  | 4410 |  | 0.47 |  | 4.23 |  |  | 4740 | [5 empty] | 13350 | [5 empty] | 0.31 |  |  |  | 5.9 |  |  | 6615 |  | 0.47 |  | 6.34 |  | 7110
9300 |  | 0.2 |  |  | 4.07 |  |  | 4560 |  | 0.37 |  | 4.37 |  |  | 4900 | [5 empty] | 13950 | [5 empty] | 0.2 |  |  |  | 6.1 |  |  | 6840 |  | 0.37 |  | 6.56 |  | 7350
9700 |  | 0.11 |  |  | 4.17 |  |  | 4670 |  | 0.3 |  | 4.47 |  |  | 5010 | [5 empty] | 14550 | [5 empty] | 0.11 |  |  |  | 6.25 |  |  | 7005 |  | 0.3 |  | 6.7 |  | 7515
10100 |  | 0.04 |  |  | 4.25 |  |  | 4770 |  | 0.23 |  | 4.56 |  |  | 5110 | [5 empty] | 15150 | [5 empty] | 0.04 |  |  |  | 6.38 |  |  | 7155 |  | 0.23 |  | 6.84 |  | 7665
10500 |  | — |  |  | — |  |  | — |  | 0.17 |  | 4.66 |  |  | 5220 | [5 empty] | 15750 | [5 empty] | — |  |  |  | — |  |  | — |  | 0.17 |  | 6.98 |  | 7830
10900 |  | — |  |  | — |  |  | — |  | 0.12 |  | 4.75 |  |  | 5330 | [5 empty] | 16350 | [5 empty] | — |  |  |  | — |  |  | — |  | 0.12 |  | 7.13 |  | 7995
11300 |  | — |  |  | — |  |  | — |  | 0.07 |  | 4.8 |  |  | 5380 | [5 empty] | 16950 | [5 empty] | — |  |  |  | — |  |  | — |  | 0.07 |  | 7.2 |  | 8070
11700 |  | — |  |  | — |  |  | — |  | 0.04 |  | 4.83 |  |  | 5420 | [5 empty] | 17550 | [5 empty] | — |  |  |  | — |  |  | — |  | 0.04 |  | 7.25 |  | 8130
LEGEND Bhp — Brake Horsepower ESP — External Static Pressure (in. wg) Watts — Input Watts to Motor
High Capacity Power Exhaust Accessory
PART NO. |  |  |  |  | VOLTAGE | [6 empty] | CFM PERFORMANCE VS. STATIC PRESSURE | [21 empty] | TOTAL AMPS |  | NOISE (dB)
[12 empty] | 1/4 in. |  |  |  |  | 3/8 in. | [5 empty] | 1/2 in. | [5 empty] | 5/8 in. | [6 empty] | at 1 foot |  |  | at 10 foot
Single Module
CRPWREXH071A00 |  |  |  |  | 230V/3PH | [6 empty] | 9817 |  |  |  |  | 9631 | [5 empty] | 9591 | [5 empty] | 8964 |  |  |  |  | 12.8 |  | 88 |  |  | 77
CRPWREXH072A00 |  |  |  |  | 460V/3PH | [28 empty] | 6.4
CRPWREXH073A00 |  |  |  |  | 575V/3PH | [28 empty] | 4.8
Two Module
CRPWREXH074A00 |  |  |  |  | 230V/3PH | [6 empty] | 19634 |  |  |  |  | 19262 | [5 empty] | 19182 | [5 empty] | 17928 |  |  |  |  | 25.6 |  | 88 |  |  | 77
CRPWREXH075A00 |  |  |  |  | 460V/3PH | [28 empty] | 12.8
CRPWREXH076A00 |  |  |  |  | 575V/3PH | [28 empty] | 9.6
Three Module
CRPWREXH077A00 |  |  |  |  | 230V/3PH | [6 empty] | 29451 |  |  |  |  | 28893 | [5 empty] | 28773 | [5 empty] | 26892 |  |  |  |  | 38.4 |  | 88 |  |  | 77
CRPWREXH078A00 |  |  |  |  | 460V/3PH | [28 empty] | 19.2
CRPWREXH079A00 |  |  |  |  | 575V/3PH | [28 empty] | 14.4
Humidi-Mizer System Component Pressure Drops (in. wg) Size 020-035 Units
COMPONENT |  |  |  | AIRFLOW (cfm)
|  |  |  | 4000 | [5 empty] | 6000 | [5 empty] | 8000 | [7 empty] | 10000 | [7 empty] | 12000 |  |  |  |  | 14000
HUMIDI-MIZER |  |  |  | 0.012 | [5 empty] | 0.022 | [5 empty] | 0.035 | [7 empty] | 0.05 | [7 empty] | 0.068 |  |  |  |  | 0.089
Humidi-Mizer System Component Pressure Drops (in. wg) Size 040,050 Units
COMPONENT |  |  |  | AIRFLOW (cfm)
|  |  |  | 8000 |  |  |  |  | 10000 |  |  |  | 12000 | [6 empty] | 14000 | [6 empty] | 16000 | [6 empty] | 18000 |  |  |  | 20000
HUMIDI-MIZER |  |  |  | 0.035 |  |  |  |  | 0.05 |  |  |  | 0.068 | [6 empty] | 0.089 | [6 empty] | 0.112 | [6 empty] | 0.137 |  |  |  | 0.165
Humidi-Mizer System Component Pressure Drops (in. wg) Size 060 Units
COMPONENT |  |  |  | AIRFLOW (cfm)
|  |  |  | 12000 |  |  |  |  | 14000 |  |  |  | 16000 | [6 empty] | 18000 | [6 empty] | 20000 | [6 empty] | 22000 |  |  |  | 24000
HUMIDI-MIZER |  |  |  | 0.002 |  |  |  |  | 0.004 |  |  |  | 0.01 | [6 empty] | 0.023 | [6 empty] | 0.044 | [6 empty] | 0.077 |  |  |  | 0.125