## Table 1
Performance data (cont)
Fan Performance — 48P 030 and 50P2,P3,P6,P7 030 Units without Discharge Plenum*
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [7 empty] | 0.6 | [5 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  | rpm |  |  |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
6,000 7,500 |  | 222 248 |  |  |  |  | 0.59 0.94 |  |  |  | 284 300 |  |  |  | 0.91 1.28 |  |  |  | 339 350 |  |  | 1.27 1.68 |  |  | 388 395 |  |  |  | 1.66 2.11 |  |  |  | 430 437 |  | 2.07 2.57 |  |  |  |  | 469 475 |  |  | 2.50 3.05 |  |  | 504 511 |  | 2.93 3.54 |  | 536 544 |  | 3.38 4.05
9000 |  | 278 |  |  |  |  | 1.46 |  |  |  | 323 |  |  |  | 1.8 |  |  |  | 366 |  |  | 2.22 |  |  | 407 |  |  |  | 2.69 |  |  |  | 446 |  | 3.19 |  |  |  |  | 483 |  |  | 3.71 |  |  | 517 |  | 4.25 |  | 550 |  | 4.81
10500 |  | 311 |  |  |  |  | 2.16 |  |  |  | 349 |  |  |  | 2.52 |  |  |  | 387 |  |  | 2.95 |  |  | 424 |  |  |  | 3.43 |  |  |  | 459 |  | 3.96 |  |  |  |  | 493 |  |  | 4.51 |  |  | 526 |  | 5.1 |  | 558 |  | 5.7
12000 |  | 344 |  |  |  |  | 3.08 |  |  |  | 378 |  |  |  | 3.44 |  |  |  | 412 |  |  | 3.89 |  |  | 445 |  |  |  | 4.39 |  |  |  | 477 |  | 4.93 |  |  |  |  | 508 |  |  | 5.51 |  |  | 539 |  | 6.12 |  | 569 |  | 6.75
13500 |  | 379 |  |  |  |  | 4.25 |  |  |  | 410 |  |  |  | 4.62 |  |  |  | 440 |  |  | 5.07 |  |  | 469 |  |  |  | 5.58 |  |  |  | 498 |  | 6.13 |  |  |  |  | 527 |  |  | 6.73 |  |  | 555 |  | 7.36 |  | 583 |  | 8.02
15000 |  | 415 |  |  |  |  | 5.69 |  |  |  | 442 |  |  |  | 6.06 |  |  |  | 470 |  |  | 6.52 |  |  | 496 |  |  |  | 7.04 |  |  |  | 523 |  | 7.61 |  |  |  |  | 549 |  |  | 8.22 |  |  | 575 |  | 8.87 |  | 601 |  | 9.55
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [7 empty] | 2.2 | [5 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
6,000 7,500 |  | 567 575 |  |  |  |  | 3.84 4.57 |  |  |  | 595 604 |  |  |  | 4.30 5.10 |  |  |  | 622 632 |  |  | 4.78 5.63 |  |  | 647 658 |  |  |  | 5.26 6.18 |  |  |  | 671 683 |  | 5.75 6.73 |  |  |  |  | 695 707 |  |  | 6.25 7.29 |  |  | 717 730 |  | 6.76 7.86 |  | 738 752 |  | 7.27 8.43
9000 |  | 581 |  |  |  |  | 5.38 |  |  |  | 611 |  |  |  | 5.97 |  |  |  | 639 |  |  | 6.56 |  |  | 665 |  |  |  | 7.16 |  |  |  | 691 |  | 7.78 |  |  |  |  | 715 |  |  | 8.4 |  |  | 739 |  | 9.03 |  | 761 |  | 9.66
10500 |  | 588 |  |  |  |  | 6.31 |  |  |  | 617 |  |  |  | 6.95 |  |  |  | 645 |  |  | 7.59 |  |  | 672 |  |  |  | 8.25 |  |  |  | 697 |  | 8.92 |  |  |  |  | 722 |  |  | 9.59 |  |  | 746 |  | 10.28 |  | 769 |  | 10.97
12000 |  | 598 |  |  |  |  | 7.41 |  |  |  | 625 |  |  |  | 8.08 |  |  |  | 652 |  |  | 8.77 |  |  | 679 |  |  |  | 9.47 |  |  |  | 704 |  | 10.19 |  |  |  |  | 728 |  |  | 10.91 |  |  | 752 |  | 11.65 |  | 775 |  | 12.39
13500 |  | 610 |  |  |  |  | 8.71 |  |  |  | 637 |  |  |  | 9.41 |  |  |  | 662 |  |  | 10.14 |  |  | 687 |  |  |  | 10.88 |  |  |  | 712 |  | 11.63 |  |  |  |  | 736 |  |  | 12.4 |  |  | 759 |  | 13.18 |  | 782 |  | 13.98
15000 |  | 626 |  |  |  |  | 10.25 |  |  |  | 651 |  |  |  | 10.98 |  |  |  | 675 |  |  | 11.74 |  |  | 699 |  |  |  | 12.51 |  |  |  | 723 |  | 13.3 |  |  |  |  | 746 |  |  | 14.1 |  |  | 768 |  | 14.92 |  | 790 |  | 15.75
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [7 empty] | 3.8 | [5 empty] | 4
|  | rpm |  |  |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  | rpm |  |  |  | bhp
6,000 7,500 |  | 759 773 |  |  |  |  | 7.79 9.01 |  |  |  | 779 794 |  |  |  | 8.32 9.60 |  |  |  | 799 814 |  |  | 8.85 10.20 |  |  | 817 833 |  |  |  | 9.39 10.80
9000 |  | 783 |  |  |  |  | 10.3 |  |  |  | 805 |  |  |  | 10.95 |  |  |  | 825 |  |  | 11.6 |  |  | 845 |  |  |  | 12.26
10500 |  | 791 |  |  |  |  | 11.67 |  |  |  | 812 |  |  |  | 12.38 |  |  |  | 833 |  |  | 13.09 |  |  | 854 |  |  |  | 13.81
12000 |  | 797 |  |  |  |  | 13.15 |  |  |  | 819 |  |  |  | 13.91 |  |  |  | 840 |  |  | 14.68 |  |  | 860 |  |  |  | 15.45
13500 |  | 804 |  |  |  |  | 14.77 |  |  |  | 825 |  |  |  | 15.59 |  |  |  | 846 |  |  | 16.41 |  |  | 867 |  |  |  | 17.23
15000 |  | 812 |  |  |  |  | 16.59 |  |  |  | 833 |  |  |  | 17.45 |  |  |  | 853 |  |  | 18.31 |  |  | 874 |  |  |  | 19.19
LEGEND | [10 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 48P 035 and 50P2,P3,P6,P7 035 Units without Discharge Plenum*
AIRFLOW (cfm) |  |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  |  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [5 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  |  | rpm |  |  |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  |  |  |  | bhp |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  | bhp |  | rpm |  | bhp
7000 |  |  | 246 |  |  |  |  | 0.84 |  |  |  | 301 |  |  |  | 1.19 |  |  | 352 |  |  | 1.58 |  |  | 398 |  |  |  |  | 2.01 |  |  | 440 |  |  | 2.46 |  |  |  | 479 |  |  |  | 2.93 |  | 514 |  | 3.4 |  | 547 |  | 3.9
8000 |  |  | 266 |  |  |  |  | 1.14 |  |  |  | 315 |  |  |  | 1.5 |  |  | 362 |  |  | 1.92 |  |  | 406 |  |  |  |  | 2.37 |  |  | 447 |  |  | 2.85 |  |  |  | 484 |  |  |  | 3.35 |  | 519 |  | 3.87 |  | 552 |  | 4.39
10000 |  |  | 310 |  |  |  |  | 1.98 |  |  |  | 350 |  |  |  | 2.36 |  |  | 389 |  |  | 2.8 |  |  | 427 |  |  |  |  | 3.3 |  |  | 464 |  |  | 3.83 |  |  |  | 499 |  |  |  | 4.38 |  | 532 |  | 4.96 |  | 564 |  | 5.55
12000 |  |  | 357 |  |  |  |  | 3.2 |  |  |  | 390 |  |  |  | 3.6 |  |  | 424 |  |  | 4.06 |  |  | 457 |  |  |  |  | 4.58 |  |  | 489 |  |  | 5.15 |  |  |  | 520 |  |  |  | 5.74 |  | 551 |  | 6.36 |  | 580 |  | 7.01
14000 |  |  | 406 |  |  |  |  | 4.87 |  |  |  | 435 |  |  |  | 5.28 |  |  | 463 |  |  | 5.76 |  |  | 492 |  |  |  |  | 6.3 |  |  | 520 |  |  | 6.89 |  |  |  | 548 |  |  |  | 7.52 |  | 576 |  | 8.18 |  | 603 |  | 8.86
15000 |  |  | 430 |  |  |  |  | 5.89 |  |  |  | 458 |  |  |  | 6.31 |  |  | 485 |  |  | 6.8 |  |  | 511 |  |  |  |  | 7.35 |  |  | 538 |  |  | 7.95 |  |  |  | 564 |  |  |  | 8.59 |  | 590 |  | 9.26 |  | 616 |  | 9.96
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
7000 |  | 577 |  |  |  | 4.4 |  |  |  |  | 606 |  |  | 4.91 |  |  |  | 633 |  |  | 5.43 |  |  |  | 659 |  |  |  | 5.95 |  |  |  | 684 |  | 6.49 |  |  |  |  | 707 |  |  | 7.03 |  |  | 730 |  | 7.58 |  | 752 |  | 8.14
8000 |  | 583 |  |  |  | 4.94 |  |  |  |  | 612 |  |  | 5.49 |  |  |  | 640 |  |  | 6.05 |  |  |  | 666 |  |  |  | 6.62 |  |  |  | 691 |  | 7.19 |  |  |  |  | 715 |  |  | 7.78 |  |  | 738 |  | 8.37 |  | 760 |  | 8.97
10000 |  | 594 |  |  |  | 6.16 |  |  |  |  | 623 |  |  | 6.79 |  |  |  | 651 |  |  | 7.42 |  |  |  | 677 |  |  |  | 8.07 |  |  |  | 703 |  | 8.73 |  |  |  |  | 727 |  |  | 9.39 |  |  | 751 |  | 10.06 |  | 774 |  | 10.74
12000 |  | 609 |  |  |  | 7.67 |  |  |  |  | 636 |  |  | 8.36 |  |  |  | 663 |  |  | 9.05 |  |  |  | 689 |  |  |  | 9.77 |  |  |  | 714 |  | 10.49 |  |  |  |  | 738 |  |  | 11.22 |  |  | 762 |  | 11.97 |  | 785 |  | 12.72
14000 |  | 629 |  |  |  | 9.57 |  |  |  |  | 655 |  |  | 10.3 |  |  |  | 680 |  |  | 11.04 |  |  |  | 704 |  |  |  | 11.81 |  |  |  | 728 |  | 12.59 |  |  |  |  | 751 |  |  | 13.38 |  |  | 774 |  | 14.18 |  | 796 |  | 14.99
15000 |  | 641 |  |  |  | 10.69 |  |  |  |  | 666 |  |  | 11.44 |  |  |  | 690 |  |  | 12.2 |  |  |  | 714 |  |  |  | 12.99 |  |  |  | 737 |  | 13.79 |  |  |  |  | 760 |  |  | 14.61 |  |  | 782 |  | 15.44 |  | 804 |  | 16.28
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [6 empty] | 3.8 | [6 empty] | 4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
7000 |  | 773 |  |  |  | 8.7 |  |  |  |  | 793 |  |  | 9.27 |  |  |  | 813 |  |  | 9.85 |  |  |  | 832 |  |  |  | 10.43
8000 |  | 782 |  |  |  | 9.57 |  |  |  |  | 802 |  |  | 10.18 |  |  |  | 823 |  |  | 10.8 |  |  |  | 842 |  |  |  | 11.43
10000 |  | 796 |  |  |  | 11.42 |  |  |  |  | 817 |  |  | 12.11 |  |  |  | 838 |  |  | 12.81 |  |  |  | 858 |  |  |  | 13.52
12000 |  | 807 |  |  |  | 13.48 |  |  |  |  | 828 |  |  | 14.25 |  |  |  | 849 |  |  | 15.02 |  |  |  | 869 |  |  |  | 15.8
14000 |  | 818 |  |  |  | 15.82 |  |  |  |  | 840 |  |  | 16.66 |  |  |  | 860 |  |  | 17.5 |  |  |  | 880 |  |  |  | 18.35
15000 |  | 825 |  |  |  | 17.13 |  |  |  |  | 846 |  |  | 18 |  |  |  | 866 |  |  | 18.87 |  |  |  | 886 |  |  |  | 19.76
LEGEND | [10 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 48P 040 and 50P2,P3,P6,P7 040 Units without Discharge Plenum*
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
8,000 10,000 |  | 252 290 |  |  |  | 0.98 1.67 |  |  |  |  | 303 333 |  |  | 1.33 2.11 |  |  |  | 350 373 |  |  | 1.72 2.55 |  |  |  | 394 412 |  |  |  | 2.14 3.01 |  |  |  | 434 448 |  | 2.58 3.51 |  |  |  |  | 472 483 |  |  | 3.06 4.03 |  |  | 507 517 |  | 3.55 4.58 |  | 540 549 |  | 4.07 5.16
12000 |  | 330 |  |  |  | 2.65 |  |  |  |  | 369 |  |  | 3.18 |  |  |  | 404 |  |  | 3.7 |  |  |  | 438 |  |  |  | 4.23 |  |  |  | 470 |  | 4.78 |  |  |  |  | 501 |  |  | 5.35 |  |  | 532 |  | 5.94 |  | 562 |  | 6.56
14000 |  | 372 |  |  |  | 3.96 |  |  |  |  | 407 |  |  | 4.61 |  |  |  | 439 |  |  | 5.22 |  |  |  | 469 |  |  |  | 5.83 |  |  |  | 498 |  | 6.44 |  |  |  |  | 526 |  |  | 7.07 |  |  | 554 |  | 7.72 |  | 581 |  | 8.38
16000 |  | 415 |  |  |  | 5.67 |  |  |  |  | 447 |  |  | 6.44 |  |  |  | 476 |  |  | 7.15 |  |  |  | 504 |  |  |  | 7.85 |  |  |  | 530 |  | 8.54 |  |  |  |  | 556 |  |  | 9.24 |  |  | 581 |  | 9.95 |  | 605 |  | 10.67
18000 |  | 459 |  |  |  | 7.84 |  |  |  |  | 488 |  |  | 8.72 |  |  |  | 515 |  |  | 9.55 |  |  |  | 541 |  |  |  | 10.34 |  |  |  | 565 |  | 11.12 |  |  |  |  | 589 |  |  | 11.91 |  |  | 612 |  | 12.69 |  | 634 |  | 13.47
20000 |  | 503 |  |  |  | 10.51 |  |  |  |  | 530 |  |  | 11.51 |  |  |  | 555 |  |  | 12.46 |  |  |  | 579 |  |  |  | 13.36 |  |  |  | 602 |  | 14.24 |  |  |  |  | 624 |  |  | 15.11 |  |  | 645 |  | 15.98 |  | 666 |  | 16.84
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
8,000 10,000 |  | 571 579 |  |  |  | 4.60 5.75 |  |  |  |  | 600 608 |  |  | 5.14 6.36 |  |  |  | 628 636 |  |  | 5.70 6.98 |  |  |  | 654 662 |  |  |  | 6.27 7.62 |  |  |  | 679 688 |  | 6.85 8.28 |  |  |  |  | 703 712 |  |  | 7.44 8.94 |  |  | 726 736 |  | 8.04 9.62 |  | 748 758 |  | 8.65 10.30
12000 |  | 590 |  |  |  | 7.21 |  |  |  |  | 618 |  |  | 7.87 |  |  |  | 645 |  |  | 8.55 |  |  |  | 671 |  |  |  | 9.25 |  |  |  | 696 |  | 9.96 |  |  |  |  | 720 |  |  | 10.69 |  |  | 744 |  | 11.43 |  | 766 |  | 12.19
14000 |  | 607 |  |  |  | 9.07 |  |  |  |  | 633 |  |  | 9.78 |  |  |  | 658 |  |  | 10.51 |  |  |  | 683 |  |  |  | 11.25 |  |  |  | 707 |  | 12.02 |  |  |  |  | 730 |  |  | 12.8 |  |  | 753 |  | 13.6 |  | 775 |  | 14.41
16000 |  | 629 |  |  |  | 11.41 |  |  |  |  | 653 |  |  | 12.16 |  |  |  | 676 |  |  | 12.94 |  |  |  | 699 |  |  |  | 13.73 |  |  |  | 722 |  | 14.54 |  |  |  |  | 744 |  |  | 15.37 |  |  | 766 |  | 16.22 |  | 787 |  | 17.08
18000 |  | 656 |  |  |  | 14.28 |  |  |  |  | 678 |  |  | 15.09 |  |  |  | 700 |  |  | 15.91 |  |  |  | 721 |  |  |  | 16.76 |  |  |  | 742 |  | 17.62 |  |  |  |  | 762 |  |  | 18.49 |  |  | 783 |  | 19.39 |  | 803 |  | 20.29
20000 |  | 687 |  |  |  | 17.71 |  |  |  |  | 707 |  |  | 18.6 |  |  |  | 727 |  |  | 19.48 |  |  |  | 747 |  |  |  | 20.38 |  |  |  | 766 |  | 21.3 |  |  |  |  | 785 |  |  | 22.22 |  |  | 804 |  | 23.17 |  | — |  | —
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [6 empty] | 3.8 | [6 empty] | 4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
8,000 10,000 |  | 770 780 |  |  |  | 9.27 11.00 |  |  |  |  | 791 802 |  |  | 9.90 11.71 |  |  |  | 811 822 |  |  | 10.54 12.43 |  |  |  | 830 842 |  |  |  | 11.18 13.15
12000 |  | 789 |  |  |  | 12.96 |  |  |  |  | 810 |  |  | 13.73 |  |  |  | 831 |  |  | 14.52 |  |  |  | 851 |  |  |  | 15.32
14000 |  | 797 |  |  |  | 15.24 |  |  |  |  | 818 |  |  | 16.07 |  |  |  | 839 |  |  | 16.93 |  |  |  | 859 |  |  |  | 17.79
16000 |  | 808 |  |  |  | 17.95 |  |  |  |  | 828 |  |  | 18.85 |  |  |  | 849 |  |  | 19.75 |  |  |  | 868 |  |  |  | 20.67
18000 |  | 823 |  |  |  | 21.21 |  |  |  |  | 842 |  |  | 22.15 |  |  |  | 862 |  |  | 23.11 |  |  |  | — |  |  |  | —
20000 |  | — |  |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
LEGEND | [10 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 48P 050 and 50P2,P3,P6,P7 050 Units without Discharge Plenum*
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
9000 |  | 276 |  |  |  | 1.34 |  |  |  |  | 323 |  |  | 1.73 |  |  |  | 366 |  |  | 2.15 |  |  |  | 407 |  |  |  | 2.6 |  |  |  | 445 |  | 3.08 |  |  |  |  | 482 |  |  | 3.58 |  |  | 516 |  | 4.11 |  | 549 |  | 4.66
10000 |  | 296 |  |  |  | 1.74 |  |  |  |  | 339 |  |  | 2.17 |  |  |  | 379 |  |  | 2.62 |  |  |  | 418 |  |  |  | 3.09 |  |  |  | 454 |  | 3.59 |  |  |  |  | 489 |  |  | 4.12 |  |  | 522 |  | 4.68 |  | 554 |  | 5.26
12000 |  | 339 |  |  |  | 2.76 |  |  |  |  | 376 |  |  | 3.29 |  |  |  | 411 |  |  | 3.81 |  |  |  | 445 |  |  |  | 4.35 |  |  |  | 477 |  | 4.91 |  |  |  |  | 509 |  |  | 5.49 |  |  | 539 |  | 6.09 |  | 568 |  | 6.71
14000 |  | 382 |  |  |  | 4.15 |  |  |  |  | 416 |  |  | 4.79 |  |  |  | 448 |  |  | 5.4 |  |  |  | 478 |  |  |  | 6.01 |  |  |  | 506 |  | 6.63 |  |  |  |  | 535 |  |  | 7.26 |  |  | 562 |  | 7.92 |  | 589 |  | 8.6
16000 |  | 427 |  |  |  | 5.96 |  |  |  |  | 458 |  |  | 6.71 |  |  |  | 487 |  |  | 7.42 |  |  |  | 514 |  |  |  | 8.11 |  |  |  | 540 |  | 8.81 |  |  |  |  | 565 |  |  | 9.52 |  |  | 590 |  | 10.23 |  | 615 |  | 10.97
18000 |  | 473 |  |  |  | 8.26 |  |  |  |  | 501 |  |  | 9.12 |  |  |  | 527 |  |  | 9.93 |  |  |  | 552 |  |  |  | 10.72 |  |  |  | 576 |  | 11.5 |  |  |  |  | 600 |  |  | 12.29 |  |  | 623 |  | 13.08 |  | 645 |  | 13.88
20000 |  | 519 |  |  |  | 11.1 |  |  |  |  | 545 |  |  | 12.06 |  |  |  | 570 |  |  | 12.99 |  |  |  | 593 |  |  |  | 13.88 |  |  |  | 615 |  | 14.76 |  |  |  |  | 637 |  |  | 15.63 |  |  | 658 |  | 16.5 |  | 679 |  | 17.38
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
9000 |  | 579 |  |  |  | 5.23 |  |  |  |  | 608 |  |  | 5.81 |  |  |  | 636 |  |  | 6.41 |  |  |  | 662 |  |  |  | 7.02 |  |  |  | 687 |  | 7.64 |  |  |  |  | 712 |  |  | 8.27 |  |  | 735 |  | 8.91 |  | 757 |  | 9.57
10000 |  | 584 |  |  |  | 5.85 |  |  |  |  | 613 |  |  | 6.47 |  |  |  | 641 |  |  | 7.1 |  |  |  | 667 |  |  |  | 7.74 |  |  |  | 692 |  | 8.4 |  |  |  |  | 717 |  |  | 9.07 |  |  | 740 |  | 9.75 |  | 763 |  | 10.44
12000 |  | 597 |  |  |  | 7.36 |  |  |  |  | 625 |  |  | 8.03 |  |  |  | 651 |  |  | 8.72 |  |  |  | 677 |  |  |  | 9.42 |  |  |  | 702 |  | 10.14 |  |  |  |  | 726 |  |  | 10.88 |  |  | 750 |  | 11.63 |  | 772 |  | 12.39
14000 |  | 615 |  |  |  | 9.29 |  |  |  |  | 641 |  |  | 10.01 |  |  |  | 666 |  |  | 10.74 |  |  |  | 690 |  |  |  | 11.5 |  |  |  | 714 |  | 12.27 |  |  |  |  | 738 |  |  | 13.06 |  |  | 760 |  | 13.87 |  | 783 |  | 14.69
16000 |  | 639 |  |  |  | 11.71 |  |  |  |  | 663 |  |  | 12.48 |  |  |  | 686 |  |  | 13.27 |  |  |  | 709 |  |  |  | 14.07 |  |  |  | 731 |  | 14.89 |  |  |  |  | 753 |  |  | 15.73 |  |  | 775 |  | 16.58 |  | 796 |  | 17.45
18000 |  | 667 |  |  |  | 14.69 |  |  |  |  | 689 |  |  | 15.51 |  |  |  | 711 |  |  | 16.35 |  |  |  | 732 |  |  |  | 17.2 |  |  |  | 753 |  | 18.07 |  |  |  |  | 773 |  |  | 18.96 |  |  | 793 |  | 19.86 |  | 813 |  | 20.78
20000 |  | 699 |  |  |  | 18.25 |  |  |  |  | 719 |  |  | 19.14 |  |  |  | 739 |  |  | 20.04 |  |  |  | 759 |  |  |  | 20.95 |  |  |  | 778 |  | 21.88 |  |  |  |  | 797 |  |  | 22.82 |  |  | 816 |  | 23.77 |  | — |  | —
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [6 empty] | 3.8 | [6 empty] | 4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
9000 |  | 779 |  |  |  | 10.23 |  |  |  |  | 800 |  |  | 10.9 |  |  |  | 821 |  |  | 11.58 |  |  |  | 840 |  |  |  | 12.27
10000 |  | 785 |  |  |  | 11.14 |  |  |  |  | 806 |  |  | 11.85 |  |  |  | 826 |  |  | 12.57 |  |  |  | 846 |  |  |  | 13.3
12000 |  | 794 |  |  |  | 13.16 |  |  |  |  | 816 |  |  | 13.94 |  |  |  | 836 |  |  | 14.73 |  |  |  | 857 |  |  |  | 15.54
14000 |  | 804 |  |  |  | 15.52 |  |  |  |  | 825 |  |  | 16.37 |  |  |  | 846 |  |  | 17.22 |  |  |  | 866 |  |  |  | 18.1
16000 |  | 817 |  |  |  | 18.34 |  |  |  |  | 837 |  |  | 19.24 |  |  |  | 857 |  |  | 20.15 |  |  |  | 877 |  |  |  | 21.08
18000 |  | 833 |  |  |  | 21.71 |  |  |  |  | 853 |  |  | 22.66 |  |  |  | 872 |  |  | 23.62 |  |  |  | — |  |  |  | —
20000 |  | — |  |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
LEGEND | [10 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 48P 055 and 50P2,P3,P6,P7 055 Units without Discharge Plenum*
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [7 empty] | 0.4 | [7 empty] | 0.6 | [6 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
10,000 12,500 |  | 207 235 |  |  |  | 1.04 1.69 |  |  |  | 253 276 |  |  | 1.50 2.23 |  |  |  |  | 295 312 |  |  | 2.03 2.78 |  |  |  | 334 346 |  |  | 2.66 3.40 |  |  |  |  | 371 379 |  | 3.41 4.10 |  |  |  |  | 405 410 |  |  | 4.26 4.88 |  |  | 438 440 |  | 5.20 5.75 |  | 468 469 |  | 6.20 6.70
15000 |  | 265 |  |  |  | 2.59 |  |  |  | 302 |  |  | 3.23 |  |  |  |  | 335 |  |  | 3.85 |  |  |  | 365 |  |  | 4.51 |  |  |  |  | 394 |  | 5.2 |  |  |  |  | 422 |  |  | 5.96 |  |  | 449 |  | 6.78 |  | 476 |  | 7.67
17500 |  | 295 |  |  |  | 3.78 |  |  |  | 331 |  |  | 4.52 |  |  |  |  | 361 |  |  | 5.24 |  |  |  | 389 |  |  | 5.97 |  |  |  |  | 415 |  | 6.71 |  |  |  |  | 440 |  |  | 7.48 |  |  | 465 |  | 8.3 |  | 489 |  | 9.17
20000 |  | 327 |  |  |  | 5.31 |  |  |  | 360 |  |  | 6.15 |  |  |  |  | 388 |  |  | 6.98 |  |  |  | 414 |  |  | 7.79 |  |  |  |  | 439 |  | 8.6 |  |  |  |  | 462 |  |  | 9.43 |  |  | 485 |  | 10.28 |  | 507 |  | 11.17
22500 |  | 359 |  |  |  | 7.23 |  |  |  | 390 |  |  | 8.16 |  |  |  |  | 417 |  |  | 9.09 |  |  |  | 442 |  |  | 10 |  |  |  |  | 465 |  | 10.9 |  |  |  |  | 487 |  |  | 11.81 |  |  | 508 |  | 12.72 |  | 528 |  | 13.65
25000 |  | 392 |  |  |  | 9.59 |  |  |  | 421 |  |  | 10.6 |  |  |  |  | 447 |  |  | 11.62 |  |  |  | 470 |  |  | 12.64 |  |  |  |  | 492 |  | 13.64 |  |  |  |  | 513 |  |  | 14.63 |  |  | 533 |  | 15.62 |  | 552 |  | 16.62
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
10,000 12,500 |  | 497 497 |  |  |  | 7.27 7.73 |  |  |  |  | 523 523 |  |  | 8.39 8.83 |  |  |  | 549 549 |  |  | 9.55 10.00 |  |  |  | 573 573 |  |  |  | 10.75 11.22 |  |  |  | 596 597 |  | 11.98 12.49 |  |  |  |  | 618 619 |  |  | 13.23 13.81 |  |  | 639 641 |  | 14.51 15.16 |  | 659 662 |  | 15.81 16.55
15000 |  | 501 |  |  |  | 8.63 |  |  |  |  | 526 |  |  | 9.67 |  |  |  | 550 |  |  | 10.77 |  |  |  | 574 |  |  |  | 11.94 |  |  |  | 597 |  | 13.17 |  |  |  |  | 619 |  |  | 14.46 |  |  | 641 |  | 15.8 |  | 662 |  | 17.19
17500 |  | 512 |  |  |  | 10.09 |  |  |  |  | 535 |  |  | 11.07 |  |  |  | 557 |  |  | 12.11 |  |  |  | 579 |  |  |  | 13.21 |  |  |  | 601 |  | 14.38 |  |  |  |  | 622 |  |  | 15.6 |  |  | 643 |  | 16.88 |  | 663 |  | 18.21
20000 |  | 528 |  |  |  | 12.09 |  |  |  |  | 549 |  |  | 13.06 |  |  |  | 570 |  |  | 14.07 |  |  |  | 590 |  |  |  | 15.12 |  |  |  | 610 |  | 16.24 |  |  |  |  | 630 |  |  | 17.4 |  |  | 649 |  | 18.62 |  | 668 |  | 19.89
22500 |  | 548 |  |  |  | 14.6 |  |  |  |  | 567 |  |  | 15.59 |  |  |  | 587 |  |  | 16.61 |  |  |  | 605 |  |  |  | 17.66 |  |  |  | 624 |  | 18.75 |  |  |  |  | 642 |  |  | 19.88 |  |  | 660 |  | 21.06 |  | 678 |  | 22.28
25000 |  | 571 |  |  |  | 17.63 |  |  |  |  | 589 |  |  | 18.66 |  |  |  | 607 |  |  | 19.71 |  |  |  | 624 |  |  |  | 20.78 |  |  |  | 642 |  | 21.89 |  |  |  |  | 659 |  |  | 23.02 |  |  | 676 |  | 24.19 |  | 692 |  | 25.39
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [7 empty] | 3.8 | [6 empty] | 4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
10,000 12,500 |  | 679 682 |  |  |  | 17.13 17.98 |  |  |  |  | 697 702 |  |  | 18.46 19.43 |  |  |  |  | 715 721 |  |  | 19.81 20.90 |  |  |  | 733 739 |  |  |  | 21.17 22.40
15000 |  | 682 |  |  |  | 18.63 |  |  |  |  | 702 |  |  | 20.1 |  |  |  |  | 721 |  |  | 21.62 |  |  |  | 740 |  |  |  | 23.17
17500 |  | 683 |  |  |  | 19.6 |  |  |  |  | 702 |  |  | 21.04 |  |  |  |  | 721 |  |  | 22.53 |  |  |  | 740 |  |  |  | 24.06
20000 |  | 687 |  |  |  | 21.2 |  |  |  |  | 706 |  |  | 22.57 |  |  |  |  | 724 |  |  | 24 |  |  |  | 742 |  |  |  | 25.46
22500 |  | 696 |  |  |  | 23.55 |  |  |  |  | 713 |  |  | 24.86 |  |  |  |  | 731 |  |  | 26.22 |  |  |  | 748 |  |  |  | 27.62
25000 |  | 709 |  |  |  | 26.62 |  |  |  |  | 725 |  |  | 27.91 |  |  |  |  | 741 |  |  | 29.22 |  |  |  | — |  |  |  | —
LEGEND | [10 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 48P 060 and 50P2,P3,P6,P7 060 Units without Discharge Plenum*
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
12,000 15,000 |  | 234 271 |  |  |  | 1.54 2.65 |  |  |  |  | 276 309 |  | 2.03 3.27 |  |  |  |  | 312 341 |  |  | 2.57 3.88 |  |  |  | 348 370 |  |  |  | 3.20 4.53 |  |  |  | 382 399 |  | 3.93 5.24 |  |  |  |  | 415 428 |  |  | 4.74 6.04 |  |  | 446 455 |  | 5.63 6.91 |  | 476 482 |  | 6.58 7.85
18000 |  | 308 |  |  |  | 4.22 |  |  |  |  | 344 |  | 5 |  |  |  |  | 374 |  |  | 5.73 |  |  |  | 400 |  |  |  | 6.46 |  |  |  | 426 |  | 7.22 |  |  |  |  | 450 |  |  | 8.02 |  |  | 474 |  | 8.88 |  | 498 |  | 9.81
21000 |  | 348 |  |  |  | 6.36 |  |  |  |  | 380 |  | 7.29 |  |  |  |  | 408 |  |  | 8.18 |  |  |  | 434 |  |  |  | 9.04 |  |  |  | 457 |  | 9.88 |  |  |  |  | 479 |  |  | 10.74 |  |  | 501 |  | 11.64 |  | 522 |  | 12.58
24000 |  | 390 |  |  |  | 9.19 |  |  |  |  | 417 |  | 10.24 |  |  |  |  | 444 |  |  | 11.29 |  |  |  | 469 |  |  |  | 12.29 |  |  |  | 491 |  | 13.27 |  |  |  |  | 512 |  |  | 14.23 |  |  | 532 |  | 15.21 |  | 551 |  | 16.2
27000 |  | 433 |  |  |  | 12.8 |  |  |  |  | 456 |  | 13.93 |  |  |  |  | 481 |  |  | 15.14 |  |  |  | 504 |  |  |  | 16.3 |  |  |  | 526 |  | 17.44 |  |  |  |  | 546 |  |  | 18.53 |  |  | 565 |  | 19.62 |  | 583 |  | 20.71
30000 |  | 476 |  |  |  | 17.29 |  |  |  |  | 497 |  | 18.5 |  |  |  |  | 519 |  |  | 19.82 |  |  |  | 541 |  |  |  | 21.15 |  |  |  | 562 |  | 22.45 |  |  |  |  | 581 |  |  | 23.7 |  |  | 599 |  | 24.93 |  | 617 |  | 26.14
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
12,000 15,000 |  | 504 509 |  |  |  | 7.56 8.87 |  |  |  |  | 530 535 |  | 8.57 9.95 |  |  |  |  | 555 559 |  |  | 9.61 11.07 |  |  |  | 578 583 |  |  |  | 10.66 12.25 |  |  |  | 600 606 |  | 11.73 13.45 |  |  |  |  | 621 628 |  |  | 12.81 14.68 |  |  | 641 650 |  | 13.91 15.95 |  | 660 670 |  | 15.01 17.23
18000 |  | 521 |  |  |  | 10.79 |  |  |  |  | 544 |  | 11.85 |  |  |  |  | 567 |  |  | 12.97 |  |  |  | 590 |  |  |  | 14.14 |  |  |  | 612 |  | 15.38 |  |  |  |  | 633 |  |  | 16.66 |  |  | 654 |  | 17.99 |  | 675 |  | 19.36
21000 |  | 543 |  |  |  | 13.56 |  |  |  |  | 563 |  | 14.6 |  |  |  |  | 583 |  |  | 15.69 |  |  |  | 603 |  |  |  | 16.84 |  |  |  | 623 |  | 18.05 |  |  |  |  | 643 |  |  | 19.31 |  |  | 662 |  | 20.63 |  | 682 |  | 21.99
24000 |  | 570 |  |  |  | 17.22 |  |  |  |  | 588 |  | 18.28 |  |  |  |  | 607 |  |  | 19.39 |  |  |  | 625 |  |  |  | 20.53 |  |  |  | 642 |  | 21.72 |  |  |  |  | 660 |  |  | 22.95 |  |  | 678 |  | 24.24 |  | 695 |  | 25.58
27000 |  | 601 |  |  |  | 21.81 |  |  |  |  | 618 |  | 22.93 |  |  |  |  | 635 |  |  | 24.07 |  |  |  | 651 |  |  |  | 25.25 |  |  |  | 667 |  | 26.46 |  |  |  |  | 684 |  |  | 27.7 |  |  | 700 |  | 28.98 |  | 715 |  | 30.31
30000 |  | 634 |  |  |  | 27.34 |  |  |  |  | 650 |  | 28.56 |  |  |  |  | 666 |  |  | 29.78 |  |  |  | 681 |  |  |  | 31.02 |  |  |  | 696 |  | 32.28 |  |  |  |  | 711 |  |  | 33.56 |  |  | 726 |  | 34.88 |  | — |  | —
AIRFLOW (cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 3.4 | [8 empty] | 3.6 | [7 empty] | 3.8 | [6 empty] | 4
| rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
12,000 15,000 | 679 690 |  |  |  | 16.11 18.52 |  |  |  |  | 697 709 |  |  | 17.23 19.84 |  |  |  |  | 714 727 |  |  | 18.35 21.15 |  |  |  | 730 745 |  |  |  | 19.49 22.49
18000 | 695 |  |  |  | 20.76 |  |  |  |  | 714 |  |  | 22.2 |  |  |  |  | 733 |  |  | 23.66 |  |  |  | — |  |  |  | —
21000 | 701 |  |  |  | 23.41 |  |  |  |  | 719 |  |  | 24.87 |  |  |  |  | 738 |  |  | 26.38 |  |  |  | — |  |  |  | —
24000 | 713 |  |  |  | 26.97 |  |  |  |  | 730 |  |  | 28.4 |  |  |  |  | 747 |  |  | 29.89 |  |  |  | — |  |  |  | —
27000 | 731 |  |  |  | 31.67 |  |  |  |  | 747 |  |  | 33.08 |  |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
30000 | — |  |  |  | — |  |  |  |  | — |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
LEGEND | [10 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 48P 070 and 50P2,P3,P6,P7 070 Units without Discharge Plenum*
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
14,000 17,500 |  | 258 302 |  |  |  | 2.23 3.92 |  |  |  |  | 297 338 |  |  | 2.80 4.67 |  |  |  | 330 368 |  |  | 3.38 5.39 |  |  |  | 362 395 |  |  |  | 4.02 6.10 |  |  |  | 392 421 |  | 4.73 6.84 |  |  |  |  | 422 446 |  |  | 5.53 7.64 |  |  | 451 471 |  | 6.42 8.50 |  | 480 495 |  | 7.37 9.42
21000 |  | 348 |  |  |  | 6.36 |  |  |  |  | 380 |  |  | 7.29 |  |  |  | 408 |  |  | 8.18 |  |  |  | 434 |  |  |  | 9.04 |  |  |  | 457 |  | 9.88 |  |  |  |  | 479 |  |  | 10.74 |  |  | 501 |  | 11.64 |  | 522 |  | 12.57
24500 |  | 397 |  |  |  | 9.74 |  |  |  |  | 424 |  |  | 10.8 |  |  |  | 450 |  |  | 11.88 |  |  |  | 475 |  |  |  | 12.91 |  |  |  | 497 |  | 13.91 |  |  |  |  | 517 |  |  | 14.89 |  |  | 537 |  | 15.88 |  | 556 |  | 16.89
28000 |  | 447 |  |  |  | 14.18 |  |  |  |  | 470 |  |  | 15.35 |  |  |  | 494 |  |  | 16.6 |  |  |  | 516 |  |  |  | 17.82 |  |  |  | 538 |  | 19.01 |  |  |  |  | 558 |  |  | 20.16 |  |  | 576 |  | 21.29 |  | 594 |  | 22.41
30000 |  | 476 |  |  |  | 17.29 |  |  |  |  | 497 |  |  | 18.5 |  |  |  | 519 |  |  | 19.82 |  |  |  | 541 |  |  |  | 21.15 |  |  |  | 562 |  | 22.45 |  |  |  |  | 581 |  |  | 23.7 |  |  | 599 |  | 24.93 |  | 617 |  | 26.14
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
14,000 17,500 |  | 507 519 |  |  |  | 8.39 10.42 |  |  |  |  | 533 542 |  |  | 9.46 11.48 |  |  |  | 558 565 |  |  | 10.57 12.60 |  |  |  | 582 588 |  |  |  | 11.71 13.78 |  |  |  | 605 610 |  | 12.89 15.02 |  |  |  |  | 627 632 |  |  | 14.08 16.30 |  |  | 648 653 |  | 15.29 17.62 |  | 668 674 |  | 16.52 18.99
21000 |  | 543 |  |  |  | 13.56 |  |  |  |  | 563 |  |  | 14.6 |  |  |  | 583 |  |  | 15.69 |  |  |  | 603 |  |  |  | 16.84 |  |  |  | 623 |  | 18.05 |  |  |  |  | 643 |  |  | 19.31 |  |  | 662 |  | 20.63 |  | 682 |  | 21.99
24500 |  | 575 |  |  |  | 17.93 |  |  |  |  | 593 |  |  | 18.99 |  |  |  | 611 |  |  | 20.1 |  |  |  | 629 |  |  |  | 21.24 |  |  |  | 646 |  | 22.43 |  |  |  |  | 664 |  |  | 23.67 |  |  | 681 |  | 24.96 |  | 698 |  | 26.29
28000 |  | 612 |  |  |  | 23.55 |  |  |  |  | 628 |  |  | 24.69 |  |  |  | 645 |  |  | 25.86 |  |  |  | 661 |  |  |  | 27.05 |  |  |  | 677 |  | 28.27 |  |  |  |  | 692 |  |  | 29.53 |  |  | 708 |  | 30.82 |  | 723 |  | 32.15
30000 |  | 634 |  |  |  | 27.34 |  |  |  |  | 650 |  |  | 28.56 |  |  |  | 666 |  |  | 29.78 |  |  |  | 681 |  |  |  | 31.02 |  |  |  | 696 |  | 32.28 |  |  |  |  | 711 |  |  | 33.56 |  |  | 726 |  | 34.88 |  | — |  | —
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [7 empty] | 3.8 | [6 empty] | 4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
14,000 17,500 |  | 687 694 |  |  |  | 17.76 20.38 |  |  |  |  | 706 713 |  |  | 19.01 21.79 |  |  |  |  | 724 732 |  |  | 20.27 23.24 |  |  |  | 741 — |  |  |  | 21.54 —
21000 |  | 701 |  |  |  | 23.41 |  |  |  |  | 719 |  |  | 24.87 |  |  |  |  | 738 |  |  | 26.38 |  |  |  | — |  |  |  | —
24500 |  | 715 |  |  |  | 27.67 |  |  |  |  | 732 |  |  | 29.1 |  |  |  |  | 749 |  |  | 30.58 |  |  |  | — |  |  |  | —
28000 |  | 739 |  |  |  | 33.51 |  |  |  |  | — |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
30000 |  | — |  |  |  | — |  |  |  |  | — |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
LEGEND | [10 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 50P2,P3,P6,P7 030 Units with Discharge Plenum and 50P4,P5,P8,P9 030 Units
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [5 empty] | 0.8 | [6 empty] | 1 | [6 empty] | 1.2 | [6 empty] | 1.4 |  |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  | rpm |  |  |  | bhp |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp
6,000 7,500 |  | 255 291 |  |  |  | 0.95 1.51 |  |  |  |  | 313 340 |  |  | 1.35 1.93 |  |  |  | 364 386 |  |  | 1.82 2.41 |  |  | 411 428 |  |  |  | 2.35 2.94 |  |  | 454 468 |  |  | 2.92 3.51 |  |  |  | 494 505 |  |  |  | 3.52 4.13 |  |  | 530 541 |  | 4.14 4.78 |  |  | 563 574 |  | 4.78 5.46
9000 |  | 330 |  |  |  | 2.28 |  |  |  |  | 372 |  |  | 2.73 |  |  |  | 413 |  |  | 3.22 |  |  | 451 |  |  |  | 3.76 |  |  | 487 |  |  | 4.34 |  |  |  | 522 |  |  |  | 4.96 |  |  | 555 |  | 5.61 |  |  | 587 |  | 6.3
10500 |  | 371 |  |  |  | 3.28 |  |  |  |  | 408 |  |  | 3.76 |  |  |  | 444 |  |  | 4.28 |  |  | 479 |  |  |  | 4.84 |  |  | 512 |  |  | 5.43 |  |  |  | 544 |  |  |  | 6.06 |  |  | 574 |  | 6.71 |  |  | 604 |  | 7.4
12000 |  | 413 |  |  |  | 4.56 |  |  |  |  | 447 |  |  | 5.07 |  |  |  | 479 |  |  | 5.61 |  |  | 510 |  |  |  | 6.19 |  |  | 540 |  |  | 6.8 |  |  |  | 570 |  |  |  | 7.44 |  |  | 598 |  | 8.11 |  |  | 626 |  | 8.8
13500 |  | 456 |  |  |  | 6.12 |  |  |  |  | 487 |  |  | 6.66 |  |  |  | 516 |  |  | 7.23 |  |  | 544 |  |  |  | 7.83 |  |  | 572 |  |  | 8.46 |  |  |  | 599 |  |  |  | 9.12 |  |  | 626 |  | 9.81 |  |  | 651 |  | 10.51
15000 |  | 500 |  |  |  | 7.99 |  |  |  |  | 528 |  |  | 8.58 |  |  |  | 555 |  |  | 9.18 |  |  | 581 |  |  |  | 9.8 |  |  | 606 |  |  | 10.45 |  |  |  | 631 |  |  |  | 11.13 |  |  | 656 |  | 11.83 |  |  | 680 |  | 12.56
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm | bhp |  |  | rpm |  | bhp
6,000 7,500 |  | 594 605 |  |  |  | 5.43 6.16 |  |  |  |  | 623 635 |  |  | 6.09 6.88 |  |  |  | 651 664 |  |  | 6.75 7.62 |  |  |  | 676 691 |  |  |  | 7.41 8.36 |  |  |  | 701 716 |  | 8.08 9.11 |  |  |  |  | 725 741 |  |  | 8.75 9.88 |  |  | 747 765 | 9.42 10.64 |  |  | 769 787 |  | 10.10 11.41
9000 |  | 617 |  |  |  | 7.02 |  |  |  |  | 646 |  |  | 7.76 |  |  |  | 674 |  |  | 8.52 |  |  |  | 702 |  |  |  | 9.31 |  |  |  | 728 |  | 10.11 |  |  |  |  | 753 |  |  | 10.93 |  |  | 777 | 11.76 |  |  | 800 |  | 12.6
10500 |  | 633 |  |  |  | 8.12 |  |  |  |  | 660 |  |  | 8.86 |  |  |  | 687 |  |  | 9.64 |  |  |  | 713 |  |  |  | 10.43 |  |  |  | 739 |  | 11.25 |  |  |  |  | 764 |  |  | 12.09 |  |  | 788 | 12.95 |  |  | 811 |  | 13.82
12000 |  | 652 |  |  |  | 9.52 |  |  |  |  | 679 |  |  | 10.27 |  |  |  | 704 |  |  | 11.04 |  |  |  | 729 |  |  |  | 11.84 |  |  |  | 753 |  | 12.66 |  |  |  |  | 777 |  |  | 13.5 |  |  | 800 | 14.37 |  |  | 823 |  | 15.26
13500 |  | 676 |  |  |  | 11.25 |  |  |  |  | 701 |  |  | 12 |  |  |  | 725 |  |  | 12.78 |  |  |  | 748 |  |  |  | 13.58 |  |  |  | 771 |  | 14.4 |  |  |  |  | 794 |  |  | 15.24 |  |  | 816 | 16.11 |  |  | 838 |  | 16.99
15000 |  | 703 |  |  |  | 13.3 |  |  |  |  | 726 |  |  | 14.07 |  |  |  | 749 |  |  | 14.86 |  |  |  | 771 |  |  |  | 15.66 |  |  |  | 793 |  | 16.49 |  |  |  |  | 814 |  |  | 17.34 |  |  | 835 | 18.2 |  |  | 856 |  | 19.09
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [7 empty] | 3.8 | [6 empty] | 4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
6,000 7,500 |  | 789 809 |  |  |  | 10.77 12.18 |  |  |  |  | 809 830 |  |  |  | 11.45 12.96 |  |  |  | 829 851 |  |  | 12.13 13.73 |  |  |  | 848 870 |  |  |  | 12.81 14.51
9000 |  | 823 |  |  |  | 13.44 |  |  |  |  | 844 |  |  |  | 14.29 |  |  |  | 866 |  |  | 15.15 |  |  |  | 886 |  |  |  | 16.01
10500 |  | 833 |  |  |  | 14.71 |  |  |  |  | 856 |  |  |  | 15.61 |  |  |  | 877 |  |  | 16.52 |  |  |  | 898 |  |  |  | 17.44
12000 |  | 845 |  |  |  | 16.16 |  |  |  |  | 867 |  |  |  | 17.08 |  |  |  | 888 |  |  | 18.01 |  |  |  | — |  |  |  | —
13500 |  | 859 |  |  |  | 17.9 |  |  |  |  | 880 |  |  |  | 18.82 |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
15000 |  | 876 |  |  |  | 20 |  |  |  |  | 896 |  |  |  | 20.92 |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
LEGEND NOTES:
1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor- mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
50 VAV units only. Brake Horsepower
bhp —
Performance data (cont)
Fan Performance — 50P2,P3,P6,P7 035 Units with Discharge Plenum and 50P4,P5,P8,P9 035 Units
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [5 empty] | 0.8 | [6 empty] | 1 | [6 empty] | 1.2 | [6 empty] | 1.4 |  |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  | rpm |  |  |  | bhp |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  | bhp
7,000 8,000 |  | 285 311 |  |  |  | 1.35 1.81 |  |  |  |  | 337 358 |  |  | 1.78 2.25 |  |  |  | 384 402 |  |  | 2.26 2.75 |  |  | 428 442 |  |  |  | 2.80 3.29 |  |  | 469 481 |  |  | 3.38 3.87 |  |  |  | 507 517 |  |  |  | 4.00 4.50 |  |  | 542 551 |  | 4.66 5.16 |  |  | 576 584 |  | 5.34 5.86
10000 |  | 367 |  |  |  | 3.04 |  |  |  |  | 406 |  |  | 3.52 |  |  |  | 443 |  |  | 4.05 |  |  | 479 |  |  |  | 4.61 |  |  | 512 |  |  | 5.21 |  |  |  | 545 |  |  |  | 5.84 |  |  | 576 |  | 6.51 |  |  | 606 |  | 7.21
12000 |  | 426 |  |  |  | 4.74 |  |  |  |  | 459 |  |  | 5.26 |  |  |  | 491 |  |  | 5.82 |  |  | 522 |  |  |  | 6.42 |  |  | 552 |  |  | 7.05 |  |  |  | 581 |  |  |  | 7.7 |  |  | 609 |  | 8.38 |  |  | 637 |  | 9.09
14000 |  | 486 |  |  |  | 6.98 |  |  |  |  | 515 |  |  | 7.55 |  |  |  | 543 |  |  | 8.15 |  |  | 570 |  |  |  | 8.78 |  |  | 597 |  |  | 9.44 |  |  |  | 623 |  |  |  | 10.12 |  |  | 649 |  | 10.83 |  |  | 674 |  | 11.55
15000 |  | 517 |  |  |  | 8.33 |  |  |  |  | 544 |  |  | 8.92 |  |  |  | 570 |  |  | 9.54 |  |  | 596 |  |  |  | 10.18 |  |  | 621 |  |  | 10.85 |  |  |  | 646 |  |  |  | 11.55 |  |  | 671 |  | 12.27 |  |  | 694 |  | 13.01
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 |  |  |  |  | 3 |  |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  | rpm |  | bhp |  |  | rpm |  | bhp
7,000 8,000 |  | 607 615 |  |  |  | 6.03 6.58 |  |  |  |  | 637 645 |  |  | 6.74 7.32 |  |  |  | 665 673 |  |  | 7.46 8.07 |  |  |  | 691 700 |  |  |  | 8.18 8.84 |  |  |  | 717 726 |  | 8.91 9.62 |  |  |  |  | 741 751 |  |  | 9.65 10.41 |  | 764 775 |  | 10.39 11.20 |  |  | 786 797 |  | 11.13 12.00
10000 |  | 636 |  |  |  | 7.94 |  |  |  |  | 664 |  |  | 8.7 |  |  |  | 691 |  |  | 9.48 |  |  |  | 717 |  |  |  | 10.29 |  |  |  | 743 |  | 11.11 |  |  |  |  | 768 |  |  | 11.96 |  | 792 |  | 12.82 |  |  | 815 |  | 13.69
12000 |  | 663 |  |  |  | 9.83 |  |  |  |  | 689 |  |  | 10.59 |  |  |  | 715 |  |  | 11.38 |  |  |  | 739 |  |  |  | 12.19 |  |  |  | 764 |  | 13.03 |  |  |  |  | 787 |  |  | 13.88 |  | 810 |  | 14.76 |  |  | 833 |  | 15.66
14000 |  | 698 |  |  |  | 12.31 |  |  |  |  | 722 |  |  | 13.08 |  |  |  | 745 |  |  | 13.88 |  |  |  | 768 |  |  |  | 14.69 |  |  |  | 791 |  | 15.53 |  |  |  |  | 813 |  |  | 16.39 |  | 834 |  | 17.27 |  |  | 856 |  | 18.17
15000 |  | 718 |  |  |  | 13.78 |  |  |  |  | 741 |  |  | 14.56 |  |  |  | 763 |  |  | 15.36 |  |  |  | 785 |  |  |  | 16.19 |  |  |  | 807 |  | 17.03 |  |  |  |  | 828 |  |  | 17.9 |  | 849 |  | 18.78 |  |  | 869 |  | 19.69
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [9 empty] | 3.6 | [6 empty] | 3.8 | [6 empty] | 4
|  | rpm |  |  |  | bhp | [5 empty] | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
7,000 8,000 |  | 807 819 |  |  |  | 11.88 12.80 | [5 empty] | 828 841 |  |  | 12.62 13.61 |  |  |  | 848 861 |  |  | 13.37 14.42 |  |  |  | 867 881 |  |  |  | 14.12 15.23
10000 |  | 837 |  |  |  | 14.57 | [5 empty] | 859 |  |  | 15.47 |  |  |  | 881 |  |  | 16.37 |  |  |  | —- |  |  |  | —
12000 |  | 855 |  |  |  | 16.57 | [5 empty] | 876 |  |  | 17.51 |  |  |  | 897 |  |  | 18.45 |  |  |  | — |  |  |  | —
14000 |  | 876 |  |  |  | 19.1 | [5 empty] | 897 |  |  | 20.04 |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
15000 |  | 890 |  |  |  | 20.61 | [5 empty] | — |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
LEGEND NOTES:
1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor- mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
50 VAV units only. Brake Horsepower
bhp —
Performance data (cont)
Fan Performance — 50P2,P3,P6,P7 040 Units with Discharge Plenum and 50P4,P5,P8,P9 040 Units
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
8,000 10,000 |  | 293 343 |  |  |  | 1.62 2.66 |  |  |  |  | 344 385 |  |  | 2.10 3.19 |  |  |  | 390 425 |  |  | 2.62 3.76 |  |  |  | 432 463 |  |  |  | 3.18 4.36 |  |  |  | 470 498 |  | 3.76 4.99 |  |  |  |  | 507 532 |  |  | 4.36 5.64 |  |  | 541 563 |  | 4.97 6.31 |  | 573 594 |  | 5.60 7.00
12000 |  | 395 |  |  |  | 4.09 |  |  |  |  | 431 |  |  | 4.68 |  |  |  | 466 |  |  | 5.29 |  |  |  | 500 |  |  |  | 5.93 |  |  |  | 532 |  | 6.6 |  |  |  |  | 562 |  |  | 7.3 |  |  | 592 |  | 8.01 |  | 620 |  | 8.75
14000 |  | 449 |  |  |  | 5.97 |  |  |  |  | 481 |  |  | 6.62 |  |  |  | 512 |  |  | 7.28 |  |  |  | 541 |  |  |  | 7.96 |  |  |  | 570 |  | 8.67 |  |  |  |  | 598 |  |  | 9.4 |  |  | 626 |  | 10.16 |  | 652 |  | 10.93
16000 |  | 504 |  |  |  | 8.32 |  |  |  |  | 533 |  |  | 9.06 |  |  |  | 560 |  |  | 9.77 |  |  |  | 587 |  |  |  | 10.5 |  |  |  | 613 |  | 11.25 |  |  |  |  | 638 |  |  | 12.02 |  |  | 663 |  | 12.81 |  | 688 |  | 13.62
18000 |  | 559 |  |  |  | 11.2 |  |  |  |  | 586 |  |  | 12.04 |  |  |  | 611 |  |  | 12.82 |  |  |  | 635 |  |  |  | 13.59 |  |  |  | 659 |  | 14.38 |  |  |  |  | 682 |  |  | 15.19 |  |  | 705 |  | 16.01 |  | 727 |  | 16.86
20000 |  | 615 |  |  |  | 14.66 |  |  |  |  | 640 |  |  | 15.59 |  |  |  | 663 |  |  | 16.44 |  |  |  | 685 |  |  |  | 17.28 |  |  |  | 707 |  | 18.11 |  |  |  |  | 728 |  |  | 18.96 |  |  | 749 |  | 19.83 |  | 770 |  | 20.71
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
8,000 10,000 |  | 603 623 |  |  |  | 6.23 7.70 |  |  |  |  | 632 651 |  |  | 6.87 8.41 |  |  |  | 659 678 |  |  | 7.50 9.13 |  |  |  | 685 703 |  |  |  | 8.14 9.86 |  |  |  | 710 728 |  | 8.78 10.60 |  |  |  |  | 734 752 |  |  | 9.43 11.33 |  |  | 757 776 |  | 10.07 12.08 |  | 779 798 |  | 10.71 12.82
12000 |  | 648 |  |  |  | 9.5 |  |  |  |  | 674 |  |  | 10.26 |  |  |  | 699 |  |  | 11.04 |  |  |  | 724 |  |  |  | 11.83 |  |  |  | 748 |  | 12.63 |  |  |  |  | 772 |  |  | 13.44 |  |  | 794 |  | 14.25 |  | 817 |  | 15.07
14000 |  | 677 |  |  |  | 11.73 |  |  |  |  | 702 |  |  | 12.54 |  |  |  | 726 |  |  | 13.35 |  |  |  | 750 |  |  |  | 14.19 |  |  |  | 772 |  | 15.04 |  |  |  |  | 795 |  |  | 15.89 |  |  | 817 |  | 16.76 |  | 838 |  | 17.64
16000 |  | 712 |  |  |  | 14.45 |  |  |  |  | 735 |  |  | 15.3 |  |  |  | 757 |  |  | 16.16 |  |  |  | 779 |  |  |  | 17.03 |  |  |  | 801 |  | 17.92 |  |  |  |  | 822 |  |  | 18.82 |  |  | 843 |  | 19.73 |  | 863 |  | 20.65
18000 |  | 749 |  |  |  | 17.73 |  |  |  |  | 771 |  |  | 18.61 |  |  |  | 792 |  |  | 19.5 |  |  |  | 813 |  |  |  | 20.42 |  |  |  | 833 |  | 21.34 |  |  |  |  | 853 |  |  | 22.27 |  |  | 873 |  | 23.23 |  | — |  | —
20000 |  | 790 |  |  |  | 21.61 |  |  |  |  | 811 |  |  | 22.52 |  |  |  | 830 |  |  | 23.45 |  |  |  | — |  |  |  | — |  |  |  | — |  | — |  |  |  |  | — |  |  | — |  |  | — |  | — |  | — |  | —
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [6 empty] | 3.8 | [7 empty] | 4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  |  |  | bhp
8,000 10,000 |  | 800 820 |  |  |  | 11.35 13.57 |  |  |  |  | 821 841 |  |  | 12.00 14.31 |  |  |  | 841 862 |  |  |  | 12.64 15.06 |  |  |  | 860 882 |  |  |  | 13.28 15.81
12000 |  | 838 |  |  |  | 15.9 |  |  |  |  | 859 |  |  | 16.73 |  |  |  | 880 |  |  |  | 17.57 |  |  |  | 900 |  |  |  | 18.4
14000 |  | 859 |  |  |  | 18.53 |  |  |  |  | 879 |  |  | 19.42 |  |  |  | 899 |  |  |  | 20.32 |  |  |  | — |  |  |  | —
16000 |  | 883 |  |  |  | 21.58 |  |  |  |  | — |  |  | — |  |  |  | — |  |  |  | — |  |  |  | — |  |  |  | —
18000 |  | — |  |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  |  | — |  |  |  | — |  |  |  | —
20000 |  | — |  |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  |  | — |  |  |  | — |  |  |  | —
LEGEND NOTES:
1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor- mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
50 VAV units only. Brake Horsepower
bhp —
Performance data (cont)
Fan Performance — 50P2,P3,P6,P7 050 Units with Discharge Plenum and 50P4,P5,P8,P9 050 Units
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
9000 |  | 324 |  |  |  | 2.15 |  |  |  |  | 369 |  |  | 2.67 |  |  |  | 412 |  |  | 3.23 |  |  |  | 452 |  |  |  | 3.83 |  |  |  | 488 |  | 4.44 |  |  |  |  | 523 |  |  | 5.08 |  |  | 556 |  | 5.73 |  | 587 |  | 6.4
10000 |  | 349 |  |  |  | 2.74 |  |  |  |  | 392 |  |  | 3.28 |  |  |  | 431 |  |  | 3.87 |  |  |  | 469 |  |  |  | 4.48 |  |  |  | 504 |  | 5.12 |  |  |  |  | 537 |  |  | 5.78 |  |  | 569 |  | 6.46 |  | 599 |  | 7.16
12000 |  | 403 |  |  |  | 4.23 |  |  |  |  | 439 |  |  | 4.82 |  |  |  | 474 |  |  | 5.45 |  |  |  | 507 |  |  |  | 6.11 |  |  |  | 539 |  | 6.8 |  |  |  |  | 570 |  |  | 7.51 |  |  | 599 |  | 8.23 |  | 627 |  | 8.98
14000 |  | 459 |  |  |  | 6.17 |  |  |  |  | 490 |  |  | 6.83 |  |  |  | 521 |  |  | 7.5 |  |  |  | 550 |  |  |  | 8.2 |  |  |  | 579 |  | 8.93 |  |  |  |  | 607 |  |  | 9.69 |  |  | 634 |  | 10.46 |  | 660 |  | 11.25
16000 |  | 515 |  |  |  | 8.63 |  |  |  |  | 544 |  |  | 9.34 |  |  |  | 571 |  |  | 10.07 |  |  |  | 597 |  |  |  | 10.82 |  |  |  | 623 |  | 11.59 |  |  |  |  | 649 |  |  | 12.38 |  |  | 674 |  | 13.2 |  | 698 |  | 14.03
18000 |  | 573 |  |  |  | 11.65 |  |  |  |  | 599 |  |  | 12.44 |  |  |  | 623 |  |  | 13.21 |  |  |  | 647 |  |  |  | 14 |  |  |  | 671 |  | 14.82 |  |  |  |  | 694 |  |  | 15.65 |  |  | 716 |  | 16.5 |  | 739 |  | 17.37
20000 |  | 630 |  |  |  | 15.28 |  |  |  |  | 654 |  |  | 16.14 |  |  |  | 677 |  |  | 16.97 |  |  |  | 699 |  |  |  | 17.81 |  |  |  | 720 |  | 18.66 |  |  |  |  | 741 |  |  | 19.53 |  |  | 762 |  | 20.43 |  | 783 |  | 21.34
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
9000 |  | 617 |  |  |  | 7.08 |  |  |  |  | 645 |  |  | 7.77 |  |  |  | 672 |  |  | 8.47 |  |  |  | 698 |  |  |  | 9.18 |  |  |  | 723 |  | 9.9 |  |  |  |  | 747 |  |  | 10.62 |  |  | 770 |  | 11.34 |  | 793 |  | 12.07
10000 |  | 628 |  |  |  | 7.87 |  |  |  |  | 656 |  |  | 8.59 |  |  |  | 682 |  |  | 9.33 |  |  |  | 708 |  |  |  | 10.07 |  |  |  | 733 |  | 10.82 |  |  |  |  | 757 |  |  | 11.58 |  |  | 780 |  | 12.35 |  | 802 |  | 13.12
12000 |  | 654 |  |  |  | 9.74 |  |  |  |  | 680 |  |  | 10.51 |  |  |  | 706 |  |  | 11.3 |  |  |  | 730 |  |  |  | 12.1 |  |  |  | 754 |  | 12.9 |  |  |  |  | 778 |  |  | 13.73 |  |  | 800 |  | 14.56 |  | 822 |  | 15.39
14000 |  | 686 |  |  |  | 12.06 |  |  |  |  | 710 |  |  | 12.88 |  |  |  | 734 |  |  | 13.71 |  |  |  | 757 |  |  |  | 14.55 |  |  |  | 780 |  | 15.41 |  |  |  |  | 802 |  |  | 16.27 |  |  | 824 |  | 17.15 |  | 845 |  | 18.04
16000 |  | 721 |  |  |  | 14.88 |  |  |  |  | 744 |  |  | 15.74 |  |  |  | 767 |  |  | 16.62 |  |  |  | 789 |  |  |  | 17.51 |  |  |  | 810 |  | 18.41 |  |  |  |  | 831 |  |  | 19.32 |  |  | 852 |  | 20.24 |  | 872 |  | 21.17
18000 |  | 761 |  |  |  | 18.27 |  |  |  |  | 782 |  |  | 19.17 |  |  |  | 803 |  |  | 20.09 |  |  |  | 824 |  |  |  | 21.02 |  |  |  | 844 |  | 21.96 |  |  |  |  | 864 |  |  | 22.92 |  |  | 884 |  | 23.88 |  | — |  | —
20000 |  | 803 |  |  |  | 22.27 |  |  |  |  | 823 |  |  | 23.21 |  |  |  | — |  |  | — |  |  |  | — |  |  |  | — |  |  |  | — |  | — |  |  |  |  | — |  |  | — |  |  | — |  | — |  | — |  | —
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [7 empty] | 3.8 | [6 empty] | 4
|  | rpm |  |  |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
9000 |  | 814 |  |  |  |  | 12.79 |  |  |  | 835 |  |  |  | 13.52 |  |  |  | 855 |  |  | 14.25 |  |  |  | 875 |  |  |  | 14.99
10000 |  | 824 |  |  |  |  | 13.89 |  |  |  | 845 |  |  |  | 14.67 |  |  |  | 866 |  |  | 15.45 |  |  |  | 886 |  |  |  | 16.23
12000 |  | 844 |  |  |  |  | 16.24 |  |  |  | 865 |  |  |  | 17.09 |  |  |  | 885 |  |  | 17.95 |  |  |  | — |  |  |  | —
14000 |  | 866 |  |  |  |  | 18.94 |  |  |  | 886 |  |  |  | 19.85 |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
16000 |  | 892 |  |  |  |  | 22.12 |  |  |  | — |  |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
18000 |  | — |  |  |  |  | — |  |  |  | — |  |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
20000 |  | — |  |  |  |  | — |  |  |  | — |  |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
LEGEND NOTES:
1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor- mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
50 VAV units only. Brake Horsepower
bhp —
Performance data (cont)
Fan Performance — 50P2,P3,P6,P7 055 Units with Discharge Plenum and 50P4,P5,P8,P9 055 Units
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
10,000 12,500 |  | 217 248 |  |  |  | 1.21 2.01 |  |  |  |  | 258 286 |  |  | 1.71 2.63 |  |  |  | 296 319 |  |  | 2.29 3.26 |  |  |  | 334 349 |  |  |  | 2.97 3.95 |  |  |  | 371 380 |  | 3.76 4.71 |  |  |  |  | 407 410 |  |  | 4.63 5.58 |  |  | 440 440 |  | 5.56 6.52 |  | 471 469 |  | 6.51 7.54
15000 |  | 281 |  |  |  | 3.13 |  |  |  |  | 317 |  |  | 3.9 |  |  |  | 347 |  |  | 4.64 |  |  |  | 374 |  |  |  | 5.38 |  |  |  | 400 |  | 6.18 |  |  |  |  | 425 |  |  | 7.03 |  |  | 450 |  | 7.95 |  | 476 |  | 8.95
17500 |  | 315 |  |  |  | 4.64 |  |  |  |  | 348 |  |  | 5.55 |  |  |  | 378 |  |  | 6.43 |  |  |  | 403 |  |  |  | 7.29 |  |  |  | 426 |  | 8.16 |  |  |  |  | 449 |  |  | 9.05 |  |  | 471 |  | 10 |  | 493 |  | 10.99
20000 |  | 351 |  |  |  | 6.64 |  |  |  |  | 381 |  |  | 7.64 |  |  |  | 409 |  |  | 8.68 |  |  |  | 433 |  |  |  | 9.68 |  |  |  | 456 |  | 10.66 |  |  |  |  | 477 |  |  | 11.64 |  |  | 497 |  | 12.65 |  | 516 |  | 13.68
22500 |  | 389 |  |  |  | 9.2 |  |  |  |  | 414 |  |  | 10.25 |  |  |  | 440 |  |  | 11.43 |  |  |  | 464 |  |  |  | 12.59 |  |  |  | 486 |  | 13.71 |  |  |  |  | 506 |  |  | 14.81 |  |  | 525 |  | 15.91 |  | 543 |  | 17.03
25000 |  | 427 |  |  |  | 12.39 |  |  |  |  | 449 |  |  | 13.48 |  |  |  | 473 |  |  | 14.75 |  |  |  | 496 |  |  |  | 16.06 |  |  |  | 517 |  | 17.34 |  |  |  |  | 537 |  |  | 18.59 |  |  | 555 |  | 19.82 |  | 573 |  | 21.04
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
10,000 12,500 |  | 500 498 |  |  |  | 7.48 8.63 |  |  |  |  | 527 525 |  |  | 8.46 9.76 |  |  |  | 552 552 |  |  | 9.45 10.93 |  |  |  | 576 577 |  |  |  | 10.44 12.12 |  |  |  | 598 601 |  | 11.42 13.32 |  |  |  |  | 619 624 |  |  | 12.41 14.54 |  |  | 639 646 |  | 13.41 15.76 |  | 659 667 |  | 14.41 16.99
15000 |  | 501 |  |  |  | 10.03 |  |  |  |  | 526 |  |  | 11.17 |  |  |  | 550 |  |  | 12.38 |  |  |  | 575 |  |  |  | 13.65 |  |  |  | 598 |  | 14.97 |  |  |  |  | 621 |  |  | 16.32 |  |  | 644 |  | 17.71 |  | 666 |  | 19.11
17500 |  | 514 |  |  |  | 12.05 |  |  |  |  | 536 |  |  | 13.17 |  |  |  | 557 |  |  | 14.35 |  |  |  | 579 |  |  |  | 15.6 |  |  |  | 600 |  | 16.91 |  |  |  |  | 621 |  |  | 18.28 |  |  | 643 |  | 19.7 |  | 663 |  | 21.18
20000 |  | 535 |  |  |  | 14.76 |  |  |  |  | 554 |  |  | 15.88 |  |  |  | 573 |  |  | 17.06 |  |  |  | 592 |  |  |  | 18.29 |  |  |  | 611 |  | 19.58 |  |  |  |  | 630 |  |  | 20.91 |  |  | 649 |  | 22.31 |  | 668 |  | 23.77
22500 |  | 561 |  |  |  | 18.17 |  |  |  |  | 579 |  |  | 19.34 |  |  |  | 596 |  |  | 20.54 |  |  |  | 613 |  |  |  | 21.78 |  |  |  | 629 |  | 23.06 |  |  |  |  | 646 |  |  | 24.4 |  |  | 663 |  | 25.78 |  | 680 |  | 27.2
25000 |  | 590 |  |  |  | 22.27 |  |  |  |  | 606 |  |  | 23.51 |  |  |  | 622 |  |  | 24.78 |  |  |  | 637 |  |  |  | 26.07 |  |  |  | 653 |  | 27.39 |  |  |  |  | 668 |  |  | 28.75 |  |  | 683 |  | 30.13 |  | 699 |  | 31.56
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [7 empty] | 3.8 | [6 empty] | 4
|  | rpm |  |  |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
10,000 12,500 |  | 677 687 |  |  |  |  | 15.40 18.22 |  |  |  | 695 706 |  |  |  | 16.40 19.45 |  |  |  | 712 725 |  |  | 17.40 20.69 |  |  |  | 728 742 |  |  |  | 18.41 21.92
15000 |  | 687 |  |  |  |  | 20.54 |  |  |  | 707 |  |  |  | 21.98 |  |  |  | 727 |  |  | 23.43 |  |  |  | 746 |  |  |  | 24.89
17500 |  | 684 |  |  |  |  | 22.69 |  |  |  | 704 |  |  |  | 24.24 |  |  |  | 724 |  |  | 25.83 |  |  |  | 743 |  |  |  | 27.43
20000 |  | 686 |  |  |  |  | 25.27 |  |  |  | 705 |  |  |  | 26.84 |  |  |  | 723 |  |  | 28.44 |  |  |  | 742 |  |  |  | 30.09
22500 |  | 697 |  |  |  |  | 28.68 |  |  |  | 713 |  |  |  | 30.21 |  |  |  | 730 |  |  | 31.79 |  |  |  | 747 |  |  |  | 33.42
25000 |  | 714 |  |  |  |  | 33.04 |  |  |  | 729 |  |  |  | 34.55 |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
LEGEND NOTES:
1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor- mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
50 VAV units only. Brake Horsepower
bhp —
Performance data (cont)
Fan Performance — 50P2,P3,P6,P7 060 Units with Discharge Plenum and 50P4,P5,P8,P9 060 Units
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
12,000 15,000 |  | 241 281 |  |  |  | 1.82 3.14 |  |  |  |  | 280 316 |  |  | 2.41 3.87 |  |  |  | 314 346 |  |  | 3.04 4.61 |  |  |  | 346 374 |  |  |  | 3.72 5.38 |  |  |  | 376 400 |  | 4.47 6.19 |  |  |  |  | 405 426 |  |  | 5.26 7.05 |  |  | 433 450 |  | 6.11 7.95 |  | 460 474 |  | 7.01 8.90
18000 |  | 323 |  |  |  | 5.03 |  |  |  |  | 355 |  |  | 5.92 |  |  |  | 382 |  |  | 6.8 |  |  |  | 408 |  |  |  | 7.68 |  |  |  | 431 |  | 8.58 |  |  |  |  | 454 |  |  | 9.53 |  |  | 476 |  | 10.5 |  | 498 |  | 11.52
21000 |  | 366 |  |  |  | 7.61 |  |  |  |  | 395 |  |  | 8.66 |  |  |  | 421 |  |  | 9.69 |  |  |  | 444 |  |  |  | 10.71 |  |  |  | 466 |  | 11.73 |  |  |  |  | 487 |  |  | 12.78 |  |  | 507 |  | 13.85 |  | 527 |  | 14.94
24000 |  | 410 |  |  |  | 10.97 |  |  |  |  | 437 |  |  | 12.2 |  |  |  | 460 |  |  | 13.39 |  |  |  | 482 |  |  |  | 14.55 |  |  |  | 503 |  | 15.71 |  |  |  |  | 523 |  |  | 16.88 |  |  | 541 |  | 18.07 |  | 560 |  | 19.27
27000 |  | 455 |  |  |  | 15.23 |  |  |  |  | 479 |  |  | 16.65 |  |  |  | 501 |  |  | 18 |  |  |  | 522 |  |  |  | 19.33 |  |  |  | 542 |  | 20.64 |  |  |  |  | 560 |  |  | 21.95 |  |  | 578 |  | 23.26 |  | 595 |  | 24.58
30000 |  | 500 |  |  |  | 20.52 |  |  |  |  | 522 |  |  | 22.11 |  |  |  | 543 |  |  | 23.64 |  |  |  | 563 |  |  |  | 25.14 |  |  |  | 581 |  | 26.61 |  |  |  |  | 599 |  |  | 28.06 |  |  | 616 |  | 29.52 |  | 632 |  | 30.97
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
12,000 15,000 |  | 486 498 |  |  |  | 7.94 9.90 |  |  |  |  | 511 520 |  |  | 8.91 10.93 |  |  |  | 535 543 |  |  | 9.91 12.01 |  |  |  | 559 564 |  |  |  | 10.94 13.11 |  |  |  | 581 586 |  | 11.99 14.26 |  |  |  |  | 603 606 |  |  | 13.07 15.43 |  |  | 624 627 |  | 14.16 16.63 |  | 645 646 |  | 15.28 17.86
18000 |  | 518 |  |  |  | 12.57 |  |  |  |  | 539 |  |  | 13.66 |  |  |  | 559 |  |  | 14.78 |  |  |  | 579 |  |  |  | 15.95 |  |  |  | 598 |  | 17.15 |  |  |  |  | 617 |  |  | 18.39 |  |  | 636 |  | 19.65 |  | 654 |  | 20.95
21000 |  | 546 |  |  |  | 16.07 |  |  |  |  | 564 |  |  | 17.23 |  |  |  | 583 |  |  | 18.42 |  |  |  | 600 |  |  |  | 19.64 |  |  |  | 618 |  | 20.9 |  |  |  |  | 635 |  |  | 22.19 |  |  | 653 |  | 23.51 |  | 669 |  | 24.86
24000 |  | 577 |  |  |  | 20.49 |  |  |  |  | 594 |  |  | 21.74 |  |  |  | 611 |  |  | 23 |  |  |  | 628 |  |  |  | 24.31 |  |  |  | 644 |  | 25.63 |  |  |  |  | 660 |  |  | 26.99 |  |  | 676 |  | 28.38 |  | 691 |  | 29.77
27000 |  | 611 |  |  |  | 25.91 |  |  |  |  | 628 |  |  | 27.26 |  |  |  | 643 |  |  | 28.63 |  |  |  | 659 |  |  |  | 30.03 |  |  |  | 674 |  | 31.44 |  |  |  |  | 689 |  |  | 32.87 |  |  | 703 |  | 34.33 |  | 718 |  | 35.82
30000 |  | 648 |  |  |  | 32.43 |  |  |  |  | 663 |  |  | 33.9 |  |  |  | 678 |  |  | 35.38 |  |  |  | — |  |  |  | — |  |  |  | — |  | — |  |  |  |  | — |  |  | — |  |  | — |  | — |  | — |  | —
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [7 empty] | 3.8 | [6 empty] | 4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
12,000 15,000 |  | 664 666 |  |  |  | 16.40 19.12 |  |  |  |  | 683 685 |  |  |  | 17.55 20.39 |  |  |  | 702 703 |  |  | 18.70 21.69 |  |  |  | 720 721 |  |  |  | 19.87 23.01
18000 |  | 672 |  |  |  | 22.28 |  |  |  |  | 690 |  |  |  | 23.64 |  |  |  | 708 |  |  | 25.02 |  |  |  | 725 |  |  |  | 26.44
21000 |  | 686 |  |  |  | 26.25 |  |  |  |  | 703 |  |  |  | 27.67 |  |  |  | 719 |  |  | 29.11 |  |  |  | 735 |  |  |  | 30.59
24000 |  | 707 |  |  |  | 31.23 |  |  |  |  | 722 |  |  |  | 32.71 |  |  |  | 737 |  |  | 34.2 |  |  |  | — |  |  |  | —
27000 |  | — |  |  |  | — |  |  |  |  | — |  |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
30000 |  | — |  |  |  | — |  |  |  |  | — |  |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
LEGEND NOTES:
1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor- mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
50 VAV units only. Brake Horsepower
bhp —
Performance data (cont)
Fan Performance — 50P2,P3,P6,P7 070 Units with Discharge Plenum and 50P4,P5,P8,P9 070 Units
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [7 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
14,000 17,500 |  | 268 316 |  |  |  | 2.64 4.67 |  |  |  |  | 304 348 |  |  | 3.32 5.54 |  |  |  | 335 376 |  |  | 4.02 6.39 |  |  |  | 364 402 |  |  |  | 4.76 7.25 |  |  |  | 391 426 |  | 5.55 8.14 |  |  |  |  | 418 449 |  |  | 6.39 9.06 |  |  | 444 472 |  | 7.27 10.03 |  | 468 493 |  | 8.20 11.03
21000 |  | 366 |  |  |  | 7.61 |  |  |  |  | 395 |  |  | 8.66 |  |  |  | 421 |  |  | 9.69 |  |  |  | 444 |  |  |  | 10.71 |  |  |  | 466 |  | 11.73 |  |  |  |  | 487 |  |  | 12.78 |  |  | 507 |  | 13.85 |  | 527 |  | 14.94
24500 |  | 417 |  |  |  | 11.61 |  |  |  |  | 444 |  |  | 12.87 |  |  |  | 467 |  |  | 14.09 |  |  |  | 489 |  |  |  | 15.28 |  |  |  | 509 |  | 16.47 |  |  |  |  | 529 |  |  | 17.66 |  |  | 547 |  | 18.86 |  | 565 |  | 20.08
28000 |  | 470 |  |  |  | 16.88 |  |  |  |  | 493 |  |  | 18.35 |  |  |  | 515 |  |  | 19.77 |  |  |  | 536 |  |  |  | 21.15 |  |  |  | 555 |  | 22.51 |  |  |  |  | 573 |  |  | 23.87 |  |  | 590 |  | 25.22 |  | 607 |  | 26.59
30000 |  | 500 |  |  |  | 20.52 |  |  |  |  | 522 |  |  | 22.11 |  |  |  | 543 |  |  | 23.64 |  |  |  | 563 |  |  |  | 25.14 |  |  |  | 581 |  | 26.61 |  |  |  |  | 599 |  |  | 28.06 |  |  | 616 |  | 29.52 |  | 632 |  | 30.97
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [7 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
14,000 17,500 |  | 493 515 |  |  |  | 9.17 12.07 |  |  |  |  | 516 535 |  |  | 10.19 13.14 |  |  |  | 539 556 |  |  | 11.24 14.26 |  |  |  | 562 576 |  |  |  | 12.33 15.42 |  |  |  | 583 595 |  | 13.45 16.61 |  |  |  |  | 605 615 |  |  | 14.60 17.84 |  |  | 625 634 |  | 15.77 19.09 |  | 645 652 |  | 16.96 20.39
21000 |  | 546 |  |  |  | 16.07 |  |  |  |  | 564 |  |  | 17.23 |  |  |  | 583 |  |  | 18.42 |  |  |  | 600 |  |  |  | 19.64 |  |  |  | 618 |  | 20.9 |  |  |  |  | 635 |  |  | 22.19 |  |  | 653 |  | 23.51 |  | 669 |  | 24.86
24500 |  | 583 |  |  |  | 21.32 |  |  |  |  | 600 |  |  | 22.59 |  |  |  | 616 |  |  | 23.87 |  |  |  | 633 |  |  |  | 25.18 |  |  |  | 649 |  | 26.53 |  |  |  |  | 664 |  |  | 27.89 |  |  | 680 |  | 29.29 |  | 695 |  | 30.71
28000 |  | 623 |  |  |  | 27.96 |  |  |  |  | 639 |  |  | 29.35 |  |  |  | 655 |  |  | 30.75 |  |  |  | 670 |  |  |  | 32.18 |  |  |  | 685 |  | 33.63 |  |  |  |  | 699 |  |  | 35.09 |  |  | — |  | — |  | — |  | —
30000 |  | 648 |  |  |  | 32.43 |  |  |  |  | 663 |  |  | 33.9 |  |  |  | 678 |  |  | 35.38 |  |  |  | — |  |  |  | — |  |  |  | — |  | — |  |  |  |  | — |  |  | — |  |  | — |  | — |  | — |  | —
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.4 | [8 empty] | 3.6 | [6 empty] | 3.8 | [7 empty] | 4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  |  | rpm |  |  |  | bhp
14,000 17,500 |  | 665 671 |  |  |  | 18.18 21.70 |  |  |  |  | 684 689 |  |  | 19.42 23.05 |  |  |  | 703 706 |  |  |  | 20.68 24.42 |  |  |  | 721 724 |  |  |  | 21.95 25.82
21000 |  | 686 |  |  |  | 26.24 |  |  |  |  | 703 |  |  | 27.67 |  |  |  | 719 |  |  |  | 29.11 |  |  |  | 735 |  |  |  | 30.59
24500 |  | 711 |  |  |  | 32.17 |  |  |  |  | 726 |  |  | 33.65 |  |  |  | 741 |  |  |  | 35.16 |  |  |  | — |  |  |  | —
28000 |  | — |  |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  |  | — |  |  |  | — |  |  |  | —
30000 |  | — |  |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  |  | — |  |  |  | — |  |  |  | —
LEGEND NOTES:
1. Fan performance is based on wet coils and clean 2-in. filters. 2. See Component Pressure Drop data table before using Fan Perfor- mance tables. 3. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
50 VAV units only. Brake Horsepower
bhp —
Performance data (cont)
Fan Performance — 48P 075 and 50P 075 Units with Forward-Curved Fan*
AIRFLOW (Cfm) |  |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  |  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [6 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  |  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  | bhp |  | rpm |  | bhp
14000 |  |  | 211 |  |  |  | 2.35 |  |  |  |  | 243 |  |  | 3.06 |  |  |  | 272 |  |  | 3.8 |  |  |  | 299 |  |  | 4.59 |  |  |  | 325 |  |  | 5.43 |  |  |  | 349 |  |  |  | 6.3 |  | 372 |  | 7.21 |  | 395 |  | 8.15
16000 |  |  | 232 |  |  |  | 3.27 |  |  |  |  | 261 |  |  | 4.06 |  |  |  | 288 |  |  | 4.88 |  |  |  | 313 |  |  | 5.74 |  |  |  | 337 |  |  | 6.65 |  |  |  | 360 |  |  |  | 7.59 |  | 381 |  | 8.57 |  | 402 |  | 9.58
18000 |  |  | 253 |  |  |  | 4.42 |  |  |  |  | 281 |  |  | 5.31 |  |  |  | 305 |  |  | 6.21 |  |  |  | 329 |  |  | 7.14 |  |  |  | 351 |  |  | 8.11 |  |  |  | 372 |  |  |  | 912 |  | 393 |  | 10.17 |  | 413 |  | 11.25
20000 |  |  | 275 |  |  |  | 5.83 |  |  |  |  | 301 |  |  | 6.82 |  |  |  | 324 |  |  | 7.81 |  |  |  | 346 |  |  | 8.82 |  |  |  | 366 |  |  | 9.86 |  |  |  | 386 |  |  |  | 10.94 |  | 406 |  | 12.05 |  | 425 |  | 13.2
22000 |  |  | 298 |  |  |  | 7.53 |  |  |  |  | 321 |  |  | 8.62 |  |  |  | 343 |  |  | 9.7 |  |  |  | 364 |  |  | 10.8 |  |  |  | 383 |  |  | 11.92 |  |  |  | 402 |  |  |  | 13.07 |  | 420 |  | 14.25 |  | 438 |  | 15.46
24000 |  |  | 320 |  |  |  | 9.55 |  |  |  |  | 342 |  |  | 10.75 |  |  |  | 363 |  |  | 11.93 |  |  |  | 383 |  |  | 13.11 |  |  |  | 401 |  |  | 14.31 |  |  |  | 419 |  |  |  | 15.54 |  | 436 |  | 16.79 |  | 453 |  | 18.07
26000 |  |  | 343 |  |  |  | 11.91 |  |  |  |  | 364 |  |  | 13.22 |  |  |  | 384 |  |  | 14.5 |  |  |  | 402 |  |  | 15.78 |  |  |  | 420 |  |  | 17.07 |  |  |  | 437 |  |  |  | 18.37 |  | 453 |  | 19.7 |  | 469 |  | 21.05
28000 |  |  | 367 |  |  |  | 14.65 |  |  |  |  | 386 |  |  | 16.06 |  |  |  | 405 |  |  | 17.45 |  |  |  | 422 |  |  | 18.83 |  |  |  | 439 |  |  | 20.2 |  |  |  | 455 |  |  |  | 21.59 |  | 471 |  | 23 |  | 486 |  | 24.43
30000 |  |  | 390 |  |  |  | 17.78 |  |  |  |  | 408 |  |  | 19.31 |  |  |  | 426 |  |  | 20.8 |  |  |  | 443 |  |  | 22.28 |  |  |  | 459 |  |  | 23.75 |  |  |  | 474 |  |  |  | 25.24 |  | 489 |  | 26.73 |  | 504 |  | 28.24
AIRFLOW (Cfm) |  |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  |  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [6 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  |  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  | bhp |  | rpm |  | bhp
14000 |  |  | 416 |  |  |  | 9.12 |  |  |  |  | 437 |  |  | 10.1 |  |  |  | 457 |  |  | 11.1 |  |  |  | 476 |  |  | 12.13 |  |  |  | 495 |  |  | 13.17 |  |  |  | 513 |  |  |  | 14.22 |  | 531 |  | 15.29 |  | 548 |  | 16.38
16000 |  |  | 423 |  |  |  | 10.62 |  |  |  |  | 442 |  |  | 11.68 |  |  |  | 462 |  |  | 12.77 |  |  |  | 480 |  |  | 13.88 |  |  |  | 498 |  |  | 15 |  |  |  | 516 |  |  |  | 16.15 |  | 533 |  | 17.31 |  | 550 |  | 18.48
18000 |  |  | 432 |  |  |  | 12.36 |  |  |  |  | 450 |  |  | 13.5 |  |  |  | 469 |  |  | 14.66 |  |  |  | 486 |  |  | 15.84 |  |  |  | 504 |  |  | 17.05 |  |  |  | 521 |  |  |  | 18.27 |  | 537 |  | 19.53 |  | 553 |  | 20.78
20000 |  |  | 443 |  |  |  | 14.38 |  |  |  |  | 460 |  |  | 15.58 |  |  |  | 478 |  |  | 16.82 |  |  |  | 495 |  |  | 18.07 |  |  |  | 511 |  |  | 19.35 |  |  |  | 527 |  |  |  | 20.65 |  | 543 |  | 21.98 |  | 559 |  | 23.32
22000 |  |  | 455 |  |  |  | 16.7 |  |  |  |  | 472 |  |  | 17.98 |  |  |  | 489 |  |  | 19.28 |  |  |  | 505 |  |  | 20.6 |  |  |  | 521 |  |  | 21.96 |  |  |  | 536 |  |  |  | 23.33 |  | 551 |  | 24.72 |  | 566 |  | 26.14
24000 |  |  | 470 |  |  |  | 19.38 |  |  |  |  | 486 |  |  | 20.72 |  |  |  | 501 |  |  | 22.08 |  |  |  | 517 |  |  | 23.48 |  |  |  | 532 |  |  | 24.89 |  |  |  | 547 |  |  |  | 26.34 |  | 561 |  | 27.8 |  | 576 |  | 29.29
26000 |  |  | 485 |  |  |  | 22.43 |  |  |  |  | 500 |  |  | 23.83 |  |  |  | 515 |  |  | 25.27 |  |  |  | 530 |  |  | 26.73 |  |  |  | 544 |  |  | 28.22 |  |  |  | 559 |  |  |  | 29.72 |  | 573 |  | 31.26 |  | 586 |  | 32.81
28000 |  |  | 501 |  |  |  | 25.89 |  |  |  |  | 516 |  |  | 27.36 |  |  |  | 530 |  |  | 28.86 |  |  |  | 544 |  |  | 30.38 |  |  |  | 558 |  |  | 31.94 |  |  |  | 572 |  |  |  | 33.51 |  | 585 |  | 35.11 |  | 599 |  | 36.74
30000 |  |  | 518 |  |  |  | 29.76 |  |  |  |  | 533 |  |  | 31.32 |  |  |  | 546 |  |  | 32.89 |  |  |  | 560 |  |  | 34.48 |  |  |  | 573 |  |  | 36.1 |  |  |  | 586 |  |  |  | 37.74 |  | 599 |  | 39.41 |  | 612 |  | 41.11
AIRFLOW (Cfm) |  |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  |  | 3.4 | [8 empty] | 3.6 | [6 empty] | 3.8 | [6 empty] | 4
|  |  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp
14000 |  |  | 564 |  |  |  | 17.47 |  |  |  |  | 581 |  |  | 18.58 |  |  |  | 596 |  |  | 19.71 |  |  |  | 612 |  |  | 20.84
16000 |  |  | 566 |  |  |  | 19.68 |  |  |  |  | 582 |  |  | 20.88 |  |  |  | 597 |  |  | 22.1 |  |  |  | 613 |  |  | 23.33
18000 |  |  | 569 |  |  |  | 22.06 |  |  |  |  | 585 |  |  | 23.36 |  |  |  | 600 |  |  | 24.66 |  |  |  | 615 |  |  | 25.99
20000 |  |  | 574 |  |  |  | 24.68 |  |  |  |  | 589 |  |  | 26.06 |  |  |  | 604 |  |  | 27.45 |  |  |  | 618 |  |  | 28.85
22000 |  |  | 581 |  |  |  | 27.57 |  |  |  |  | 596 |  |  | 29.04 |  |  |  | 610 |  |  | 30.51 |  |  |  | 624 |  |  | 31.99
24000 |  |  | 590 |  |  |  | 30.8 |  |  |  |  | 604 |  |  | 32.33 |  |  |  | 617 |  |  | 33.88 |  |  |  | 631 |  |  | 35.44
26000 |  |  | 600 |  |  |  | 34.39 |  |  |  |  | 613 |  |  | 35.99 |  |  |  | 627 |  |  | 37.61 |  |  |  | 640 |  |  | 39.24
28000 |  |  | 612 |  |  |  | 38.38 |  |  |  |  | 624 |  |  | 40.05 |  |  |  | 637 |  |  | 41.74 |  |  |  | 650 |  |  | 43.44
30000 |  |  | 624 |  |  |  | 42.81 |  |  |  |  | 637 |  |  | 44.54 |  |  |  | 649 |  |  | 46.29 |  |  |  | 661 |  |  | 48.06
LEGEND | [11 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. For return fan and high-capacity power exhaust units, add compo-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | nent pressure drop for economizer. Do not add component pressure drop for power exhaust. 3. See Component Pressure Drop data table before using Fan Perfor- mance tables. 4. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 48P 075 and 50P 075 Units with Airfoil Fan*
AIRFLOW (Cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.3 | [8 empty] | 0.6 | [6 empty] | 0.9 | [6 empty] | 1.2 | [6 empty] | 1.5 | [6 empty] | 1.8 | [6 empty] | 2.1 |  |  |  | 2.4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
15000 |  | 620 |  |  |  | 3.02 |  |  |  |  | 671 |  |  | 3.91 |  |  |  | 720 |  |  | 4.83 |  |  |  | 767 |  |  |  | 5.8 |  |  | 813 |  |  | 6.81 |  |  |  | 858 |  |  |  | 7.87 |  |  | 902 |  | 8.97 |  | 944 |  | 10.1
16000 |  | 655 |  |  |  | 3.52 |  |  |  |  | 703 |  |  | 4.45 |  |  |  | 749 |  |  | 5.41 |  |  |  | 794 |  |  |  | 6.42 |  |  | 838 |  |  | 7.47 |  |  |  | 881 |  |  |  | 8.56 |  |  | 922 |  | 9.69 |  | 963 |  | 10.86
18000 |  | 725 |  |  |  | 4.68 |  |  |  |  | 769 |  |  | 5.71 |  |  |  | 810 |  |  | 6.76 |  |  |  | 851 |  |  |  | 7.84 |  |  | 891 |  |  | 8.96 |  |  |  | 930 |  |  |  | 10.12 |  |  | 968 |  | 11.32 |  | 1006 |  | 12.55
20000 |  | 795 |  |  |  | 6.08 |  |  |  |  | 836 |  |  | 7.22 |  |  |  | 874 |  |  | 8.36 |  |  |  | 911 |  |  |  | 9.52 |  |  | 947 |  |  | 10.71 |  |  |  | 983 |  |  |  | 11.94 |  |  | 1019 |  | 13.2 |  | 1054 |  | 14.51
22000 |  | 867 |  |  |  | 7.75 |  |  |  |  | 904 |  |  | 9 |  |  |  | 940 |  |  | 10.24 |  |  |  | 974 |  |  |  | 11.49 |  |  | 1008 |  |  | 12.76 |  |  |  | 1041 |  |  |  | 14.06 |  |  | 1073 |  | 15.39 |  | 1105 |  | 16.76
24000 |  | 939 |  |  |  | 9.71 |  |  |  |  | 974 |  |  | 11.07 |  |  |  | 1007 |  |  | 12.41 |  |  |  | 1039 |  |  |  | 13.75 |  |  | 1070 |  |  | 15.11 |  |  |  | 1101 |  |  |  | 16.49 |  |  | 1131 |  | 17.9 |  | 1161 |  | 19.33
26000 |  | 1012 |  |  |  | 11.99 |  |  |  |  | 1044 |  |  | 13.46 |  |  |  | 1075 |  |  | 14.9 |  |  |  | 1105 |  |  |  | 16.34 |  |  | 1134 |  |  | 17.79 |  |  |  | 1163 |  |  |  | 19.25 |  |  | 1191 |  | 20.74 |  | 1219 |  | 22.25
28000 |  | 1084 |  |  |  | 14.61 |  |  |  |  | 1115 |  |  | 16.18 |  |  |  | 1144 |  |  | 17.73 |  |  |  | 1172 |  |  |  | 19.28 |  |  | 1200 |  |  | 20.82 |  |  |  | 1227 |  |  |  | 22.37 |  |  | 1253 |  | 23.94 |  | 1280 |  | 25.52
30000 |  | 1157 |  |  |  | 17.6 |  |  |  |  | 1186 |  |  | 19.28 |  |  |  | 1214 |  |  | 20.93 |  |  |  | 1240 |  |  |  | 22.57 |  |  | 1267 |  |  | 24.22 |  |  |  | 1292 |  |  |  | 25.86 |  |  | 1317 |  | 27.51 |  | 1342 |  | 29.18
AIRFLOW (Cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 2.7 | [8 empty] | 3 | [6 empty] | 3.3 | [6 empty] | 3.6 | [6 empty] | 3.9 | [6 empty] | 4.2 | [6 empty] | 4.5 |  |  |  | 4.8
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
15000 |  | 984 |  |  |  | 11.25 |  |  |  |  | 1023 |  |  | 12.42 |  |  |  | 1061 |  |  | 13.6 |  |  |  | 1097 |  |  |  | 14.8 |  |  | 1131 |  |  | 16 |  |  |  | 1165 |  |  |  | 17.22 |  |  | 1198 |  | 18.44 |  | 1229 |  | 19.67
16000 |  | 1003 |  |  |  | 12.06 |  |  |  |  | 1041 |  |  | 13.27 |  |  |  | 1078 |  |  | 14.51 |  |  |  | 1113 |  |  |  | 15.76 |  |  | 1148 |  |  | 17.02 |  |  |  | 1181 |  |  |  | 18.29 |  |  | 1214 |  | 19.56 |  | 1245 |  | 20.85
18000 |  | 1043 |  |  |  | 13.82 |  |  |  |  | 1079 |  |  | 15.12 |  |  |  | 1114 |  |  | 16.44 |  |  |  | 1149 |  |  |  | 17.79 |  |  | 1182 |  |  | 19.15 |  |  |  | 1215 |  |  |  | 20.52 |  |  | 1247 |  | 21.91 |  | 1278 |  | 23.31
20000 |  | 1088 |  |  |  | 15.84 |  |  |  |  | 1122 |  |  | 17.21 |  |  |  | 1155 |  |  | 18.6 |  |  |  | 1188 |  |  |  | 20.02 |  |  | 1220 |  |  | 21.47 |  |  |  | 1251 |  |  |  | 22.93 |  |  | 1282 |  | 24.42 |  | 1312 |  | 25.91
22000 |  | 1137 |  |  |  | 18.15 |  |  |  |  | 1169 |  |  | 19.58 |  |  |  | 1200 |  |  | 21.05 |  |  |  | 1231 |  |  |  | 22.54 |  |  | 1261 |  |  | 24.05 |  |  |  | 1291 |  |  |  | 25.59 |  |  | 1321 |  | 27.15 |  | 1350 |  | 28.74
24000 |  | 1191 |  |  |  | 20.79 |  |  |  |  | 1220 |  |  | 22.28 |  |  |  | 1249 |  |  | 23.81 |  |  |  | 1278 |  |  |  | 25.36 |  |  | 1307 |  |  | 26.94 |  |  |  | 1335 |  |  |  | 28.55 |  |  | 1363 |  | 30.18 |  | 1390 |  | 31.83
26000 |  | 1247 |  |  |  | 23.78 |  |  |  |  | 1274 |  |  | 25.33 |  |  |  | 1302 |  |  | 26.92 |  |  |  | 1329 |  |  |  | 28.53 |  |  | 1356 |  |  | 30.18 |  |  |  | 1382 |  |  |  | 31.85 |  |  | 1409 |  | 33.54 |  | 1435 |  | 35.26
28000 |  | 1306 |  |  |  | 27.12 |  |  |  |  | 1332 |  |  | 28.75 |  |  |  | 1357 |  |  | 30.41 |  |  |  | 1383 |  |  |  | 32.08 |  |  | 1408 |  |  | 33.79 |  |  |  | 1433 |  |  |  | 35.52 |  |  | 1458 |  | 37.28 |  | 1483 |  | 39.05
30000 |  | 1367 |  |  |  | 30.86 |  |  |  |  | 1391 |  |  | 32.57 |  |  |  | 1415 |  |  | 34.29 |  |  |  | 1439 |  |  |  | 36.03 |  |  | 1463 |  |  | 37.81 |  |  |  | 1487 |  |  |  | 39.6 |  |  | 1510 |  | 41.42 |  | 1534 |  | 43.25
AIRFLOW (Cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 5.1 | [8 empty] | 5.4 | [6 empty] | 5.7 | [6 empty] | 6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
15000 |  | 1260 |  |  |  | 20.91 |  |  |  |  | 1290 |  |  | 22.15 |  |  |  | 1319 |  |  | 23.41 |  |  |  | 1347 |  |  |  | 24.66
16000 |  | 1276 |  |  |  | 22.15 |  |  |  |  | 1305 |  |  | 23.45 |  |  |  | 1334 |  |  | 24.76 |  |  |  | 1362 |  |  |  | 26.08
18000 |  | 1308 |  |  |  | 24.71 |  |  |  |  | 1337 |  |  | 26.13 |  |  |  | 1366 |  |  | 27.56 |  |  |  | 1394 |  |  |  | 28.99
20000 |  | 1342 |  |  |  | 27.42 |  |  |  |  | 1370 |  |  | 28.95 |  |  |  | 1399 |  |  | 30.48 |  |  |  | 1426 |  |  |  | 32.02
22000 |  | 1378 |  |  |  | 30.33 |  |  |  |  | 1406 |  |  | 31.95 |  |  |  | 1434 |  |  | 33.57 |  |  |  | 1461 |  |  |  | 35.21
24000 |  | 1418 |  |  |  | 33.51 |  |  |  |  | 1445 |  |  | 35.2 |  |  |  | 1471 |  |  | 36.91 |  |  |  | 1497 |  |  |  | 38.64
26000 |  | 1461 |  |  |  | 37 |  |  |  |  | 1487 |  |  | 38.76 |  |  |  | 1512 |  |  | 40.54 |  |  |  | 1537 |  |  |  | 42.35
28000 |  | 1507 |  |  |  | 40.86 |  |  |  |  | 1532 |  |  | 42.69 |  |  |  | 1556 |  |  | 44.54 |  |  |  | 1580 |  |  |  | 46.4
30000 |  | 1557 |  |  |  | 45.12 |  |  |  |  | 1580 |  |  | 47.01 |  |  |  | 1603 |  |  | 48.92 |  |  |  | 1626 |  |  |  | 50.85
LEGEND | [11 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. For return fan and high-capacity power exhaust units, add compo-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | nent pressure drop for economizer. Do not add component pressure drop for power exhaust. 3. See Component Pressure Drop data table before using Fan Perfor- mance tables. 4. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 48P 090 and 50P 090 Units with Forward-Curved Fan*
AIRFLOW (Cfm) |  |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  |  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [6 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  |  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  | bhp |  | rpm |  | bhp
16000 |  |  | 232 |  |  |  | 3.27 |  |  |  |  | 261 |  |  | 4.06 |  |  |  | 288 |  |  | 4.88 |  |  |  | 313 |  |  | 5.74 |  |  |  | 337 |  |  | 6.65 |  |  |  | 360 |  |  |  | 7.59 |  | 381 |  | 8.57 |  | 402 |  | 9.58
18000 |  |  | 253 |  |  |  | 4.42 |  |  |  |  | 281 |  |  | 5.31 |  |  |  | 305 |  |  | 6.21 |  |  |  | 329 |  |  | 7.14 |  |  |  | 351 |  |  | 8.11 |  |  |  | 372 |  |  |  | 9.12 |  | 393 |  | 10.17 |  | 413 |  | 11.25
20000 |  |  | 275 |  |  |  | 5.83 |  |  |  |  | 301 |  |  | 6.82 |  |  |  | 324 |  |  | 7.81 |  |  |  | 346 |  |  | 8.82 |  |  |  | 366 |  |  | 9.86 |  |  |  | 386 |  |  |  | 10.94 |  | 406 |  | 12.05 |  | 425 |  | 13.2
22000 |  |  | 298 |  |  |  | 7.53 |  |  |  |  | 321 |  |  | 8.62 |  |  |  | 343 |  |  | 9.7 |  |  |  | 364 |  |  | 10.8 |  |  |  | 383 |  |  | 11.92 |  |  |  | 402 |  |  |  | 13.07 |  | 420 |  | 14.25 |  | 438 |  | 15.46
24000 |  |  | 320 |  |  |  | 9.55 |  |  |  |  | 342 |  |  | 10.75 |  |  |  | 363 |  |  | 11.93 |  |  |  | 383 |  |  | 13.11 |  |  |  | 401 |  |  | 14.31 |  |  |  | 419 |  |  |  | 15.54 |  | 436 |  | 16.79 |  | 453 |  | 18.07
26000 |  |  | 343 |  |  |  | 11.91 |  |  |  |  | 364 |  |  | 13.22 |  |  |  | 384 |  |  | 14.5 |  |  |  | 402 |  |  | 15.78 |  |  |  | 420 |  |  | 17.07 |  |  |  | 437 |  |  |  | 18.37 |  | 453 |  | 19.7 |  | 469 |  | 21.05
28000 |  |  | 367 |  |  |  | 14.65 |  |  |  |  | 386 |  |  | 16.06 |  |  |  | 405 |  |  | 17.45 |  |  |  | 422 |  |  | 18.83 |  |  |  | 439 |  |  | 20.2 |  |  |  | 455 |  |  |  | 21.59 |  | 471 |  | 23 |  | 486 |  | 24.43
30000 |  |  | 390 |  |  |  | 17.78 |  |  |  |  | 408 |  |  | 19.31 |  |  |  | 426 |  |  | 20.8 |  |  |  | 443 |  |  | 22.28 |  |  |  | 459 |  |  | 23.75 |  |  |  | 474 |  |  |  | 25.24 |  | 489 |  | 26.73 |  | 504 |  | 28.24
32000 |  |  | 414 |  |  |  | 21.36 |  |  |  |  | 431 |  |  | 22.99 |  |  |  | 448 |  |  | 24.59 |  |  |  | 464 |  |  | 26.17 |  |  |  | 479 |  |  | 27.75 |  |  |  | 494 |  |  |  | 29.32 |  | 508 |  | 30.9 |  | 523 |  | 32.49
34000 |  |  | 437 |  |  |  | 25.39 |  |  |  |  | 454 |  |  | 27.13 |  |  |  | 470 |  |  | 28.84 |  |  |  | 485 |  |  | 30.53 |  |  |  | 500 |  |  | 32.2 |  |  |  | 514 |  |  |  | 33.87 |  | 528 |  | 35.55 |  | 542 |  | 37.23
AIRFLOW (Cfm) |  |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  |  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [6 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  |  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  | bhp |  | rpm |  | bhp
16000 |  |  | 423 |  |  |  | 10.62 |  |  |  |  | 442 |  |  | 11.68 |  |  |  | 462 |  |  | 12.77 |  |  |  | 480 |  |  | 13.88 |  |  |  | 498 |  |  | 15 |  |  |  | 516 |  |  |  | 16.15 |  | 533 |  | 17.31 |  | 550 |  | 18.48
18000 |  |  | 432 |  |  |  | 12.36 |  |  |  |  | 450 |  |  | 13.5 |  |  |  | 469 |  |  | 14.66 |  |  |  | 486 |  |  | 15.84 |  |  |  | 504 |  |  | 17.05 |  |  |  | 521 |  |  |  | 18.27 |  | 537 |  | 19.53 |  | 553 |  | 20.78
20000 |  |  | 443 |  |  |  | 14.38 |  |  |  |  | 460 |  |  | 15.58 |  |  |  | 478 |  |  | 16.82 |  |  |  | 495 |  |  | 18.07 |  |  |  | 511 |  |  | 19.35 |  |  |  | 527 |  |  |  | 20.65 |  | 543 |  | 21.98 |  | 559 |  | 23.32
22000 |  |  | 455 |  |  |  | 16.7 |  |  |  |  | 472 |  |  | 17.98 |  |  |  | 489 |  |  | 19.28 |  |  |  | 505 |  |  | 20.6 |  |  |  | 521 |  |  | 21.96 |  |  |  | 536 |  |  |  | 23.33 |  | 551 |  | 24.72 |  | 566 |  | 26.14
24000 |  |  | 470 |  |  |  | 19.38 |  |  |  |  | 486 |  |  | 20.72 |  |  |  | 501 |  |  | 22.08 |  |  |  | 517 |  |  | 23.48 |  |  |  | 532 |  |  | 24.89 |  |  |  | 547 |  |  |  | 26.34 |  | 561 |  | 27.8 |  | 576 |  | 29.29
26000 |  |  | 485 |  |  |  | 22.43 |  |  |  |  | 500 |  |  | 23.83 |  |  |  | 515 |  |  | 25.27 |  |  |  | 530 |  |  | 26.73 |  |  |  | 544 |  |  | 28.22 |  |  |  | 559 |  |  |  | 29.72 |  | 573 |  | 31.26 |  | 586 |  | 32.81
28000 |  |  | 501 |  |  |  | 25.89 |  |  |  |  | 516 |  |  | 27.36 |  |  |  | 530 |  |  | 28.86 |  |  |  | 544 |  |  | 30.38 |  |  |  | 558 |  |  | 31.94 |  |  |  | 572 |  |  |  | 33.51 |  | 585 |  | 35.11 |  | 599 |  | 36.74
30000 |  |  | 518 |  |  |  | 29.76 |  |  |  |  | 533 |  |  | 31.32 |  |  |  | 546 |  |  | 32.89 |  |  |  | 560 |  |  | 34.48 |  |  |  | 573 |  |  | 36.1 |  |  |  | 586 |  |  |  | 37.74 |  | 599 |  | 39.41 |  | 612 |  | 41.11
32000 |  |  | 536 |  |  |  | 34.11 |  |  |  |  | 550 |  |  | 35.73 |  |  |  | 563 |  |  | 37.38 |  |  |  | 576 |  |  | 39.04 |  |  |  | 589 |  |  | 40.73 |  |  |  | 601 |  |  |  | 42.45 |  | 614 |  | 44.18 |  | 626 |  | 45.94
34000 |  |  | 555 |  |  |  | 38.92 |  |  |  |  | 568 |  |  | 40.63 |  |  |  | 581 |  |  | 42.36 |  |  |  | 593 |  |  | 44.1 |  |  |  | 605 |  |  | 45.87 |  |  |  | 618 |  |  |  | 47.64 |  | 630 |  | 49.45 |  | 641 |  | 51.27
AIRFLOW (Cfm) |  |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  |  | 3.4 | [8 empty] | 3.6 | [6 empty] | 3.8 | [6 empty] | 4
|  |  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp
16000 |  |  | 566 |  |  |  | 19.68 |  |  |  |  | 582 |  |  | 20.88 |  |  |  | 597 |  |  | 22.1 |  |  |  | 613 |  |  | 23.33
18000 |  |  | 569 |  |  |  | 22.06 |  |  |  |  | 585 |  |  | 23.36 |  |  |  | 600 |  |  | 24.66 |  |  |  | 615 |  |  | 25.99
20000 |  |  | 574 |  |  |  | 24.68 |  |  |  |  | 589 |  |  | 26.06 |  |  |  | 604 |  |  | 27.45 |  |  |  | 618 |  |  | 28.85
22000 |  |  | 581 |  |  |  | 27.57 |  |  |  |  | 596 |  |  | 29.04 |  |  |  | 610 |  |  | 30.51 |  |  |  | 624 |  |  | 31.99
24000 |  |  | 590 |  |  |  | 30.8 |  |  |  |  | 604 |  |  | 32.33 |  |  |  | 617 |  |  | 33.88 |  |  |  | 631 |  |  | 35.44
26000 |  |  | 600 |  |  |  | 34.39 |  |  |  |  | 613 |  |  | 35.99 |  |  |  | 627 |  |  | 37.61 |  |  |  | 640 |  |  | 39.24
28000 |  |  | 612 |  |  |  | 38.38 |  |  |  |  | 624 |  |  | 40.05 |  |  |  | 637 |  |  | 41.74 |  |  |  | 650 |  |  | 43.44
30000 |  |  | 624 |  |  |  | 42.81 |  |  |  |  | 637 |  |  | 44.54 |  |  |  | 649 |  |  | 46.29 |  |  |  | 661 |  |  | 48.06
32000 |  |  | 638 |  |  |  | 47.72 |  |  |  |  | 650 |  |  | 49.51 |  |  |  | 662 |  |  | 51.33 |  |  |  | 674 |  |  | 53.17
34000 |  |  | 653 |  |  |  | 53.12 |  |  |  |  | 665 |  |  | 54.98 |  |  |  | 676 |  |  | 56.87 |  |  |  | — |  |  | —
LEGEND | [11 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. For return fan and high-capacity power exhaust units, add compo-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | nent pressure drop for economizer. Do not add component pressure drop for power exhaust. 3. See Component Pressure Drop data table before using Fan Perfor- mance tables. 4. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 48P 090 and 50P 090 Units with Airfoil Fan*
AIRFLOW (Cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.3 | [8 empty] | 0.6 | [6 empty] | 0.9 | [6 empty] | 1.2 | [6 empty] | 1.5 | [6 empty] | 1.8 | [6 empty] | 2.1 |  |  |  | 2.4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
17000 |  | 690 |  |  |  | 4.07 |  |  |  |  | 735 |  |  | 5.05 |  |  |  | 779 |  |  | 6.06 |  |  |  | 822 |  |  |  | 7.1 |  |  | 863 |  |  | 8.18 |  |  |  | 904 |  |  |  | 9.31 |  |  | 945 |  | 10.47 |  | 984 |  | 11.68
18000 |  | 725 |  |  |  | 4.68 |  |  |  |  | 769 |  |  | 5.71 |  |  |  | 810 |  |  | 6.76 |  |  |  | 851 |  |  |  | 7.84 |  |  | 891 |  |  | 8.96 |  |  |  | 930 |  |  |  | 10.12 |  |  | 968 |  | 11.32 |  | 1006 |  | 12.55
20000 |  | 795 |  |  |  | 6.08 |  |  |  |  | 836 |  |  | 7.22 |  |  |  | 874 |  |  | 8.36 |  |  |  | 911 |  |  |  | 9.52 |  |  | 947 |  |  | 10.71 |  |  |  | 983 |  |  |  | 11.94 |  |  | 1019 |  | 13.2 |  | 1054 |  | 14.51
22000 |  | 867 |  |  |  | 7.75 |  |  |  |  | 904 |  |  | 9 |  |  |  | 940 |  |  | 10.24 |  |  |  | 974 |  |  |  | 11.49 |  |  | 1008 |  |  | 12.76 |  |  |  | 1041 |  |  |  | 14.06 |  |  | 1073 |  | 15.39 |  | 1105 |  | 16.76
24000 |  | 939 |  |  |  | 9.71 |  |  |  |  | 974 |  |  | 11.07 |  |  |  | 1007 |  |  | 12.41 |  |  |  | 1039 |  |  |  | 13.75 |  |  | 1070 |  |  | 15.11 |  |  |  | 1101 |  |  |  | 16.49 |  |  | 1131 |  | 17.9 |  | 1161 |  | 19.33
26000 |  | 1012 |  |  |  | 11.99 |  |  |  |  | 1044 |  |  | 13.46 |  |  |  | 1075 |  |  | 14.9 |  |  |  | 1105 |  |  |  | 16.34 |  |  | 1134 |  |  | 17.79 |  |  |  | 1163 |  |  |  | 19.25 |  |  | 1191 |  | 20.74 |  | 1219 |  | 22.25
28000 |  | 1084 |  |  |  | 14.61 |  |  |  |  | 1115 |  |  | 16.18 |  |  |  | 1144 |  |  | 17.73 |  |  |  | 1172 |  |  |  | 19.28 |  |  | 1200 |  |  | 20.82 |  |  |  | 1227 |  |  |  | 22.37 |  |  | 1253 |  | 23.94 |  | 1280 |  | 25.52
30000 |  | 1157 |  |  |  | 17.6 |  |  |  |  | 1186 |  |  | 19.28 |  |  |  | 1214 |  |  | 20.93 |  |  |  | 1240 |  |  |  | 22.57 |  |  | 1267 |  |  | 24.22 |  |  |  | 1292 |  |  |  | 25.86 |  |  | 1317 |  | 27.51 |  | 1342 |  | 29.18
32000 |  | 1231 |  |  |  | 20.97 |  |  |  |  | 1258 |  |  | 22.76 |  |  |  | 1284 |  |  | 24.52 |  |  |  | 1309 |  |  |  | 26.26 |  |  | 1334 |  |  | 28 |  |  |  | 1358 |  |  |  | 29.74 |  |  | 1382 |  | 31.48 |  | 1406 |  | 33.23
34000 |  | 1304 |  |  |  | 24.75 |  |  |  |  | 1330 |  |  | 26.65 |  |  |  | 1355 |  |  | 28.52 |  |  |  | 1379 |  |  |  | 30.36 |  |  | 1403 |  |  | 32.2 |  |  |  | 1426 |  |  |  | 34.04 |  |  | 1448 |  | 35.87 |  | 1471 |  | 37.71
AIRFLOW (Cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 2.7 | [8 empty] | 3 | [6 empty] | 3.3 | [6 empty] | 3.6 | [6 empty] | 3.9 | [6 empty] | 4.2 | [6 empty] | 4.5 |  |  |  | 4.8
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
17000 |  | 1022 |  |  |  | 12.91 |  |  |  |  | 1059 |  |  | 14.17 |  |  |  | 1096 |  |  | 15.45 |  |  |  | 1131 |  |  |  | 16.75 |  |  | 1165 |  |  | 18.06 |  |  |  | 1198 |  |  |  | 19.38 |  |  | 1230 |  | 20.72 |  | 1261 |  | 22.06
18000 |  | 1043 |  |  |  | 13.82 |  |  |  |  | 1079 |  |  | 15.12 |  |  |  | 1114 |  |  | 16.44 |  |  |  | 1149 |  |  |  | 17.79 |  |  | 1182 |  |  | 19.15 |  |  |  | 1215 |  |  |  | 20.52 |  |  | 1247 |  | 21.91 |  | 1278 |  | 23.31
20000 |  | 1088 |  |  |  | 15.84 |  |  |  |  | 1122 |  |  | 17.21 |  |  |  | 1155 |  |  | 18.6 |  |  |  | 1188 |  |  |  | 20.02 |  |  | 1220 |  |  | 21.47 |  |  |  | 1251 |  |  |  | 22.93 |  |  | 1282 |  | 24.42 |  | 1312 |  | 25.91
22000 |  | 1137 |  |  |  | 18.15 |  |  |  |  | 1169 |  |  | 19.58 |  |  |  | 1200 |  |  | 21.05 |  |  |  | 1231 |  |  |  | 22.54 |  |  | 1261 |  |  | 24.05 |  |  |  | 1291 |  |  |  | 25.59 |  |  | 1321 |  | 27.15 |  | 1350 |  | 28.74
24000 |  | 1191 |  |  |  | 20.79 |  |  |  |  | 1220 |  |  | 22.28 |  |  |  | 1249 |  |  | 23.81 |  |  |  | 1278 |  |  |  | 25.36 |  |  | 1307 |  |  | 26.94 |  |  |  | 1335 |  |  |  | 28.55 |  |  | 1363 |  | 30.18 |  | 1390 |  | 31.83
26000 |  | 1247 |  |  |  | 23.78 |  |  |  |  | 1274 |  |  | 25.33 |  |  |  | 1302 |  |  | 26.92 |  |  |  | 1329 |  |  |  | 28.53 |  |  | 1356 |  |  | 30.18 |  |  |  | 1382 |  |  |  | 31.85 |  |  | 1409 |  | 33.54 |  | 1435 |  | 35.26
28000 |  | 1306 |  |  |  | 27.12 |  |  |  |  | 1332 |  |  | 28.75 |  |  |  | 1357 |  |  | 30.41 |  |  |  | 1383 |  |  |  | 32.08 |  |  | 1408 |  |  | 33.79 |  |  |  | 1433 |  |  |  | 35.52 |  |  | 1458 |  | 37.28 |  | 1483 |  | 39.05
30000 |  | 1367 |  |  |  | 30.86 |  |  |  |  | 1391 |  |  | 32.57 |  |  |  | 1415 |  |  | 34.29 |  |  |  | 1439 |  |  |  | 36.03 |  |  | 1463 |  |  | 37.81 |  |  |  | 1487 |  |  |  | 39.6 |  |  | 1510 |  | 41.42 |  | 1534 |  | 43.25
32000 |  | 1429 |  |  |  | 35 |  |  |  |  | 1452 |  |  | 36.78 |  |  |  | 1475 |  |  | 38.58 |  |  |  | 1498 |  |  |  | 40.4 |  |  | 1520 |  |  | 42.24 |  |  |  | 1543 |  |  |  | 44.1 |  |  | 1565 |  | 45.98 |  | 1587 |  | 47.88
34000 |  | 1493 |  |  |  | 39.57 |  |  |  |  | 1515 |  |  | 41.43 |  |  |  | 1537 |  |  | 43.31 |  |  |  | 1558 |  |  |  | 45.2 |  |  | 1580 |  |  | 47.11 |  |  |  | 1601 |  |  |  | 49.05 |  |  | 1622 |  | 50.99 |  | 1643 |  | 52.96
AIRFLOW (Cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 5.1 | [8 empty] | 5.4 | [6 empty] | 5.7 | [6 empty] | 6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
17000 |  | 1291 |  |  |  | 23.42 |  |  |  |  | 1321 |  |  | 24.77 |  |  |  | 1350 |  |  | 26.14 |  |  |  | 1378 |  |  |  | 27.52
18000 |  | 1308 |  |  |  | 24.71 |  |  |  |  | 1337 |  |  | 26.13 |  |  |  | 1366 |  |  | 27.56 |  |  |  | 1394 |  |  |  | 28.99
20000 |  | 1342 |  |  |  | 27.42 |  |  |  |  | 1370 |  |  | 28.95 |  |  |  | 1399 |  |  | 30.48 |  |  |  | 1426 |  |  |  | 32.02
22000 |  | 1378 |  |  |  | 30.33 |  |  |  |  | 1406 |  |  | 31.95 |  |  |  | 1434 |  |  | 33.57 |  |  |  | 1461 |  |  |  | 35.21
24000 |  | 1418 |  |  |  | 33.51 |  |  |  |  | 1445 |  |  | 35.2 |  |  |  | 1471 |  |  | 36.91 |  |  |  | 1497 |  |  |  | 38.64
26000 |  | 1461 |  |  |  | 37 |  |  |  |  | 1487 |  |  | 38.76 |  |  |  | 1512 |  |  | 40.54 |  |  |  | 1537 |  |  |  | 42.35
28000 |  | 1507 |  |  |  | 40.86 |  |  |  |  | 1532 |  |  | 42.69 |  |  |  | 1556 |  |  | 44.54 |  |  |  | 1580 |  |  |  | 46.4
30000 |  | 1557 |  |  |  | 45.12 |  |  |  |  | 1580 |  |  | 47.01 |  |  |  | 1603 |  |  | 48.92 |  |  |  | 1626 |  |  |  | 50.85
32000 |  | 1609 |  |  |  | 49.81 |  |  |  |  | 1631 |  |  | 51.76 |  |  |  | 1653 |  |  | 53.72 |  |  |  | 1675 |  |  |  | 55.72
34000 |  | 1664 |  |  |  | 54.95 |  |  |  |  | 1685 |  |  | 56.96 |  |  |  | 1706 |  |  | 58.99 |  |  |  | 1727 |  |  |  | 61.04
LEGEND | [11 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. For return fan and high-capacity power exhaust units, add compo-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | nent pressure drop for economizer. Do not add component pressure drop for power exhaust. 3. See Component Pressure Drop data table before using Fan Perfor- mance tables. 4. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 48P 100 and 50P 100 Units with Forward-Curved Fan*
AIRFLOW (Cfm) |  |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  |  | 0.2 | [8 empty] | 0.4 | [6 empty] | 0.6 | [6 empty] | 0.8 | [6 empty] | 1 | [6 empty] | 1.2 | [5 empty] | 1.4 |  |  |  | 1.6
|  |  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  | bhp |  | rpm |  | bhp
20000 |  |  | 275 |  |  |  | 5.83 |  |  |  |  | 301 |  |  | 6.82 |  |  |  | 324 |  |  | 7.81 |  |  |  | 346 |  |  | 8.82 |  |  |  | 366 |  |  | 9.86 |  |  |  | 386 |  |  |  | 10.94 |  | 406 |  | 12.05 |  | 425 |  | 13.2
22000 |  |  | 298 |  |  |  | 7.53 |  |  |  |  | 321 |  |  | 8.62 |  |  |  | 343 |  |  | 9.7 |  |  |  | 364 |  |  | 10.8 |  |  |  | 383 |  |  | 11.92 |  |  |  | 402 |  |  |  | 13.07 |  | 420 |  | 14.25 |  | 438 |  | 15.46
24000 |  |  | 320 |  |  |  | 9.55 |  |  |  |  | 342 |  |  | 10.75 |  |  |  | 363 |  |  | 11.93 |  |  |  | 383 |  |  | 13.11 |  |  |  | 401 |  |  | 14.31 |  |  |  | 419 |  |  |  | 15.54 |  | 436 |  | 16.79 |  | 453 |  | 18.07
26000 |  |  | 343 |  |  |  | 11.91 |  |  |  |  | 364 |  |  | 13.22 |  |  |  | 384 |  |  | 14.5 |  |  |  | 402 |  |  | 15.78 |  |  |  | 420 |  |  | 17.07 |  |  |  | 437 |  |  |  | 18.37 |  | 453 |  | 19.7 |  | 469 |  | 21.05
28000 |  |  | 367 |  |  |  | 14.65 |  |  |  |  | 386 |  |  | 16.06 |  |  |  | 405 |  |  | 17.45 |  |  |  | 422 |  |  | 18.83 |  |  |  | 439 |  |  | 20.2 |  |  |  | 455 |  |  |  | 21.59 |  | 471 |  | 23 |  | 486 |  | 24.43
30000 |  |  | 390 |  |  |  | 17.78 |  |  |  |  | 408 |  |  | 19.31 |  |  |  | 426 |  |  | 20.8 |  |  |  | 443 |  |  | 22.28 |  |  |  | 459 |  |  | 23.75 |  |  |  | 474 |  |  |  | 25.24 |  | 489 |  | 26.73 |  | 504 |  | 28.24
32000 |  |  | 414 |  |  |  | 21.36 |  |  |  |  | 431 |  |  | 22.99 |  |  |  | 448 |  |  | 24.59 |  |  |  | 464 |  |  | 26.17 |  |  |  | 479 |  |  | 27.75 |  |  |  | 494 |  |  |  | 29.32 |  | 508 |  | 30.9 |  | 523 |  | 32.49
34000 |  |  | 437 |  |  |  | 25.39 |  |  |  |  | 454 |  |  | 27.13 |  |  |  | 470 |  |  | 28.84 |  |  |  | 485 |  |  | 30.53 |  |  |  | 500 |  |  | 32.2 |  |  |  | 514 |  |  |  | 33.87 |  | 528 |  | 35.55 |  | 542 |  | 37.23
36000 |  |  | 461 |  |  |  | 29.92 |  |  |  |  | 477 |  |  | 31.77 |  |  |  | 492 |  |  | 33.58 |  |  |  | 506 |  |  | 35.38 |  |  |  | 521 |  |  | 37.16 |  |  |  | 534 |  |  |  | 38.93 |  | 548 |  | 40.69 |  | 561 |  | 42.47
38000 |  |  | 485 |  |  |  | 34.96 |  |  |  |  | 500 |  |  | 36.91 |  |  |  | 514 |  |  | 38.85 |  |  |  | 528 |  |  | 40.74 |  |  |  | 542 |  |  | 42.63 |  |  |  | 555 |  |  |  | 44.5 |  | 568 |  | 46.36 |  | 581 |  | 48.23
40000 |  |  | 509 |  |  |  | 40.54 |  |  |  |  | 523 |  |  | 42.61 |  |  |  | 537 |  |  | 44.65 |  |  |  | 550 |  |  | 46.66 |  |  |  | 563 |  |  | 48.64 |  |  |  | 576 |  |  |  | 50.62 |  | 589 |  | 52.59 |  | 601 |  | 54.56
AIRFLOW (Cfm) |  |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  |  | 1.8 | [8 empty] | 2 | [6 empty] | 2.2 | [6 empty] | 2.4 | [6 empty] | 2.6 | [6 empty] | 2.8 | [5 empty] | 3 |  |  |  | 3.2
|  |  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  | bhp |  | rpm |  | bhp
20000 |  |  | 443 |  |  |  | 14.38 |  |  |  |  | 460 |  |  | 15.58 |  |  |  | 478 |  |  | 16.82 |  |  |  | 495 |  |  | 18.07 |  |  |  | 511 |  |  | 19.35 |  |  |  | 527 |  |  |  | 20.65 |  | 543 |  | 21.98 |  | 559 |  | 23.32
22000 |  |  | 455 |  |  |  | 16.7 |  |  |  |  | 472 |  |  | 17.98 |  |  |  | 489 |  |  | 19.28 |  |  |  | 505 |  |  | 20.6 |  |  |  | 521 |  |  | 21.96 |  |  |  | 536 |  |  |  | 23.33 |  | 551 |  | 24.72 |  | 566 |  | 26.14
24000 |  |  | 470 |  |  |  | 19.38 |  |  |  |  | 486 |  |  | 20.72 |  |  |  | 501 |  |  | 22.08 |  |  |  | 517 |  |  | 23.48 |  |  |  | 532 |  |  | 24.89 |  |  |  | 547 |  |  |  | 26.34 |  | 561 |  | 27.8 |  | 576 |  | 29.29
26000 |  |  | 485 |  |  |  | 22.43 |  |  |  |  | 500 |  |  | 23.83 |  |  |  | 515 |  |  | 25.27 |  |  |  | 530 |  |  | 26.73 |  |  |  | 544 |  |  | 28.22 |  |  |  | 559 |  |  |  | 29.72 |  | 573 |  | 31.26 |  | 586 |  | 32.81
28000 |  |  | 501 |  |  |  | 25.89 |  |  |  |  | 516 |  |  | 27.36 |  |  |  | 530 |  |  | 28.86 |  |  |  | 544 |  |  | 30.38 |  |  |  | 558 |  |  | 31.94 |  |  |  | 572 |  |  |  | 33.51 |  | 585 |  | 35.11 |  | 599 |  | 36.74
30000 |  |  | 518 |  |  |  | 29.76 |  |  |  |  | 533 |  |  | 31.32 |  |  |  | 546 |  |  | 32.89 |  |  |  | 560 |  |  | 34.48 |  |  |  | 573 |  |  | 36.1 |  |  |  | 586 |  |  |  | 37.74 |  | 599 |  | 39.41 |  | 612 |  | 41.11
32000 |  |  | 536 |  |  |  | 34.11 |  |  |  |  | 550 |  |  | 35.73 |  |  |  | 563 |  |  | 37.38 |  |  |  | 576 |  |  | 39.04 |  |  |  | 589 |  |  | 40.73 |  |  |  | 601 |  |  |  | 42.45 |  | 614 |  | 44.18 |  | 626 |  | 45.94
34000 |  |  | 555 |  |  |  | 38.92 |  |  |  |  | 568 |  |  | 40.63 |  |  |  | 581 |  |  | 42.36 |  |  |  | 593 |  |  | 44.1 |  |  |  | 605 |  |  | 45.87 |  |  |  | 618 |  |  |  | 47.64 |  | 630 |  | 49.45 |  | 641 |  | 51.27
36000 |  |  | 574 |  |  |  | 44.25 |  |  |  |  | 586 |  |  | 46.03 |  |  |  | 599 |  |  | 47.85 |  |  |  | 611 |  |  | 49.67 |  |  |  | 623 |  |  | 51.51 |  |  |  | 634 |  |  |  | 53.37 |  | 646 |  | 55.25 |  | 657 |  | 57.14
38000 |  |  | 593 |  |  |  | 50.1 |  |  |  |  | 605 |  |  | 51.98 |  |  |  | 617 |  |  | 53.87 |  |  |  | 629 |  |  | 55.77 |  |  |  | 640 |  |  | 57.71 |  |  |  | 652 |  |  |  | 59.63 |  | 663 |  | 61.59 |  | 674 |  | 63.54
40000 |  |  | 613 |  |  |  | 56.52 |  |  |  |  | 625 |  |  | 58.49 |  |  |  | 636 |  |  | 60.48 |  |  |  | 648 |  |  | 62.46 |  |  |  | 659 |  |  | 64.47 |  |  |  | — |  |  |  | — |  | — |  | — |  | — |  | —
AIRFLOW (Cfm) |  |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  |  | 3.4 | [8 empty] | 3.6 | [6 empty] | 3.8 | [6 empty] | 4
|  |  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp
20000 |  |  | 574 |  |  |  | 24.68 |  |  |  |  | 589 |  |  | 26.06 |  |  |  | 604 |  |  | 27.45 |  |  |  | 618 |  |  | 28.86
22000 |  |  | 581 |  |  |  | 27.57 |  |  |  |  | 596 |  |  | 29.04 |  |  |  | 610 |  |  | 30.51 |  |  |  | 624 |  |  | 31.99
24000 |  |  | 590 |  |  |  | 30.8 |  |  |  |  | 604 |  |  | 32.33 |  |  |  | 617 |  |  | 33.88 |  |  |  | 631 |  |  | 35.44
26000 |  |  | 600 |  |  |  | 34.39 |  |  |  |  | 613 |  |  | 35.99 |  |  |  | 627 |  |  | 37.61 |  |  |  | 640 |  |  | 39.24
28000 |  |  | 612 |  |  |  | 38.38 |  |  |  |  | 624 |  |  | 40.05 |  |  |  | 637 |  |  | 41.74 |  |  |  | 650 |  |  | 43.44
30000 |  |  | 624 |  |  |  | 42.81 |  |  |  |  | 637 |  |  | 44.54 |  |  |  | 649 |  |  | 46.29 |  |  |  | 661 |  |  | 48.06
32000 |  |  | 638 |  |  |  | 47.72 |  |  |  |  | 650 |  |  | 49.51 |  |  |  | 662 |  |  | 51.33 |  |  |  | 674 |  |  | 53.17
34000 |  |  | 653 |  |  |  | 53.12 |  |  |  |  | 665 |  |  | 54.98 |  |  |  | 676 |  |  | 56.87 |  |  |  | — |  |  | —
36000 |  |  | 669 |  |  |  | 59.06 |  |  |  |  | 680 |  |  | 60.98 |  |  |  | — |  |  | — |  |  |  | — |  |  | —
38000 |  |  | — |  |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  | —
40000 |  |  | — |  |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  | —
LEGEND | [11 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. For return fan and high-capacity power exhaust units, add compo-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | nent pressure drop for economizer. Do not add component pressure drop for power exhaust. 3. See Component Pressure Drop data table before using Fan Perfor- mance tables. 4. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — 48P 100 and 50P 100 Units with Airfoil Fan*
AIRFLOW (Cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.3 | [8 empty] | 0.6 | [6 empty] | 0.9 | [6 empty] | 1.2 | [6 empty] | 1.5 | [6 empty] | 1.8 | [6 empty] | 2.1 |  |  |  | 2.4
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
20000 |  | 795 |  |  |  | 6.08 |  |  |  |  | 836 |  |  | 7.22 |  |  |  | 874 |  |  | 8.36 |  |  |  | 911 |  |  |  | 9.52 |  |  | 947 |  |  | 10.71 |  |  |  | 983 |  |  |  | 11.94 |  |  | 1019 |  | 13.2 |  | 1054 |  | 14.51
22000 |  | 867 |  |  |  | 7.75 |  |  |  |  | 904 |  |  | 9 |  |  |  | 940 |  |  | 10.24 |  |  |  | 974 |  |  |  | 11.49 |  |  | 1008 |  |  | 12.76 |  |  |  | 1041 |  |  |  | 14.06 |  |  | 1073 |  | 15.39 |  | 1105 |  | 16.76
24000 |  | 939 |  |  |  | 9.71 |  |  |  |  | 974 |  |  | 11.07 |  |  |  | 1007 |  |  | 12.41 |  |  |  | 1039 |  |  |  | 13.75 |  |  | 1070 |  |  | 15.11 |  |  |  | 1101 |  |  |  | 16.49 |  |  | 1131 |  | 17.9 |  | 1161 |  | 19.33
26000 |  | 1012 |  |  |  | 11.99 |  |  |  |  | 1044 |  |  | 13.46 |  |  |  | 1075 |  |  | 14.9 |  |  |  | 1105 |  |  |  | 16.34 |  |  | 1134 |  |  | 17.79 |  |  |  | 1163 |  |  |  | 19.25 |  |  | 1191 |  | 20.74 |  | 1219 |  | 22.25
28000 |  | 1084 |  |  |  | 14.61 |  |  |  |  | 1115 |  |  | 16.18 |  |  |  | 1144 |  |  | 17.73 |  |  |  | 1172 |  |  |  | 19.28 |  |  | 1200 |  |  | 20.82 |  |  |  | 1227 |  |  |  | 22.37 |  |  | 1253 |  | 23.94 |  | 1280 |  | 25.52
30000 |  | 1157 |  |  |  | 17.6 |  |  |  |  | 1186 |  |  | 19.28 |  |  |  | 1214 |  |  | 20.93 |  |  |  | 1240 |  |  |  | 22.57 |  |  | 1267 |  |  | 24.22 |  |  |  | 1292 |  |  |  | 25.86 |  |  | 1317 |  | 27.51 |  | 1342 |  | 29.18
32000 |  | 1231 |  |  |  | 20.97 |  |  |  |  | 1258 |  |  | 22.76 |  |  |  | 1284 |  |  | 24.52 |  |  |  | 1309 |  |  |  | 26.26 |  |  | 1334 |  |  | 28 |  |  |  | 1358 |  |  |  | 29.74 |  |  | 1382 |  | 31.48 |  | 1406 |  | 33.23
34000 |  | 1304 |  |  |  | 24.75 |  |  |  |  | 1330 |  |  | 26.65 |  |  |  | 1355 |  |  | 28.52 |  |  |  | 1379 |  |  |  | 30.36 |  |  | 1403 |  |  | 32.2 |  |  |  | 1426 |  |  |  | 34.04 |  |  | 1448 |  | 35.87 |  | 1471 |  | 37.71
36000 |  | 1378 |  |  |  | 28.97 |  |  |  |  | 1402 |  |  | 30.97 |  |  |  | 1426 |  |  | 32.94 |  |  |  | 1449 |  |  |  | 34.89 |  |  | 1472 |  |  | 36.84 |  |  |  | 1494 |  |  |  | 38.76 |  |  | 1515 |  | 40.7 |  | 1537 |  | 42.64
38000 |  | 1452 |  |  |  | 33.65 |  |  |  |  | 1475 |  |  | 35.75 |  |  |  | 1498 |  |  | 37.82 |  |  |  | 1520 |  |  |  | 39.89 |  |  | 1541 |  |  | 41.92 |  |  |  | 1562 |  |  |  | 43.95 |  |  | 1583 |  | 45.98 |  | 1604 |  | 48.01
40000 |  | 1526 |  |  |  | 38.81 |  |  |  |  | 1548 |  |  | 41.02 |  |  |  | 1570 |  |  | 43.2 |  |  |  | 1591 |  |  |  | 45.35 |  |  | 1611 |  |  | 47.49 |  |  |  | 1632 |  |  |  | 49.63 |  |  | 1652 |  | 51.76 |  | 1671 |  | 53.88
AIRFLOW (Cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 2.7 | [8 empty] | 3 | [6 empty] | 3.3 | [6 empty] | 3.6 | [6 empty] | 3.9 | [6 empty] | 4.2 | [6 empty] | 4.5 |  |  |  | 4.8
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  |  | rpm |  | bhp |  | rpm |  | bhp
20000 |  | 1088 |  |  |  | 15.84 |  |  |  |  | 1122 |  |  | 17.21 |  |  |  | 1155 |  |  | 18.6 |  |  |  | 1188 |  |  |  | 20.02 |  |  | 1220 |  |  | 21.47 |  |  |  | 1251 |  |  |  | 22.93 |  |  | 1282 |  | 24.42 |  | 1312 |  | 25.91
22000 |  | 1137 |  |  |  | 18.15 |  |  |  |  | 1169 |  |  | 19.58 |  |  |  | 1200 |  |  | 21.05 |  |  |  | 1231 |  |  |  | 22.54 |  |  | 1261 |  |  | 24.05 |  |  |  | 1291 |  |  |  | 25.59 |  |  | 1321 |  | 27.15 |  | 1350 |  | 28.74
24000 |  | 1191 |  |  |  | 20.79 |  |  |  |  | 1220 |  |  | 22.28 |  |  |  | 1249 |  |  | 23.81 |  |  |  | 1278 |  |  |  | 25.36 |  |  | 1307 |  |  | 26.94 |  |  |  | 1335 |  |  |  | 28.55 |  |  | 1363 |  | 30.18 |  | 1390 |  | 31.83
26000 |  | 1247 |  |  |  | 23.78 |  |  |  |  | 1274 |  |  | 25.33 |  |  |  | 1302 |  |  | 26.92 |  |  |  | 1329 |  |  |  | 28.53 |  |  | 1356 |  |  | 30.18 |  |  |  | 1382 |  |  |  | 31.85 |  |  | 1409 |  | 33.54 |  | 1435 |  | 35.26
28000 |  | 1306 |  |  |  | 27.12 |  |  |  |  | 1332 |  |  | 28.75 |  |  |  | 1357 |  |  | 30.41 |  |  |  | 1383 |  |  |  | 32.08 |  |  | 1408 |  |  | 33.79 |  |  |  | 1433 |  |  |  | 35.52 |  |  | 1458 |  | 37.28 |  | 1483 |  | 39.05
30000 |  | 1367 |  |  |  | 30.86 |  |  |  |  | 1391 |  |  | 32.57 |  |  |  | 1415 |  |  | 34.29 |  |  |  | 1439 |  |  |  | 36.03 |  |  | 1463 |  |  | 37.81 |  |  |  | 1487 |  |  |  | 39.6 |  |  | 1510 |  | 41.42 |  | 1534 |  | 43.25
32000 |  | 1429 |  |  |  | 35 |  |  |  |  | 1452 |  |  | 36.78 |  |  |  | 1475 |  |  | 38.58 |  |  |  | 1498 |  |  |  | 40.4 |  |  | 1520 |  |  | 42.24 |  |  |  | 1543 |  |  |  | 44.1 |  |  | 1565 |  | 45.98 |  | 1587 |  | 47.88
34000 |  | 1493 |  |  |  | 39.57 |  |  |  |  | 1515 |  |  | 41.43 |  |  |  | 1537 |  |  | 43.31 |  |  |  | 1558 |  |  |  | 45.2 |  |  | 1580 |  |  | 47.11 |  |  |  | 1601 |  |  |  | 49.05 |  |  | 1622 |  | 50.99 |  | 1643 |  | 52.96
36000 |  | 1558 |  |  |  | 44.57 |  |  |  |  | 1579 |  |  | 46.53 |  |  |  | 1600 |  |  | 48.48 |  |  |  | 1620 |  |  |  | 50.46 |  |  | 1641 |  |  | 52.44 |  |  |  | 1661 |  |  |  | 54.44 |  |  | 1681 |  | 56.46 |  | 1701 |  | 58.5
38000 |  | 1624 |  |  |  | 50.05 |  |  |  |  | 1644 |  |  | 52.08 |  |  |  | 1664 |  |  | 54.13 |  |  |  | 1684 |  |  |  | 56.19 |  |  | 1703 |  |  | 58.25 |  |  |  | 1722 |  |  |  | 60.33 |  |  | 1742 |  | 62.43 |  | 1761 |  | 64.54
40000 |  | 1691 |  |  |  | 56.01 |  |  |  |  | 1710 |  |  | 58.13 |  |  |  | 1729 |  |  | 60.26 |  |  |  | 1748 |  |  |  | 62.41 |  |  | 1767 |  |  | 64.55 |  |  |  | 1785 |  |  |  | 66.71 |  |  | — |  | — |  | — |  | —
AIRFLOW (Cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 5.1 | [8 empty] | 5.4 | [6 empty] | 5.7 | [6 empty] | 6
|  | rpm |  |  |  | bhp |  |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp
20000 |  | 1342 |  |  |  | 27.42 |  |  |  |  | 1370 |  |  | 28.95 |  |  |  | 1399 |  |  | 30.48 |  |  |  | 1426 |  |  |  | 32.02
22000 |  | 1378 |  |  |  | 30.33 |  |  |  |  | 1406 |  |  | 31.95 |  |  |  | 1434 |  |  | 33.57 |  |  |  | 1461 |  |  |  | 35.21
24000 |  | 1418 |  |  |  | 33.51 |  |  |  |  | 1445 |  |  | 35.2 |  |  |  | 1471 |  |  | 36.91 |  |  |  | 1497 |  |  |  | 38.64
26000 |  | 1461 |  |  |  | 37 |  |  |  |  | 1487 |  |  | 38.76 |  |  |  | 1512 |  |  | 40.54 |  |  |  | 1537 |  |  |  | 42.35
28000 |  | 1507 |  |  |  | 40.86 |  |  |  |  | 1532 |  |  | 42.69 |  |  |  | 1556 |  |  | 44.54 |  |  |  | 1580 |  |  |  | 46.4
30000 |  | 1557 |  |  |  | 45.12 |  |  |  |  | 1580 |  |  | 47.01 |  |  |  | 1603 |  |  | 48.92 |  |  |  | 1626 |  |  |  | 50.85
32000 |  | 1609 |  |  |  | 49.81 |  |  |  |  | 1631 |  |  | 51.76 |  |  |  | 1653 |  |  | 53.72 |  |  |  | 1675 |  |  |  | 55.72
34000 |  | 1664 |  |  |  | 54.95 |  |  |  |  | 1685 |  |  | 56.96 |  |  |  | 1706 |  |  | 58.99 |  |  |  | 1727 |  |  |  | 61.04
36000 |  | 1721 |  |  |  | 60.57 |  |  |  |  | 1741 |  |  | 62.64 |  |  |  | 1761 |  |  | 64.73 |  |  |  | 1781 |  |  |  | 66.85
38000 |  | 1780 |  |  |  | 66.66 |  |  |  |  | — |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
40000 |  | — |  |  |  | — |  |  |  |  | — |  |  | — |  |  |  | — |  |  | — |  |  |  | — |  |  |  | —
LEGEND | [11 empty] | NOTES: 1. Fan performance is based on wet coils and clean 2-in. filters. 2. For return fan and high-capacity power exhaust units, add compo-
48/50 VAV units only.
bhp — Brake Horsepower *If calculating static pressure for a 48 Series unit, be sure to add gas heat pressure drop from Component Pressure Drop table. | [27 empty] | nent pressure drop for economizer. Do not add component pressure drop for power exhaust. 3. See Component Pressure Drop data table before using Fan Perfor- mance tables. 4. Conversion — bhp to kW: Kilowatts = bhp x .746 Motor efficiency See Physical Data table for motor efficiency.
Performance data (cont)
Fan Performance — Standard Capacity Power Exhaust 48/50P 030-050 Units
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 0.2 | [6 empty] | 0.4 | [5 empty] | 0.6 | [5 empty] | 0.8 | [5 empty] | 1 | [5 empty] | 1.2 |  |  |  |  | 1.4 | [6 empty] | 1.6 |  |  | 1.8 |  |  |  | 2
| rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  |  | bhp |  |  | rpm | bhp |  | rpm |  | bhp |  | rpm |  | bhp
6000 | 380 |  |  | 0.95 |  |  |  | 468 |  |  |  | 1.47 |  | 543 |  |  | 2.01 |  |  | 612 |  |  | 2.6 |  |  | 676 |  |  | 3.24 |  |  | 738 |  | 3.92 |  |  | 796 |  |  |  | 4.64 |  |  | 852 | 5.39 |  | 905 |  | 6.17 |  | 956 |  | 6.98
8000 | 440 |  |  | 1.69 |  |  |  | 523 |  |  |  | 2.4 |  | 591 |  |  | 3.08 |  |  | 651 |  |  | 3.77 |  |  | 706 |  |  | 4.49 |  |  | 759 |  | 5.23 |  |  | 810 |  |  |  | 6.01 |  |  | 859 | 6.82 |  | 907 |  | 7.66 |  | 953 |  | 8.53
10000 | 504 |  |  | 2.73 |  |  |  | 582 |  |  |  | 3.68 |  | 647 |  |  | 4.55 |  |  | 703 |  |  | 5.38 |  |  | 754 |  |  | 6.22 |  |  | 802 |  | 7.06 |  |  | 847 |  |  |  | 7.92 |  |  | 891 | 8.8 |  | 933 |  | 9.7 |  | 975 |  | 10.52
12000 | 575 |  |  | 4.17 |  |  |  | 643 |  |  |  | 5.33 |  | 705 |  |  | 6.42 |  |  | 760 |  |  | 7.45 |  |  | 809 |  |  | 8.44 |  |  | 854 |  | 9.41 |  |  | 896 |  |  |  | 10.38 |  |  | 937 | 11.27 |  | 976 |  | 12.29 |  | — |  | —
14000 | 650 |  |  | 6.09 |  |  |  | 708 |  |  |  | 7.42 |  | 766 |  |  | 8.73 |  |  | 819 |  |  | 9.97 |  |  | 867 |  |  | 11.05 |  |  | 910 |  | 12.22 |  |  | 951 |  |  |  | 13.38 |  |  | 990 | 14.53 |  | — |  | — |  | — |  | —
16000 | 729 |  |  | 8.57 |  |  |  | 778 |  |  |  | 10.02 |  | 829 |  |  | 11.43 |  |  | 879 |  |  | 12.93 |  |  | 926 |  |  | 14.37 |  |  | 969 |  | 15.76 |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
18000 | 809 |  |  | 11.57 |  |  |  | 851 |  |  |  | 13.19 |  | 896 |  |  | 14.9 |  |  | 942 |  |  | 16.61 |  |  | 987 |  |  | 18.29 |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
20000 | 891 |  |  | 15.47 |  |  |  | 927 |  |  |  | 17.22 |  | 967 |  |  | 19.08 |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
48/50P 055-100 Units
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 0.2 | [6 empty] | 0.4 | [5 empty] | 0.6 | [5 empty] | 0.8 | [5 empty] | 1 | [5 empty] | 1.2 |  |  |  |  | 1.4 | [6 empty] | 1.6 |  |  | 1.8 |  |  |  | 2
| rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  |  | bhp |  |  | rpm | bhp |  | rpm |  | bhp |  | rpm |  | bhp
10000 | 416 |  |  | 1.65 |  |  |  | 469 |  |  |  | 2.03 |  | 522 |  |  | 2.47 |  |  | 574 |  |  | 2.97 |  |  | 624 |  |  | 3.51 |  |  | 673 |  | 4.08 |  |  | 720 |  |  |  | 4.66 |  |  | 765 | 5.26 |  | 808 |  | 5.86 |  | 850 |  | 6.47
12000 | 480 |  |  | 2.67 |  |  |  | 524 |  |  |  | 3.09 |  | 568 |  |  | 3.56 |  |  | 612 |  |  | 4.09 |  |  | 656 |  |  | 4.67 |  |  | 699 |  | 5.29 |  |  | 741 |  |  |  | 5.94 |  |  | 782 | 6.61 |  | 822 |  | 7.3 |  | 861 |  | 8
14000 | 546 |  |  | 4.09 |  |  |  | 584 |  |  |  | 4.55 |  | 621 |  |  | 5.05 |  |  | 659 |  |  | 5.61 |  |  | 697 |  |  | 6.21 |  |  | 735 |  | 6.87 |  |  | 772 |  |  |  | 7.56 |  |  | 809 | 8.28 |  | 845 |  | 9.03 |  | 881 |  | 9.8
16000 | 613 |  |  | 5.95 |  |  |  | 647 |  |  |  | 6.46 |  | 680 |  |  | 7 |  |  | 713 |  |  | 7.59 |  |  | 746 |  |  | 8.22 |  |  | 779 |  | 8.9 |  |  | 812 |  |  |  | 9.62 |  |  | 845 | 10.37 |  | 878 |  | 11.16 |  | 910 |  | 11.98
18000 | 682 |  |  | 8.32 |  |  |  | 712 |  |  |  | 8.88 |  | 741 |  |  | 9.47 |  |  | 771 |  |  | 10.1 |  |  | 800 |  |  | 10.76 |  |  | 830 |  | 11.47 |  |  | 859 |  |  |  | 12.21 |  |  | 889 | 13 |  | 918 |  | 13.81 |  | — |  | —
20000 | 752 |  |  | 11.27 |  |  |  | 779 |  |  |  | 11.89 |  | 805 |  |  | 12.53 |  |  | 832 |  |  | 13.19 |  |  | 858 |  |  | 13.9 |  |  | 885 |  | 14.63 |  |  | 911 |  |  |  | 15.41 |  |  | — | — |  | — |  | — |  | — |  | —
22000 | 821 |  |  | 14.86 |  |  |  | 846 |  |  |  | 15.53 |  | 871 |  |  | 16.23 |  |  | 895 |  |  | 16.94 |  |  | 919 |  |  | 17.69 |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
24000 | 892 |  |  | 19.16 |  |  |  | 915 |  |  |  | 19.89 |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
bhp — Brake Horsepower
Fan Performance — Optional Return Fan 48/50P 030-050 Units Return Fan
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 0.2 | [6 empty] | 0.4 | [5 empty] | 0.6 | [5 empty] | 0.8 | [5 empty] | 1 | [5 empty] | 1.2 |  |  |  |  | 1.4 | [6 empty] | 1.6 |  |  | 1.8 |  |  |  | 2
| rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  |  | bhp |  |  | rpm | bhp |  | rpm |  | bhp |  | rpm |  | bhp
6000 | 553 |  |  | 0.86 |  |  |  | 592 |  |  |  | 1.09 |  | 626 |  |  | 1.3 |  |  | 655 |  |  | 1.5 |  |  | 681 |  |  | 1.69 |  |  | 705 |  | 1.88 |  |  | 727 |  |  |  | 2.05 |  |  | 748 | 2.23 |  | 768 |  | 2.4 |  | 787 |  | 2.57
8000 | 711 |  |  | 1.8 |  |  |  | 746 |  |  |  | 2.13 |  | 776 |  |  | 2.44 |  |  | 803 |  |  | 2.73 |  |  | 828 |  |  | 3.01 |  |  | 850 |  | 3.28 |  |  | 872 |  |  |  | 3.54 |  |  | 892 | 3.8 |  | 911 |  | 4.05 |  | 929 |  | 4.29
10000 | 868 |  |  | 3.23 |  |  |  | 899 |  |  |  | 3.67 |  | 927 |  |  | 4.08 |  |  | 952 |  |  | 4.48 |  |  | 975 |  |  | 4.85 |  |  | 997 |  | 5.22 |  |  | 1017 |  |  |  | 5.57 |  |  | 1036 | 5.92 |  | 1055 |  | 6.26 |  | 1072 |  | 6.59
12000 | 1025 |  |  | 5.23 |  |  |  | 1053 |  |  |  | 5.79 |  | 1078 |  |  | 6.32 |  |  | 1102 |  |  | 6.82 |  |  | 1123 |  |  | 7.3 |  |  | 1144 |  | 7.77 |  |  | 1163 |  |  |  | 8.22 |  |  | 1182 | 8.67 |  | 1200 |  | 9.1 |  | 1217 |  | 9.53
14000 | 1181 |  |  | 7.92 |  |  |  | 1206 |  |  |  | 8.6 |  | 1230 |  |  | 9.24 |  |  | 1252 |  |  | 9.85 |  |  | 1272 |  |  | 10.45 |  |  | 1292 |  | 11.03 |  |  | 1310 |  |  |  | 11.59 |  |  | 1328 | 12.14 |  | 1345 |  | 12.67 |  | 1361 |  | 13.2
16000 | 1337 |  |  | 11.38 |  |  |  | 1360 |  |  |  | 12.18 |  | 1382 |  |  | 12.94 |  |  | 1402 |  |  | 13.67 |  |  | 1422 |  |  | 14.39 |  |  | 1440 |  | 15.08 |  |  | 1458 |  |  |  | 15.75 |  |  | 1475 | 16.41 |  | 1491 |  | 17.05 |  | 1507 |  | 17.68
18000 | 1492 |  |  | 15.71 |  |  |  | 1514 |  |  |  | 16.63 |  | 1534 |  |  | 17.51 |  |  | 1553 |  |  | 18.37 |  |  | 1572 |  |  | 19.2 |  |  | 1589 |  | 20.01 |  |  | 1606 |  |  |  | 20.8 |  |  | 1623 | 21.57 |  | 1638 |  | 22.33 |  | 1654 |  | 23.07
20000 | 1647 |  |  | 21 |  |  |  | 1667 |  |  |  | 22.04 |  | 1686 |  |  | 23.05 |  |  | 1704 |  |  | 24.03 |  |  | 1722 |  |  | 24.99 |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 2.2 | [6 empty] | 2.4 | [5 empty] | 2.6 | [5 empty] | 2.8 | [5 empty] | 3 | [5 empty] | 3.2 |  |  |  |  | 3.4 | [6 empty] | 3.6 |  |  | 3.8 |  |  |  | 4
| rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  |  | bhp |  |  | rpm | bhp |  | rpm |  | bhp |  | rpm |  | bhp
6000 | 805 |  |  | 2.74 |  |  |  | 822 |  |  |  | 2.9 |  | 839 |  |  | 3.06 |  |  | 855 |  |  | 3.23 |  |  | 870 |  |  | 3.39 |  |  | 885 |  | 3.55 |  |  | 899 |  |  |  | 3.7 |  |  | 914 | 3.86 |  | 927 |  | 4.01 |  | 941 |  | 4.17
8000 | 947 |  |  | 4.54 |  |  |  | 963 |  |  |  | 4.78 |  | 979 |  |  | 5.01 |  |  | 995 |  |  | 5.24 |  |  | 1010 |  |  | 5.47 |  |  | 1025 |  | 5.7 |  |  | 1039 |  |  |  | 5.93 |  |  | 1053 | 6.15 |  | 1066 |  | 6.37 |  | 1079 |  | 6.59
10000 | 1089 |  |  | 6.91 |  |  |  | 1106 |  |  |  | 7.24 |  | 1121 |  |  | 7.55 |  |  | 1136 |  |  | 7.86 |  |  | 1151 |  |  | 8.17 |  |  | 1165 |  | 8.48 |  |  | 1179 |  |  |  | 8.78 |  |  | 1193 | 9.08 |  | 1206 |  | 9.38 |  | 1219 |  | 9.67
12000 | 1233 |  |  | 9.95 |  |  |  | 1249 |  |  |  | 10.36 |  | 1264 |  |  | 10.76 |  |  | 1279 |  |  | 11.16 |  |  | 1293 |  |  | 11.56 |  |  | 1307 |  | 11.95 |  |  | 1321 |  |  |  | 12.33 |  |  | 1334 | 12.71 |  | 1347 |  | 13.09 |  | 1360 |  | 13.47
14000 | 1377 |  |  | 13.71 |  |  |  | 1393 |  |  |  | 14.22 |  | 1407 |  |  | 14.72 |  |  | 1422 |  |  | 15.22 |  |  | 1436 |  |  | 15.71 |  |  | 1449 |  | 16.19 |  |  | 1463 |  |  |  | 16.66 |  |  | 1476 | 17.13 |  | 1488 |  | 17.6 |  | 1501 |  | 18.06
16000 | 1522 |  |  | 18.3 |  |  |  | 1537 |  |  |  | 18.91 |  | 1552 |  |  | 19.52 |  |  | 1566 |  |  | 20.11 |  |  | 1579 |  |  | 20.7 |  |  | 1593 |  | 21.28 |  |  | 1606 |  |  |  | 21.85 |  |  | 1618 | 22.42 |  | 1631 |  | 22.98 |  | 1643 |  | 23.54
18000 | 1668 |  |  | 23.8 |  |  |  | 1683 |  |  |  | 24.52 |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
20000 | — |  |  | — |  |  |  | — |  |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
Performance data (cont)
Fan Performance — Optional Return Fan 48/50P 055-070 Units Return Fan
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 0.2 | [6 empty] | 0.4 | [5 empty] | 0.6 | [5 empty] | 0.8 | [5 empty] | 1 | [5 empty] | 1.2 |  |  |  |  | 1.4 | [6 empty] | 1.6 |  |  | 1.8 |  |  |  | 2
| rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  |  | bhp |  |  | rpm | bhp |  | rpm |  | bhp |  | rpm |  | bhp
10000 | 600 |  |  | 2.34 |  |  |  | 631 |  |  |  | 2.81 |  | 659 |  |  | 3.28 |  |  | 685 |  |  | 3.77 |  |  | 711 |  |  | 4.26 |  |  | 736 |  | 4.77 |  |  | 759 |  |  |  | 5.29 |  |  | 783 | 5.83 |  | 806 |  | 6.38 |  | 829 |  | 6.96
12000 | 704 |  |  | 3.71 |  |  |  | 731 |  |  |  | 4.27 |  | 756 |  |  | 4.83 |  |  | 779 |  |  | 5.4 |  |  | 802 |  |  | 5.97 |  |  | 824 |  | 6.55 |  |  | 845 |  |  |  | 7.14 |  |  | 866 | 7.75 |  | 887 |  | 8.36 |  | 907 |  | 8.99
14000 | 808 |  |  | 5.51 |  |  |  | 831 |  |  |  | 6.17 |  | 854 |  |  | 6.83 |  |  | 875 |  |  | 7.48 |  |  | 896 |  |  | 8.14 |  |  | 916 |  | 8.8 |  |  | 935 |  |  |  | 9.47 |  |  | 954 | 10.15 |  | 973 |  | 10.83 |  | 991 |  | 11.53
16000 | 911 |  |  | 7.81 |  |  |  | 933 |  |  |  | 8.57 |  | 953 |  |  | 9.32 |  |  | 973 |  |  | 10.07 |  |  | 992 |  |  | 10.82 |  |  | 1010 |  | 11.57 |  |  | 1028 |  |  |  | 12.32 |  |  | 1046 | 13.08 |  | 1063 |  | 13.84 |  | 1079 |  | 14.61
18000 | 1014 |  |  | 10.67 |  |  |  | 1034 |  |  |  | 11.52 |  | 1053 |  |  | 12.37 |  |  | 1071 |  |  | 13.22 |  |  | 1089 |  |  | 14.06 |  |  | 1106 |  | 14.9 |  |  | 1122 |  |  |  | 15.75 |  |  | 1139 | 16.59 |  | 1155 |  | 17.44 |  | 1170 |  | 18.29
20000 | 1117 |  |  | 14.12 |  |  |  | 1136 |  |  |  | 15.09 |  | 1153 |  |  | 16.04 |  |  | 1170 |  |  | 16.98 |  |  | 1186 |  |  | 17.92 |  |  | 1202 |  | 18.86 |  |  | 1218 |  |  |  | 19.79 |  |  | 1233 | 20.73 |  | 1248 |  | 21.66 |  | 1263 |  | 22.6
22000 | 1220 |  |  | 18.26 |  |  |  | 1237 |  |  |  | 19.32 |  | 1254 |  |  | 20.37 |  |  | 1269 |  |  | 21.42 |  |  | 1285 |  |  | 22.45 |  |  | 1300 |  | 23.49 |  |  | 1315 |  |  |  | 24.52 |  |  | 1329 | 25.55 |  | 1343 |  | 26.58 |  | 1357 |  | 27.61
24000 | 1323 |  |  | 23.11 |  |  |  | 1339 |  |  |  | 24.28 |  | 1354 |  |  | 25.44 |  |  | 1369 |  |  | 26.58 |  |  | 1384 |  |  | 27.72 |  |  | 1398 |  | 28.85 |  |  | 1412 |  |  |  | 29.98 |  |  | — | — |  | — |  | — |  | — |  | —
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 2.2 | [6 empty] | 2.4 | [5 empty] | 2.6 | [5 empty] | 2.8 | [5 empty] | 3 | [5 empty] | 3.2 |  |  |  |  | 3.4 | [6 empty] | 3.6 |  |  | 3.8 |  |  |  | 4
| rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  |  | bhp |  |  | rpm | bhp |  | rpm |  | bhp |  | rpm |  | bhp
10000 | 851 |  |  | 7.55 |  |  |  | 873 |  |  |  | 8.17 |  | 895 |  |  | 8.8 |  |  | 916 |  |  | 9.45 |  |  | 938 |  |  | 10.13 |  |  | 959 |  | 10.83 |  |  | 980 |  |  |  | 11.55 |  |  | 1001 | 12.3 |  | 1022 |  | 13.07 |  | 1043 |  | 13.86
12000 | 926 |  |  | 9.63 |  |  |  | 946 |  |  |  | 10.28 |  | 965 |  |  | 10.95 |  |  | 984 |  |  | 11.63 |  |  | 1002 |  |  | 12.33 |  |  | 1021 |  | 13.05 |  |  | 1039 |  |  |  | 13.78 |  |  | 1058 | 14.53 |  | 1076 |  | 15.3 |  | 1094 |  | 16.08
14000 | 1009 |  |  | 12.23 |  |  |  | 1026 |  |  |  | 12.94 |  | 1044 |  |  | 13.66 |  |  | 1061 |  |  | 14.4 |  |  | 1078 |  |  | 15.15 |  |  | 1094 |  | 15.91 |  |  | 1111 |  |  |  | 16.68 |  |  | 1127 | 17.46 |  | 1143 |  | 18.26 |  | 1159 |  | 19.07
16000 | 1096 |  |  | 15.39 |  |  |  | 1112 |  |  |  | 16.17 |  | 1128 |  |  | 16.96 |  |  | 1143 |  |  | 17.76 |  |  | 1159 |  |  | 18.57 |  |  | 1174 |  | 19.38 |  |  | 1189 |  |  |  | 20.22 |  |  | 1204 | 21.05 |  | 1219 |  | 21.9 |  | 1234 |  | 22.75
18000 | 1185 |  |  | 19.14 |  |  |  | 1201 |  |  |  | 20.01 |  | 1215 |  |  | 20.87 |  |  | 1230 |  |  | 21.74 |  |  | 1244 |  |  | 22.62 |  |  | 1259 |  | 23.5 |  |  | 1273 |  |  |  | 24.4 |  |  | 1287 | 25.3 |  | 1300 |  | 26.21 |  | 1314 |  | 27.13
20000 | 1277 |  |  | 23.54 |  |  |  | 1291 |  |  |  | 24.49 |  | 1305 |  |  | 25.43 |  |  | 1319 |  |  | 26.38 |  |  | 1333 |  |  | 27.34 |  |  | 1346 |  | 28.3 |  |  | 1359 |  |  |  | 29.27 |  |  | 1372 | 30.24 |  | — |  | — |  | — |  | —
22000 | 1370 |  |  | 28.64 |  |  |  | 1384 |  |  |  | 29.67 |  | 1397 |  |  | 30.7 |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
24000 | — |  |  | — |  |  |  | — |  |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
Fan Performance — Optional Return Fan (48/50P2,P3,P4,P5075-100 Units)
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 0.2 | [6 empty] | 0.4 | [5 empty] | 0.6 | [5 empty] | 0.8 | [5 empty] | 1 | [5 empty] | 1.2 |  |  |  |  | 1.4 | [6 empty] | 1.6 |  |  | 1.8 |  |  |  | 2
| rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  |  | bhp |  |  | rpm | bhp |  | rpm |  | bhp |  | rpm |  | bhp
14000 | 594 |  |  | 3.61 |  |  |  | 594 |  |  |  | 3.61 |  | 617 |  |  | 4.02 |  |  | 646 |  |  | 4.58 |  |  | 674 |  |  | 5.16 |  |  | 700 |  | 5.75 |  |  | 725 |  |  |  | 6.36 |  |  | 749 | 6.99 |  | 772 |  | 7.62 |  | 795 |  | 8.25
16000 | 619 |  |  | 4.09 |  |  |  | 652 |  |  |  | 4.76 |  | 681 |  |  | 5.4 |  |  | 708 |  |  | 6.02 |  |  | 733 |  |  | 6.65 |  |  | 757 |  | 7.29 |  |  | 781 |  |  |  | 7.94 |  |  | 803 | 8.61 |  | 825 |  | 9.3 |  | 847 |  | 9.99
18000 | 687 |  |  | 5.57 |  |  |  | 718 |  |  |  | 6.35 |  | 746 |  |  | 7.07 |  |  | 771 |  |  | 7.76 |  |  | 795 |  |  | 8.45 |  |  | 817 |  | 9.14 |  |  | 839 |  |  |  | 9.85 |  |  | 860 | 10.56 |  | 881 |  | 11.2 |  | 901 |  | 11.96
20000 | 756 |  |  | 7.37 |  |  |  | 786 |  |  |  | 8.25 |  | 812 |  |  | 9.06 |  |  | 836 |  |  | 9.84 |  |  | 858 |  |  | 10.59 |  |  | 879 |  | 11.25 |  |  | 900 |  |  |  | 12.03 |  |  | 920 | 12.82 |  | 939 |  | 13.62 |  | 958 |  | 14.43
22000 | 825 |  |  | 9.5 |  |  |  | 853 |  |  |  | 10.5 |  | 878 |  |  | 11.31 |  |  | 901 |  |  | 12.2 |  |  | 923 |  |  | 13.06 |  |  | 943 |  | 13.9 |  |  | 962 |  |  |  | 14.75 |  |  | 981 | 15.6 |  | 1000 |  | 16.46 |  | 1018 |  | 17.33
24000 | 895 |  |  | 11.94 |  |  |  | 922 |  |  |  | 13.08 |  | 945 |  |  | 14.12 |  |  | 967 |  |  | 15.1 |  |  | 988 |  |  | 16.05 |  |  | 1007 |  | 16.99 |  |  | 1026 |  |  |  | 17.91 |  |  | 1044 | 18.83 |  | 1061 |  | 19.76 |  | 1079 |  | 20.69
26000 | 965 |  |  | 14.94 |  |  |  | 990 |  |  |  | 16.21 |  | 1013 |  |  | 17.36 |  |  | 1034 |  |  | 18.46 |  |  | 1054 |  |  | 19.51 |  |  | 1073 |  | 20.53 |  |  | 1091 |  |  |  | 21.54 |  |  | 1108 | 22.54 |  | 1125 |  | 23.54 |  | 1141 |  | 24.54
28000 | 1035 |  |  | 18.43 |  |  |  | 1059 |  |  |  | 19.81 |  | 1081 |  |  | 21.09 |  |  | 1101 |  |  | 22.29 |  |  | 1120 |  |  | 23.45 |  |  | 1138 |  | 24.57 |  |  | 1156 |  |  |  | 25.67 |  |  | 1172 | 26.76 |  | 1189 |  | 27.83 |  | 1204 |  | 28.91
30000 | 1105 |  |  | 22.42 |  |  |  | 1128 |  |  |  | 23.93 |  | 1149 |  |  | 25.33 |  |  | 1169 |  |  | 26.65 |  |  | 1187 |  |  | 27.92 |  |  | 1205 |  | 29.14 |  |  | 1222 |  |  |  | 30.34 |  |  | 1238 | 31.51 |  | 1253 |  | 32.67 |  | 1269 |  | 33.83
32000 | 1176 |  |  | 26.96 |  |  |  | 1198 |  |  |  | 28.59 |  | 1218 |  |  | 30.11 |  |  | 1237 |  |  | 31.55 |  |  | 1255 |  |  | 32.93 |  |  | 1272 |  | 34.26 |  |  | 1288 |  |  |  | 35.56 |  |  | 1304 | 36.83 |  | 1319 |  | 38.08 |  | 1333 |  | 39.32
34000 | 1246 |  |  | 32.09 |  |  |  | 1267 |  |  |  | 33.83 |  | 1287 |  |  | 35.47 |  |  | 1305 |  |  | 37.03 |  |  | 1322 |  |  | 38.53 |  |  | 1339 |  | 39.97 |  |  | 1355 |  |  |  | 41.38 |  |  | 1370 | 42.75 |  | 1385 |  | 44.1 |  | 1399 |  | 45.43
36000 | 1317 |  |  | 37.83 |  |  |  | 1337 |  |  |  | 39.69 |  | 1356 |  |  | 41.46 |  |  | 1374 |  |  | 43.14 |  |  | 1391 |  |  | 44.75 |  |  | 1407 |  | 46.31 |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
38000 | 1388 |  |  | 44.22 |  |  |  | 1407 |  |  |  | 46.21 |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
40000 | — |  |  | — |  |  |  | — |  |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
AIRFLOW (Cfm) | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
| 2.2 | [6 empty] | 2.4 | [5 empty] | 2.6 | [5 empty] | 2.8 | [5 empty] | 3 | [5 empty] | 3.2 |  |  |  |  | 3.4 | [6 empty] | 3.6 |  |  | 3.8 |  |  |  | 4
| rpm |  |  | bhp |  |  |  | rpm |  |  |  | bhp |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  |  | bhp |  |  | rpm |  | bhp |  |  | rpm |  |  |  | bhp |  |  | rpm | bhp |  | rpm |  | bhp |  | rpm |  | bhp
14000 | 816 |  |  | 8.89 |  |  |  | 836 |  |  |  | 9.52 |  | 856 |  |  | 10.15 |  |  | 874 |  |  | 10.67 |  |  | 892 |  |  | 11.31 |  |  | 910 |  | 11.94 |  |  | 926 |  |  |  | 12.57 |  |  | 942 | 13.19 |  | 958 |  | 13.8 |  | 973 |  | 14.42
16000 | 867 |  |  | 10.59 |  |  |  | 887 |  |  |  | 11.31 |  | 907 |  |  | 12.05 |  |  | 926 |  |  | 12.78 |  |  | 944 |  |  | 13.52 |  |  | 961 |  | 14.25 |  |  | 978 |  |  |  | 14.98 |  |  | 995 | 15.71 |  | 1011 |  | 16.44 |  | 1026 |  | 17.16
18000 | 921 |  |  | 12.74 |  |  |  | 940 |  |  |  | 13.52 |  | 959 |  |  | 14.33 |  |  | 977 |  |  | 15.13 |  |  | 995 |  |  | 15.95 |  |  | 1012 |  | 16.77 |  |  | 1029 |  |  |  | 17.59 |  |  | 1046 | 18.42 |  | 1062 |  | 19.24 |  | 1078 |  | 20.07
20000 | 977 |  |  | 15.25 |  |  |  | 995 |  |  |  | 16.1 |  | 1013 |  |  | 16.96 |  |  | 1031 |  |  | 17.82 |  |  | 1048 |  |  | 18.7 |  |  | 1065 |  | 19.59 |  |  | 1081 |  |  |  | 20.49 |  |  | 1097 | 21.39 |  | 1113 |  | 22.3 |  | 1129 |  | 23.21
22000 | 1035 |  |  | 18.21 |  |  |  | 1052 |  |  |  | 19.1 |  | 1069 |  |  | 20.01 |  |  | 1086 |  |  | 20.93 |  |  | 1103 |  |  | 21.86 |  |  | 1119 |  | 22.81 |  |  | 1135 |  |  |  | 23.76 |  |  | 1150 | 24.73 |  | 1166 |  | 25.71 |  | 1181 |  | 26.69
24000 | 1095 |  |  | 21.62 |  |  |  | 1112 |  |  |  | 22.58 |  | 1128 |  |  | 23.54 |  |  | 1144 |  |  | 24.51 |  |  | 1159 |  |  | 25.49 |  |  | 1175 |  | 26.49 |  |  | 1190 |  |  |  | 27.5 |  |  | 1205 | 28.52 |  | 1220 |  | 29.55 |  | 1234 |  | 30.58
26000 | 1157 |  |  | 25.54 |  |  |  | 1173 |  |  |  | 26.55 |  | 1188 |  |  | 27.57 |  |  | 1203 |  |  | 28.59 |  |  | 1218 |  |  | 29.64 |  |  | 1233 |  | 30.68 |  |  | 1247 |  |  |  | 31.74 |  |  | 1262 | 32.81 |  | 1276 |  | 33.89 |  | 1290 |  | 34.98
28000 | 1220 |  |  | 29.98 |  |  |  | 1235 |  |  |  | 31.06 |  | 1249 |  |  | 32.14 |  |  | 1264 |  |  | 33.23 |  |  | 1278 |  |  | 34.32 |  |  | 1292 |  | 35.42 |  |  | 1306 |  |  |  | 36.53 |  |  | 1320 | 37.65 |  | 1334 |  | 38.78 |  | 1347 |  | 39.93
30000 | 1283 |  |  | 34.98 |  |  |  | 1298 |  |  |  | 36.13 |  | 1312 |  |  | 37.28 |  |  | 1326 |  |  | 38.42 |  |  | 1340 |  |  | 39.58 |  |  | 1353 |  | 40.74 |  |  | 1367 |  |  |  | 41.92 |  |  | 1380 | 43.09 |  | 1393 |  | 44.27 |  | 1406 |  | 45.46
32000 | 1348 |  |  | 40.55 |  |  |  | 1362 |  |  |  | 41.78 |  | 1375 |  |  | 43 |  |  | 1389 |  |  | 44.22 |  |  | 1402 |  |  | 45.45 |  |  | 1415 |  | 46.67 |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
34000 | 1413 |  |  | 46.75 |  |  |  | — |  |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
36000 | — |  |  | — |  |  |  | — |  |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
38000 | — |  |  | — |  |  |  | — |  |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
40000 | — |  |  | — |  |  |  | — |  |  |  | — |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  |  | — |  | — |  |  | — |  |  |  | — |  |  | — | — |  | — |  | — |  | — |  | —
bhp — Brake Horsepower
Performance data (cont)
Fan Performance — Optional High-Capacity Power Exhaust (48/50P2,P3,P4,P5075-100)
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 0.2 | [12 empty] | 0.4 | [11 empty] | 0.6 | [9 empty] | 0.8 | [9 empty] | 1
|  | rpm | [6 empty] | bhp | [5 empty] | rpm |  |  |  |  | bhp | [6 empty] | rpm |  |  |  |  | bhp |  |  |  |  | rpm | [6 empty] | bhp |  |  | rpm |  |  |  | bhp
14000 |  | 436 | [6 empty] | 3.79 | [5 empty] | 480 |  |  |  |  | 4.28 | [6 empty] | 520 |  |  |  |  | 4.86 |  |  |  |  | 557 | [6 empty] | 5.48 |  |  | 592 |  |  |  | 6.11
16000 |  | 486 | [6 empty] | 5.37 | [5 empty] | 526 |  |  |  |  | 5.86 | [6 empty] | 563 |  |  |  |  | 6.47 |  |  |  |  | 597 | [6 empty] | 7.12 |  |  | 629 |  |  |  | 7.8
18000 |  | 536 | [6 empty] | 7.37 | [5 empty] | 574 |  |  |  |  | 7.84 | [6 empty] | 608 |  |  |  |  | 8.45 |  |  |  |  | 639 | [6 empty] | 9.14 |  |  | 670 |  |  |  | 9.86
20000 |  | 588 | [6 empty] | 9.81 | [5 empty] | 622 |  |  |  |  | 10.26 | [6 empty] | 654 |  |  |  |  | 10.87 |  |  |  |  | 684 | [6 empty] | 11.57 |  |  | 712 |  |  |  | 12.32
22000 |  | 639 | [6 empty] | 12.75 | [5 empty] | 671 |  |  |  |  | 13.16 | [6 empty] | 701 |  |  |  |  | 13.76 |  |  |  |  | 730 | [6 empty] | 14.46 |  |  | 757 |  |  |  | 15.23
24000 |  | 692 | [6 empty] | 16.21 | [5 empty] | 722 |  |  |  |  | 16.59 | [6 empty] | 750 |  |  |  |  | 17.16 |  |  |  |  | 777 | [6 empty] | 17.86 |  |  | 802 |  |  |  | 18.65
26000 |  | 745 | [6 empty] | 20.24 | [5 empty] | 772 |  |  |  |  | 20.58 | [6 empty] | 799 |  |  |  |  | 21.13 |  |  |  |  | 824 | [6 empty] | 21.82 |  |  | 849 |  |  |  | 22.6
28000 |  | 798 | [6 empty] | 24.87 | [5 empty] | 824 |  |  |  |  | 25.18 | [6 empty] | 849 |  |  |  |  | 25.7 |  |  |  |  | 873 | [6 empty] | 26.37 |  |  | 896 |  |  |  | 27.14
30000 |  | 851 | [6 empty] | 30.15 | [5 empty] | 875 |  |  |  |  | 30.43 | [6 empty] | 899 |  |  |  |  | 30.91 |  |  |  |  | 922 | [6 empty] | 31.55 |  |  | 944 |  |  |  | 32.31
32000 |  | 905 | [6 empty] | 36.1 | [5 empty] | 928 |  |  |  |  | 36.35 | [6 empty] | 950 |  |  |  |  | 36.8 |  |  |  |  | 972 | [6 empty] | 37.41 |  |  | 993 |  |  |  | 38.14
34000 |  | 959 | [6 empty] | 42.76 | [5 empty] | 980 |  |  |  |  | 42.98 | [6 empty] | 1001 |  |  |  |  | 43.4 |  |  |  |  | 1022 | [6 empty] | 43.98 |  |  | 1042 |  |  |  | 44.69
36000 |  | 1013 | [6 empty] | 50.17 | [5 empty] | 1033 |  |  |  |  | 50.37 | [6 empty] | 1053 |  |  |  |  | 50.75 |  |  |  |  | 1072 | [6 empty] | 51.3 |  |  | 1092 |  |  |  | 51.98
38000 |  | 1067 | [6 empty] | 58.36 | [5 empty] | 1086 |  |  |  |  | 58.53 | [6 empty] | 1105 |  |  |  |  | 58.89 |  |  |  |  | 1124 | [6 empty] | 59.4 |  |  | 1142 |  |  |  | 60.05
40000 |  | 1121 | [6 empty] | 67.37 | [5 empty] | 1139 |  |  |  |  | 67.52 | [6 empty] | 1157 |  |  |  |  | 67.84 |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 1.2 | [12 empty] | 1.4 | [11 empty] | 1.6 | [9 empty] | 1.8 | [9 empty] | 2
|  | rpm | [6 empty] | bhp | [5 empty] | rpm |  |  |  |  | bhp | [6 empty] | rpm |  |  |  |  | bhp |  |  |  |  | rpm | [6 empty] | bhp |  |  | rpm |  |  |  | bhp
14000 |  | 626 | [6 empty] | 6.76 | [5 empty] | 659 |  |  |  |  | 7.42 | [6 empty] | 691 |  |  |  |  | 8.09 |  |  |  |  | 722 | [6 empty] | 8.77 |  |  | 752 |  |  |  | 9.45
16000 |  | 660 | [6 empty] | 8.5 | [5 empty] | 690 |  |  |  |  | 9.22 | [6 empty] | 720 |  |  |  |  | 9.94 |  |  |  |  | 749 | [6 empty] | 10.68 |  |  | 777 |  |  |  | 11.42
18000 |  | 698 | [6 empty] | 10.6 | [5 empty] | 726 |  |  |  |  | 11.36 | [6 empty] | 754 |  |  |  |  | 12.14 |  |  |  |  | 780 | [6 empty] | 12.93 |  |  | 806 |  |  |  | 13.73
20000 |  | 739 | [6 empty] | 13.1 | [5 empty] | 765 |  |  |  |  | 13.91 | [6 empty] | 791 |  |  |  |  | 14.73 |  |  |  |  | 816 | [6 empty] | 15.57 |  |  | 840 |  |  |  | 16.41
22000 |  | 782 | [6 empty] | 16.05 | [5 empty] | 807 |  |  |  |  | 16.89 | [6 empty] | 831 |  |  |  |  | 17.75 |  |  |  |  | 854 | [6 empty] | 18.63 |  |  | 877 |  |  |  | 19.52
24000 |  | 827 | [6 empty] | 19.48 | [5 empty] | 850 |  |  |  |  | 20.35 | [6 empty] | 873 |  |  |  |  | 21.25 |  |  |  |  | 895 | [6 empty] | 22.16 |  |  | 917 |  |  |  | 23.1
26000 |  | 872 | [6 empty] | 23.44 | [5 empty] | 894 |  |  |  |  | 24.33 | [6 empty] | 916 |  |  |  |  | 25.26 |  |  |  |  | 937 | [6 empty] | 26.21 |  |  | 958 |  |  |  | 27.17
28000 |  | 918 | [6 empty] | 27.99 | [5 empty] | 940 |  |  |  |  | 28.89 | [6 empty] | 961 |  |  |  |  | 29.83 |  |  |  |  | 981 | [6 empty] | 30.81 |  |  | 1001 |  |  |  | 31.81
30000 |  | 965 | [6 empty] | 33.15 | [5 empty] | 986 |  |  |  |  | 34.06 | [6 empty] | 1006 |  |  |  |  | 35.01 |  |  |  |  | 1026 | [6 empty] | 36 |  |  | 1045 |  |  |  | 37.02
32000 |  | 1013 | [6 empty] | 38.98 | [5 empty] | 1033 |  |  |  |  | 39.88 | [6 empty] | 1053 |  |  |  |  | 40.84 |  |  |  |  | 1071 | [6 empty] | 41.84 |  |  | 1090 |  |  |  | 42.88
34000 |  | 1062 | [6 empty] | 45.5 | [5 empty] | 1081 |  |  |  |  | 46.39 | [6 empty] | 1100 |  |  |  |  | 47.35 |  |  |  |  | 1118 | [6 empty] | 48.36 |  |  | 1136 |  |  |  | 49.41
36000 |  | 1111 | [6 empty] | 52.77 | [5 empty] | 1129 |  |  |  |  | 53.65 | [6 empty] | 1147 |  |  |  |  | 54.59 |  |  |  |  | 1165 | [6 empty] | 55.6 |  |  | — |  |  |  | —
38000 |  | 1160 | [6 empty] | 60.81 | [5 empty] | — |  |  |  |  | — | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
40000 |  | — | [6 empty] | — | [5 empty] | — |  |  |  |  | — | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 2.2 | [12 empty] | 2.4 | [11 empty] | 2.6 | [9 empty] | 2.8 | [9 empty] | 3
|  | rpm | [6 empty] | bhp | [5 empty] | rpm |  |  |  |  | bhp | [6 empty] | rpm |  |  |  |  | bhp |  |  |  |  | rpm | [6 empty] | bhp |  |  | rpm |  |  |  | bhp
14000 |  | 782 | [6 empty] | 10.14 | [5 empty] | 811 |  |  |  |  | 10.83 | [6 empty] | 839 |  |  |  |  | 11.53 |  |  |  |  | 866 | [6 empty] | 12.23 |  |  | 892 |  |  |  | 12.93
16000 |  | 805 | [6 empty] | 12.18 | [5 empty] | 832 |  |  |  |  | 12.93 | [6 empty] | 858 |  |  |  |  | 13.69 |  |  |  |  | 884 | [6 empty] | 14.46 |  |  | 910 |  |  |  | 15.23
18000 |  | 832 | [6 empty] | 14.53 | [5 empty] | 858 |  |  |  |  | 15.35 | [6 empty] | 882 |  |  |  |  | 16.17 |  |  |  |  | 907 | [6 empty] | 16.99 |  |  | 931 |  |  |  | 17.82
20000 |  | 864 | [6 empty] | 17.27 | [5 empty] | 888 |  |  |  |  | 18.14 | [6 empty] | 911 |  |  |  |  | 19.01 |  |  |  |  | 934 | [6 empty] | 19.89 |  |  | 957 |  |  |  | 20.78
22000 |  | 900 | [6 empty] | 20.43 | [5 empty] | 922 |  |  |  |  | 21.34 | [6 empty] | 944 |  |  |  |  | 22.26 |  |  |  |  | 966 | [6 empty] | 23.2 |  |  | 987 |  |  |  | 24.14
24000 |  | 938 | [6 empty] | 24.04 | [5 empty] | 959 |  |  |  |  | 25 | [6 empty] | 980 |  |  |  |  | 25.98 |  |  |  |  | 1000 | [6 empty] | 26.95 |  |  | 1020 |  |  |  | 27.94
26000 |  | 979 | [6 empty] | 28.17 | [5 empty] | 998 |  |  |  |  | 29.16 | [6 empty] | 1018 |  |  |  |  | 30.17 |  |  |  |  | 1037 | [6 empty] | 31.2 |  |  | 1057 |  |  |  | 32.23
28000 |  | 1020 | [6 empty] | 32.83 | [5 empty] | 1040 |  |  |  |  | 33.86 | [6 empty] | 1058 |  |  |  |  | 34.91 |  |  |  |  | 1077 | [6 empty] | 35.98 |  |  | 1095 |  |  |  | 37.05
30000 |  | 1064 | [6 empty] | 38.07 | [5 empty] | 1082 |  |  |  |  | 39.14 | [6 empty] | 1100 |  |  |  |  | 40.23 |  |  |  |  | 1118 | [6 empty] | 41.33 |  |  | 1135 |  |  |  | 42.44
32000 |  | 1108 | [6 empty] | 43.95 | [5 empty] | 1126 |  |  |  |  | 45.05 | [6 empty] | 1143 |  |  |  |  | 46.16 |  |  |  |  | 1160 | [6 empty] | 47.29 |  |  | — |  |  |  | —
34000 |  | 1153 | [6 empty] | 50.49 | [5 empty] | 1170 |  |  |  |  | 51.61 | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
36000 |  | — | [6 empty] | — | [5 empty] | — |  |  |  |  | — | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
38000 |  | — | [6 empty] | — | [5 empty] | — |  |  |  |  | — | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
40000 |  | — | [6 empty] | — | [5 empty] | — |  |  |  |  | — | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
AIRFLOW (cfm) |  | AVAILABLE EXTERNAL STATIC PRESSURE (in. wg)
|  | 3.2 | [12 empty] | 3.4 | [11 empty] | 3.6 | [9 empty] | 3.8 | [9 empty] | 4
|  | rpm | [6 empty] | bhp | [5 empty] | rpm |  |  |  |  | bhp | [6 empty] | rpm |  |  |  |  | bhp |  |  |  |  | rpm | [6 empty] | bhp |  |  | rpm |  |  |  | bhp
14000 |  | 918 | [6 empty] | 13.64 | [5 empty] | 943 |  |  |  |  | 14.34 | [6 empty] | 967 |  |  |  |  | 15.05 |  |  |  |  | 990 | [6 empty] | 15.75 |  |  | 1013 |  |  |  | 16.46
16000 |  | 934 | [6 empty] | 16 | [5 empty] | 959 |  |  |  |  | 16.77 | [6 empty] | 983 |  |  |  |  | 17.55 |  |  |  |  | 1006 | [6 empty] | 18.33 |  |  | 1029 |  |  |  | 19.11
18000 |  | 955 | [6 empty] | 18.66 | [5 empty] | 978 |  |  |  |  | 19.5 | [6 empty] | 1001 |  |  |  |  | 20.34 |  |  |  |  | 1024 | [6 empty] | 21.19 |  |  | 1046 |  |  |  | 22.04
20000 |  | 979 | [6 empty] | 21.67 | [5 empty] | 1001 |  |  |  |  | 22.57 | [6 empty] | 1023 |  |  |  |  | 23.47 |  |  |  |  | 1045 | [6 empty] | 24.38 |  |  | 1066 |  |  |  | 25.29
22000 |  | 1008 | [6 empty] | 25.08 | [5 empty] | 1029 |  |  |  |  | 26.03 | [6 empty] | 1050 |  |  |  |  | 26.99 |  |  |  |  | 1070 | [6 empty] | 27.96 |  |  | 1090 |  |  |  | 28.92
24000 |  | 1040 | [6 empty] | 28.93 | [5 empty] | 1060 |  |  |  |  | 29.94 | [6 empty] | 1080 |  |  |  |  | 30.94 |  |  |  |  | 1099 | [6 empty] | 31.96 |  |  | 1118 |  |  |  | 32.98
26000 |  | 1075 | [6 empty] | 33.27 | [5 empty] | 1094 |  |  |  |  | 34.32 | [6 empty] | 1113 |  |  |  |  | 35.37 |  |  |  |  | 1131 | [6 empty] | 36.44 |  |  | 1149 |  |  |  | 37.51
28000 |  | 1113 | [6 empty] | 38.14 | [5 empty] | 1131 |  |  |  |  | 39.23 | [6 empty] | 1148 |  |  |  |  | 40.33 |  |  |  |  | 1166 | [6 empty] | 41.44 |  |  | — |  |  |  | —
30000 |  | 1152 | [6 empty] | 43.56 | [5 empty] | 1169 |  |  |  |  | 44.69 | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
32000 |  | — | [6 empty] | — | [5 empty] | — |  |  |  |  | — | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
34000 |  | — | [6 empty] | — | [5 empty] | — |  |  |  |  | — | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
36000 |  | — | [6 empty] | — | [5 empty] | — |  |  |  |  | — | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
38000 |  | — | [6 empty] | — | [5 empty] | — |  |  |  |  | — | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
40000 |  | — | [6 empty] | — | [5 empty] | — |  |  |  |  | — | [6 empty] | — |  |  |  |  | — |  |  |  |  | — | [6 empty] | — |  |  | — |  |  |  | —
LEGEND bhp — Brake Horsepower