## Table 1
SPECIFICATIONS | [18 empty] | 13 TON
General Data |  |  | Nominal Tonnage | [7 empty] | 13 Ton | [7 empty] | 13 Ton
|  |  | Model Number | [7 empty] | LCM156U4M | [7 empty] | LCM156U4V
|  |  | Efficiency Type | [7 empty] | Ultra-High | [7 empty] | Ultra-High
|  |  | Blower Type | [7 empty] | SZVAV (Single Zone Variable Air Volume) | [7 empty] | VAV (Variable Air Volume)
Cooling Performance |  |  | Gross Cooling Capacity - Btuh | [7 empty] | 154000 | [7 empty] | 154000
|  |  | 1 Net Cooling Cap |  |  |  | acity - Btuh |  |  |  | 150000 | [7 empty] | 150000
|  |  | 1 AHRI Rated Ai |  |  |  | r Flow - cfm |  |  |  | 4250 | [7 empty] | 4250
|  |  | Total Unit Power - kW | [7 empty] | 12.3 | [7 empty] | 12.3
|  |  | 1 IEER |  |  |  | (Btuh/Watt) |  |  |  | 19 | [7 empty] | 18.5
|  |  | 1 EER |  |  |  | (Btuh/Watt) |  |  |  | 12.2 | [7 empty] | 12.2
Refrigerant Charge |  |  | Refrigerant Type | [7 empty] | R-410A | [7 empty] | R-410A
|  |  | Without Reheat |  |  |  | Circuit 1 |  |  |  | 16 lbs. 12 oz. | [7 empty] | 16 lbs. 12 oz.
[7 empty] | Circuit 2 |  |  |  | 9 lbs. 9 oz. | [7 empty] | 9 lbs. 9 oz.
[7 empty] | Circuit 3 |  |  |  | 9 lbs. 8 oz. | [7 empty] | 9 lbs. 8 oz.
|  |  | With Reheat |  |  |  | Circuit 1 |  |  |  | 21 lbs. 3 oz. | [7 empty] | - - -
[7 empty] | Circuit 2 |  |  |  | 12 lbs. 8 oz. | [7 empty] | - - -
[7 empty] | Circuit 3 |  |  |  | 9 lbs. 8 oz. | [7 empty] | - - -
Electric Heating Options Available | [10 empty] | 15-30-45-60 kW
Compressor Type (number) | [10 empty] | Variable Capacity Scroll (1) Fixed Capacity Scroll (2)
Outdoor Coils |  |  | Net face area (total) - sq. ft. | [7 empty] | 55.2 | [7 empty] | 55.2
|  |  | Tube diameter - in. | [7 empty] | 3/8 | [7 empty] | 3/8
|  |  | Number of rows | [7 empty] | 2 | [7 empty] | 2
|  |  | Fins per inch | [7 empty] | 20 | [7 empty] | 20
Outdoor Coil Fans |  |  | Motor - (No.) horsepower | [7 empty] | (4) 1/3 ECM | [7 empty] | (4) 1/3 ECM
[7 empty] | Motor rpm |  |  |  | 450-1075 | [7 empty] | 450-1075
|  |  | Total Motor watts | [7 empty] | 155 - 1150 | [7 empty] | 155 - 1150
|  |  | Diameter - (No.) in. | [7 empty] | (4) 24 | [7 empty] | (4) 24
|  |  | Number of blades | [7 empty] | 3 | [7 empty] | 3
|  |  | Total Air volume - cfm | [7 empty] | 16000 | [7 empty] | 16000
Indoor Coils |  |  | Net face area (total) - sq. ft. | [7 empty] | 21.4 | [7 empty] | 21.4
|  |  | Tube diameter - in. | [7 empty] | 3/8 | [7 empty] | 3/8
|  |  | Number of rows | [7 empty] | 3 | [7 empty] | 3
|  |  | Fins per inch | [7 empty] | 14 | [7 empty] | 14
|  |  | Drain connection - No. and size | [7 empty] | (1) 1 in. FPT | [7 empty] | (1) 1 in. FPT
|  |  | Expansion device type | [7 empty] | Balance port TXV, removable head
2 Indoor |  |  | Nominal motor output | [7 empty] | 3 hp, 5 hp
Blower |  |  | Max. usable motor output (US) | [7 empty] | 3.45 hp, 5.75 hp
and Drive Selection |  |  | Motor - Drive kit number | [7 empty] | 3 hp Kit 1 535-725 rpm Kit 2 710-965 rpm 5 hp Kit 3 685-856 rpm Kit 4 850-1045 rpm Kit 5 945-1185 rpm
|  |  | Blower wheel nominal D x W - in. | [7 empty] | (2) 15 x 15 in. | [7 empty] | (2) 15 x 15 in.
Filters | [6 empty] | Type of filter |  |  |  | MERV 4, Disposable
|  |  | Number and size - in. | [7 empty] | (6) 24 x 24 x 2
Electrical characteristics | [10 empty] | 208/230V, 460V, or 575V - 60 hz -3 phase
NOTE - Net capacity includes evaporator blower motor heat deduction. Gross capacity does not include evaporator blower motor heat deduction. 1 AHRI Certified to AHRI Standard 340/360; 95°F outdoor air temperature and 80°F db/67°F wb entering evaporator air; minimum external duct static pressure. 2 Using total air volume and system static pressure requirements determine from blower performance tables rpm and motor output required. Maximum usable output of motors furnished are shown. In Canada, nominal motor output is also maximum usable motor output. If motors of comparable output are used, be sure to keep within the service factor limitations outlined on the motor nameplate. NOTE – Blower motor service factor = 1.0.
SPECIFICATIONS | [18 empty] | 15 TON ¦ 17.5 TON
General Data |  |  | Nominal Tonnage | [7 empty] | 15 Ton |  |  |  | 15 Ton |  |  |  | 17.5 Ton |  |  |  | 17.5 Ton
|  |  | Model Number | [7 empty] | LCM180U4M |  |  |  | LCM180U4V |  |  |  | LCM210U4M |  |  |  | LCM210U4V
|  |  | Efficiency Type | [7 empty] | Ultra-High |  |  |  | Ultra-High |  |  |  | Ultra-High |  |  |  | Ultra-High
|  |  | Blower Type | [7 empty] | SZVAV (Single Zone Variable Air Volume) |  |  |  | VAV (Variable Air Volume) |  |  |  | SZVAV (Single Zone Variable Air Volume) |  |  |  | VAV (Variable Air Volume)
Cooling Performance |  |  | Gross Cooling Capacity - Btuh | [7 empty] | 176000 |  |  |  | 176000 |  |  |  | 206000 |  |  |  | 206000
|  |  | 1 Net Cooling Cap |  |  |  | acity - Btuh |  |  |  | 172000 |  |  |  | 172000 |  |  |  | 200000 |  |  |  | 200000
|  |  | 1 AHRI Rated Ai |  |  |  | r Flow - cfm |  |  |  | 5250 |  |  |  | 5250 |  |  |  | 5400 |  |  |  | 5400
|  |  | Total Unit Power - kW | [7 empty] | 14.3 |  |  |  | 14.3 |  |  |  | 16.4 |  |  |  | 16.4
|  |  | 1 IEER |  |  |  | (Btuh/Watt) |  |  |  | 19 |  |  |  | 17.5 |  |  |  | 18.8 |  |  |  | 18
|  |  | 1 EER |  |  |  | (Btuh/Watt) |  |  |  | 12 |  |  |  | 12 |  |  |  | 12.2 |  |  |  | 12.2
Refrigerant Charge |  |  | Refrigerant Type | [7 empty] | R-410A |  |  |  | R-410A |  |  |  | R-410A |  |  |  | R-410A
|  |  | Without Reheat |  |  |  | Circuit 1 |  |  |  | 19 lbs. 14 oz. |  |  |  | 19 lbs. 14 oz. |  |  |  | 10 lbs. 8 oz. |  |  |  | 10 lbs. 8 oz.
[7 empty] | Circuit 2 |  |  |  | 10 lbs. 15 oz. |  |  |  | 10 lbs. 15 oz. |  |  |  | 9 lbs. 10 oz. |  |  |  | 9 lbs. 10 oz.
[7 empty] | Circuit 3 |  |  |  | 10 lbs. 6 oz. |  |  |  | 10 lbs. 6 oz. |  |  |  | 9 lbs. 10 oz. |  |  |  | 9 lbs. 10 oz.
[7 empty] | Circuit 4 |  |  |  | - - - |  |  |  | - - - |  |  |  | 9 lbs. 12 oz. |  |  |  | 9 lbs. 12 oz.
|  |  | With Reheat |  |  |  | Circuit 1 |  |  |  | 22 lbs. 2 oz. |  |  |  | - - - |  |  |  | 10 lbs. 8 oz. |  |  |  | - - -
[7 empty] | Circuit 2 |  |  |  | 12 lbs. 6 oz. |  |  |  | - - - |  |  |  | 11 lbs. 0 oz. |  |  |  | - - -
[7 empty] | Circuit 3 |  |  |  | 10 lbs. 6 oz. |  |  |  | - - - |  |  |  | 9 lbs. 10 oz. |  |  |  | - - -
[7 empty] | Circuit 4 |  |  |  | - - - |  |  |  | - - - |  |  |  | 9 lbs. 12 oz. |  |  |  | - - -
Electric Heating Options Available | [10 empty] | 15-30-45-60 kW | [7 empty] | 15-30-45-60-90 kW
Compressor Type (number) | [10 empty] | Variable Capacity Scroll (1) Fixed Capacity Scroll (2) | [7 empty] | Variable Capacity Scroll (1) Fixed Capacity Scroll (3)
Outdoor Coils (Fin/Tube) |  |  | Net face area (total) - sq. ft. | [7 empty] | 55.2 |  |  |  | 55.2 |  |  |  | 55.2 |  |  |  | 55.2
|  |  | Tube diameter - in. | [7 empty] | 3/8 |  |  |  | 3/8 |  |  |  | 3/8 |  |  |  | 3/8
|  |  | Number of rows | [7 empty] | 2 |  |  |  | 2 |  |  |  | 2 |  |  |  | 2
|  |  | Fins per inch | [7 empty] | 20 |  |  |  | 20 |  |  |  | 20 |  |  |  | 20
Outdoor Coil Fans |  |  | Motor - (No.) horsepower | [7 empty] | (4) 1/3 ECM |  |  |  | (4) 1/3 ECM |  |  |  | (6) 1/3 ECM |  |  |  | (6) 1/3 ECM
[7 empty] | Motor rpm |  |  |  | 280-1075 |  |  |  | 280-1075 |  |  |  | 640-950 |  |  |  | 640-950
|  |  | Total Motor watts | [7 empty] | 150 -1350 |  |  |  | 150 -1350 |  |  |  | 290 -1250 |  |  |  | 290 -1250
|  |  | Diameter - (No.) in. | [7 empty] | (4) 24 |  |  |  | (4) 24 |  |  |  | (6) 24 |  |  |  | (6) 24
|  |  | Number of blades | [7 empty] | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 3
|  |  | Total Air volume - cfm | [7 empty] | 16000 |  |  |  | 16000 |  |  |  | 18600 |  |  |  | 18600
Indoor Coils |  |  | Net face area (total) - sq. ft. | [7 empty] | 21.4 |  |  |  | 21.4 |  |  |  | 21.4 |  |  |  | 21.4
|  |  | Tube diameter - in. | [7 empty] | 3/8 |  |  |  | 3/8 |  |  |  | 3/8 |  |  |  | 3/8
|  |  | Number of rows | [7 empty] | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 3
|  |  | Fins per inch | [7 empty] | 14 |  |  |  | 14 |  |  |  | 14 |  |  |  | 14
|  |  | Drain connection - No. and size | [7 empty] | (1) 1 in. FPT |  |  |  | (1) 1 in. FPT |  |  |  | (1) 1 in. FPT |  |  |  | (1) 1 in. FPT
|  |  | Expansion device type | [7 empty] | Balance port TXV, removable head
2 Indoor |  |  | Nominal motor output | [7 empty] | 3 hp, 5 hp, 7.5 hp
Blower |  |  | Max. usable motor output (US) | [7 empty] | 3.45 hp, 5.75 hp, 8.62 hp
and Drive Selection |  |  | Motor - Drive kit number | [7 empty] | 3 hp Kit 1 535-725 rpm Kit 2 710-965 rpm 5 hp Kit 3 685-856 rpm Kit 4 850-1045 rpm Kit 5 945-1185 rpm 7.5 hp Kit 6 850-1045 rpm Kit 7 945-1185 rpm Kit 8 1045-1285 rpm
|  |  | Blower wheel nominal D x W - in. | [7 empty] | (2) 15 x 15
Filters | [6 empty] | Type of filter |  |  |  | MERV 4, Disposable
|  |  | Number and size - in. | [7 empty] | (6) 24 x 24 x 2
Electrical characteristics | [10 empty] | 208/230V, 460V, or 575V - 60 hz -3 phase
NOTE - Net capacity includes evaporator blower motor heat deduction. Gross capacity does not include evaporator blower motor heat deduction. 1 AHRI Certified to AHRI Standard 340/360; 95°F outdoor air temperature and 80°F db/67°F wb entering evaporator air; minimum external duct static pressure. 2 Using total air volume and system static pressure requirements determine from blower performance tables rpm and motor output required. Maximum usable output of motors furnished are shown. In Canada, nominal motor output is also maximum usable motor output. If motors of comparable output are used, be sure to keep within the service factor limitations outlined on the motor nameplate. NOTE – Blower motor service factor = 1.0.
SPECIFICATIONS | [18 empty] | 20 TON ¦ 25 TON
General Data |  |  | Nominal Tonnage | [7 empty] | 20 Ton |  |  |  | 20 Ton |  |  |  | 25 Ton |  |  |  | 25 Ton
|  |  | Model Number | [7 empty] | LCM240U4M |  |  |  | LCM240U4V |  |  |  | LCM300U4M |  |  |  | LCM300U4V
|  |  | Efficiency Type | [7 empty] | Ultra-High |  |  |  | Ultra-High |  |  |  | Ultra-High |  |  |  | Ultra-High
|  |  | Blower Type | [7 empty] | SZVAV (Single Zone Variable Air Volume) |  |  |  | VAV (Variable Air Volume) |  |  |  | SZVAV (Single Zone Variable Air Volume) |  |  |  | VAV (Variable Air Volume)
Cooling Performance |  |  | Gross Cooling Capacity - Btuh | [7 empty] | 235000 |  |  |  | 235000 |  |  |  | 277000 |  |  |  | 277000
|  |  | 1 Net Cooling Capac | [5 empty] | ity - Btuh |  | 228000 |  |  |  | 228000 |  |  |  | 270000 |  |  |  | 270000
|  |  | 1 AHRI Rated Air Fl | [5 empty] | ow - cfm |  | 6000 |  |  |  | 6000 |  |  |  | 7400 |  |  |  | 7400
|  |  | Total Unit Power - kW | [7 empty] | 19 |  |  |  | 19 |  |  |  | 25.4 |  |  |  | 25.4
|  |  | 1 IEER (Bt | [5 empty] | uh/Watt) |  | 18.4 |  |  |  | 17.5 |  |  |  | 17.5 |  |  |  | 16.5
|  |  | 1 EER (Bt | [5 empty] | uh/Watt) |  | 12 |  |  |  | 12 |  |  |  | 10.6 |  |  |  | 10.6
Refrigerant Charge |  |  | Refrigerant Type | [7 empty] | R-410A |  |  |  | R-410A |  |  |  | R-410A |  |  |  | R-410A
|  |  | Without Humiditrol™+ | [5 empty] | Circuit 1 |  | 12 lbs. 2 oz. |  |  |  | 12 lbs. 2 oz. |  |  |  | 12 lbs. 8 oz. |  |  |  | 12 lbs. 8 oz.
[9 empty] | Circuit 2 |  | 12 lbs. 7 oz. |  |  |  | 12 lbs. 7 oz. |  |  |  | 11 lbs. 8 oz. |  |  |  | 11 lbs. 8 oz.
[9 empty] | Circuit 3 |  | 12 lbs. 0 oz. |  |  |  | 12 lbs. 0 oz. |  |  |  | 14 lbs. 8 oz. |  |  |  | 14 lbs. 8 oz.
[9 empty] | Circuit 4 |  | 12 lbs. 10 oz. |  |  |  | 12 lbs. 10 oz. |  |  |  | 11 lbs. 8 oz. |  |  |  | 11 lbs. 8 oz.
|  |  | With Humiditrol™+ | [5 empty] | Circuit 1 |  | 13 lbs. 4 oz. |  |  |  | - - - |  |  |  | 17 lbs. 2 oz. |  |  |  | - - -
[9 empty] | Circuit 2 |  | 13 lbs. 12 oz. |  |  |  | - - - |  |  |  | 17 lbs. 5 oz. |  |  |  | - - -
[9 empty] | Circuit 3 |  | 12 lbs. 0 oz. |  |  |  | - - - |  |  |  | 14 lbs. 8 oz. |  |  |  | - - -
[9 empty] | Circuit 4 |  | 12 lbs. 10 oz. |  |  |  | - - - |  |  |  | 11 lbs. 8 oz. |  |  |  | - - -
Electric Heat Options Available | [10 empty] | 15-30-45-60-90 kW
Compressor Type (number) | [10 empty] | Variable Capacity Scroll (1) Fixed Capacity Scroll (3)
Outdoor Coils (Fin/Tube) |  |  | Net face area (total) - sq. ft. | [7 empty] | 55.2 |  |  |  | 55.2 |  |  |  | 55.2 |  |  |  | 55.2
|  |  | Tube diameter - in. | [7 empty] | 3/8 |  |  |  | 3/8 |  |  |  | 3/8 |  |  |  | 3/8
|  |  | Number of rows | [7 empty] | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 3
|  |  | Fins per inch | [7 empty] | 20 |  |  |  | 20 |  |  |  | 20 |  |  |  | 20
Outdoor Coil Fans |  |  | Motor - (No.) horsepower | [7 empty] | (6) 1/3 ECM |  |  |  | (6) 1/3 ECM |  |  |  | (6) 1/3 ECM |  |  |  | (6) 1/3 ECM
|  |  | Motor rpm | [7 empty] | 450 - 950 |  |  |  | 450 - 950 |  |  |  | 515 - 1000 |  |  |  | 515 - 1000
|  |  | Total Motor watts | [7 empty] | 130 -1530 |  |  |  | 130 -1530 |  |  |  | 180 - 1730 |  |  |  | 180 - 1730
|  |  | Diameter - (No.) in. | [7 empty] | (6) 24 |  |  |  | (6) 24 |  |  |  | (6) 24 |  |  |  | (6) 24
|  |  | Number of blades | [7 empty] | 3 |  |  |  | 3 |  |  |  | 3 |  |  |  | 3
|  |  | Total Air volume - cfm | [7 empty] | 18000 |  |  |  | 18000 |  |  |  | 18300 |  |  |  | 18300
Indoor Coils |  |  | Net face area (total) - sq. ft. | [7 empty] | 21.4 |  |  |  | 21.4 |  |  |  | 21.4 |  |  |  | 21.4
|  |  | Tube diameter - in. | [7 empty] | 3/8 |  |  |  | 3/8 |  |  |  | 3/8 |  |  |  | 3/8
|  |  | Number of rows | [7 empty] | 4 |  |  |  | 4 |  |  |  | 4 |  |  |  | 4
|  |  | Fins per inch | [7 empty] | 14 |  |  |  | 14 |  |  |  | 14 |  |  |  | 14
|  |  | Drain connection - No. and size | [7 empty] | (1) 1 in. FPT |  |  |  | (1) 1 in. FPT |  |  |  | (1) 1 in. FPT |  |  |  | (1) 1 in. FPT
|  |  | Expansion device type | [7 empty] | Balance port TXV, removable head
2 Indoor |  |  | Nominal motor output | [7 empty] | 5 hp, 7.5 hp, 10 hp
Blower |  |  | Max. usable motor output (US) | [7 empty] | 5.75 hp, 8.62 hp, 11.5 hp
and Drive Selection |  |  | Motor - Drive kit number | [7 empty] | 5 hp Kit 3 685-856 rpm Kit 4 850-1045 rpm Kit 5 945-1185 rpm 7.5 hp Kit 6 850-1045 rpm Kit 7 945-1185 rpm Kit 8 1045-1285 rpm 10 hp Kit 7 945-1185 rpm Kit 10 1045-1285 rpm Kit 11 1135-1365 rpm
|  |  | Blower wheel nominal D x W - in. | [7 empty] | (2) 15 x 15
Filters |  |  | Type of filter | [7 empty] | MERV 4, Disposable
|  |  | Number and size - in. | [7 empty] | (6) 24 x 24 x 2
Electrical characteristics | [10 empty] | 208/230V, 460V, or 575V - 60 hz -3 phase
NOTE - Net capacity includes evaporator blower motor heat deduction. Gross capacity does not include evaporator blower motor heat deduction. 1 AHRI Certified to AHRI Standard 340/360; 95°F outdoor air temperature and 80°F db/67°F wb entering evaporator air; minimum external duct static pressure. 2 Using total air volume and system static pressure requirements determine from blower performance tables rpm and motor output required. Maximum usable output of motors furnished are shown. In Canada, nominal motor output is also maximum usable motor output. If motors of comparable output are used, be sure to keep within the service factor limitations outlined on the motor nameplate. NOTE – Blower motor service factor = 1.0.
COOLING RATINGS
NOTE − For Temperatures and Capacities not shown in tables, see bulletin − Cooling Unit Rating Table Correction Factor Data in Miscellaneous Engineering Data section.
13 TON - LCM156U4M/V (ONE COMPRESSOR OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 1200 | 33.6 |  | 0.91 | 0.83 | 0.97 |  | 1 |  | 32.3 | 1.09 | 0.85 | 0.98 | 1 |  | 31.1 | 1.28 | 0.87 | 0.98 | 1 | 30 | 1.51 |  | 0.88 | 0.99 | 1
| 1500 | 35.2 |  | 0.91 | 0.89 | 0.99 |  | 1 |  | 34 | 1.08 | 0.91 | 1 | 1 |  | 32.7 | 1.28 | 0.93 | 1 | 1 | 31.5 | 1.51 |  | 0.94 | 1 | 1
| 1800 | 36.7 |  | 0.9 | 0.93 | 1 |  | 1 |  | 35.4 | 1.08 | 0.94 | 1 | 1 |  | 34.1 | 1.29 | 0.95 | 1 | 1 | 32.9 | 1.52 |  | 0.96 | 1 | 1
67°F | 1200 | 35.1 |  | 0.91 | 0.53 | 0.77 |  | 0.95 |  | 33.8 | 1.08 | 0.54 | 0.79 | 0.96 |  | 32.5 | 1.28 | 0.55 | 0.82 | 0.97 | 31.2 | 1.51 |  | 0.56 | 0.84 | 0.98
| 1500 | 36.6 |  | 0.9 | 0.57 | 0.84 |  | 0.98 |  | 35.2 | 1.08 | 0.58 | 0.87 | 0.99 |  | 33.8 | 1.28 | 0.59 | 0.89 | 0.99 | 32.5 | 1.52 |  | 0.61 | 0.92 | 1
| 1800 | 37.7 |  | 0.9 | 0.6 | 0.91 |  | 1 |  | 36.2 | 1.08 | 0.61 | 0.93 | 1 |  | 34.8 | 1.29 | 0.63 | 0.94 | 1 | 33.4 | 1.52 |  | 0.65 | 0.95 | 1
71°F | 1200 | 36.8 |  | 0.9 | 0.24 | 0.48 |  | 0.72 |  | 35.4 | 1.08 | 0.23 | 0.49 | 0.74 |  | 34 | 1.29 | 0.23 | 0.51 | 0.76 | 32.7 | 1.52 |  | 0.24 | 0.52 | 0.79
| 1500 | 38.2 |  | 0.9 | 0.23 | 0.52 |  | 0.79 |  | 36.7 | 1.08 | 0.23 | 0.54 | 0.82 |  | 35.4 | 1.29 | 0.24 | 0.55 | 0.84 | 33.9 | 1.52 |  | 0.24 | 0.57 | 0.88
| 1800 | 39.4 |  | 0.89 | 0.24 | 0.57 |  | 0.86 |  | 37.8 | 1.08 | 0.24 | 0.58 | 0.89 |  | 36.3 | 1.29 | 0.25 | 0.6 | 0.92 | 34.9 | 1.52 |  | 0.26 | 0.62 | 0.93
NOTE - Compressor operating at maximum capacity.
13 TON - LCM156U4M/V (TWO COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 3120 | 113.8 |  | 5.18 | 0.72 | 0.84 |  | 0.96 |  | 110.4 | 5.76 | 0.73 | 0.86 | 0.97 |  | 105.4 | 6.6 | 0.74 | 0.88 | 0.98 | 100 | 7.51 |  | 0.76 | 0.9 | 0.99
| 3900 | 119.2 |  | 5.18 | 0.76 | 0.9 |  | 0.99 |  | 115.6 | 5.78 | 0.77 | 0.92 | 1 |  | 110.6 | 6.62 | 0.79 | 0.94 | 1 | 105.8 | 7.51 |  | 0.8 | 0.95 | 1
| 4680 | 124.2 |  | 5.19 | 0.8 | 0.95 |  | 1 |  | 120.6 | 5.79 | 0.81 | 0.97 | 1 |  | 115.3 | 6.64 | 0.83 | 0.98 | 1 | 110.5 | 7.53 |  | 0.85 | 0.99 | 1
67°F | 3120 | 119.8 |  | 5.18 | 0.58 | 0.7 |  | 0.81 |  | 116.3 | 5.78 | 0.58 | 0.71 | 0.82 |  | 111 | 6.63 | 0.59 | 0.72 | 0.84 | 106 | 7.55 |  | 0.6 | 0.74 | 0.86
| 3900 | 126.5 |  | 5.18 | 0.6 | 0.74 |  | 0.87 |  | 122.5 | 5.8 | 0.61 | 0.75 | 0.89 |  | 116.7 | 6.66 | 0.62 | 0.77 | 0.91 | 110.8 | 7.08 |  | 0.63 | 0.78 | 0.93
| 4680 | 130.1 |  | 5.19 | 0.62 | 0.77 |  | 0.92 |  | 126.9 | 5.81 | 0.63 | 0.79 | 0.94 |  | 120.9 | 6.66 | 0.64 | 0.81 | 0.96 | 114.7 | 7.6 |  | 0.66 | 0.83 | 0.97
71°F | 3120 | 124.9 |  | 5.19 | 0.44 | 0.56 |  | 0.68 |  | 120.8 | 5.85 | 0.45 | 0.57 | 0.68 |  | 116.1 | 6.66 | 0.45 | 0.58 | 0.7 | 110.9 | 7.58 |  | 0.45 | 0.59 | 0.71
| 3900 | 132.1 |  | 5.19 | 0.44 | 0.59 |  | 0.71 |  | 127.5 | 5.87 | 0.45 | 0.59 | 0.73 |  | 122.2 | 6.68 | 0.45 | 0.61 | 0.74 | 116.6 | 7.61 |  | 0.46 | 0.62 | 0.76
| 4680 | 137.5 |  | 5.19 | 0.46 | 0.61 |  | 0.75 |  | 132.4 | 5.88 | 0.46 | 0.62 | 0.76 |  | 126.7 | 6.7 | 0.47 | 0.63 | 0.79 | 120.7 | 7.62 |  | 0.46 | 0.65 | 0.81
NOTE - Compressors operating at maximum capacity.
13 TON - LCM156U4M/V (THREE COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 4160 | 155.2 |  | 8.72 | 0.72 | 0.84 |  | 0.95 |  | 144.8 | 9.9 | 0.72 | 0.85 | 0.97 |  | 133.7 | 11.22 | 0.73 | 0.87 | 0.99 | 122.3 | 12.69 |  | 0.75 | 0.89 | 1
| 5200 | 164.5 |  | 8.75 | 0.77 | 0.9 |  | 1 |  | 153.3 | 9.93 | 0.78 | 0.92 | 1 |  | 141.3 | 11.25 | 0.79 | 0.95 | 1 | 129.5 | 12.71 |  | 0.81 | 0.97 | 1
| 6240 | 171.3 |  | 8.77 | 0.81 | 0.96 |  | 1 |  | 160.1 | 9.95 | 0.83 | 0.98 | 1 |  | 148.4 | 11.28 | 0.85 | 0.99 | 1 | 136.7 | 12.73 |  | 0.87 | 1 | 1
67°F | 4160 | 163.2 |  | 8.75 | 0.56 | 0.69 |  | 0.81 |  | 152 | 9.92 | 0.56 | 0.7 | 0.82 |  | 140.3 | 11.25 | 0.55 | 0.72 | 0.84 | 128.7 | 12.71 |  | 0.55 | 0.72 | 0.86
| 5200 | 172.1 |  | 8.77 | 0.59 | 0.74 |  | 0.87 |  | 160.8 | 9.95 | 0.61 | 0.75 | 0.89 |  | 148.9 | 11.28 | 0.6 | 0.77 | 0.92 | 136.3 | 12.73 |  | 0.61 | 0.79 | 0.95
| 6240 | 179.4 |  | 8.79 | 0.63 | 0.79 |  | 0.93 |  | 167.5 | 9.97 | 0.64 | 0.8 | 0.96 |  | 154.8 | 11.3 | 0.63 | 0.82 | 0.98 | 141.7 | 12.75 |  | 0.64 | 0.85 | 0.99
71°F | 4160 | 174 |  | 8.78 | 0.42 | 0.55 |  | 0.67 |  | 162.3 | 9.96 | 0.41 | 0.55 | 0.68 |  | 150.2 | 11.28 | 0.4 | 0.55 | 0.69 | 137.8 | 12.74 |  | 0.38 | 0.54 | 0.71
| 5200 | 183.2 |  | 8.8 | 0.43 | 0.59 |  | 0.73 |  | 170.8 | 9.98 | 0.42 | 0.59 | 0.74 |  | 158.1 | 11.31 | 0.41 | 0.6 | 0.75 | 144.6 | 12.75 |  | 0.4 | 0.6 | 0.77
| 6240 | 189.8 |  | 8.81 | 0.45 | 0.62 |  | 0.78 |  | 177 | 9.99 | 0.44 | 0.62 | 0.79 |  | 163.6 | 11.32 | 0.43 | 0.63 | 0.81 | 149.6 | 12.77 |  | 0.45 | 0.64 | 0.83
NOTE - Compressors operating at maximum capacity.
COOLING RATINGS
NOTE − For Temperatures and Capacities not shown in tables, see bulletin − Cooling Unit Rating Table Correction Factor Data in Miscellaneous Engineering Data section.
15 TON - LCM180U4M/V (ONE COMPRESSOR OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 1600 | 36.1 |  | 1.02 | 0.9 | 1 |  | 1 |  | 33.8 | 1.22 | 0.91 | 1 | 1 |  | 31.7 | 1.44 | 0.93 | 1 | 1 | 29.6 | 1.69 |  | 0.95 | 1 | 1
| 2000 | 38.1 |  | 1.01 | 0.98 | 1 |  | 1 |  | 35.8 | 1.22 | 1 | 1 | 1 |  | 33.7 | 1.44 | 1 | 1 | 1 | 31.4 | 1.7 |  | 1 | 1 | 1
| 2400 | 39.8 |  | 1.01 | 1 | 1 |  | 1 |  | 37.5 | 1.22 | 1 | 1 | 1 |  | 35.2 | 1.45 | 1 | 1 | 1 | 32.9 | 1.71 |  | 1 | 1 | 1
67°F | 1600 | 37.9 |  | 1.01 | 0.57 | 0.86 |  | 1 |  | 35.5 | 1.22 | 0.57 | 0.87 | 1 |  | 33.1 | 1.44 | 0.56 | 0.89 | 1 | 30.9 | 1.7 |  | 0.55 | 0.91 | 1
| 2000 | 39.4 |  | 1.01 | 0.62 | 0.94 |  | 1 |  | 36.9 | 1.22 | 0.62 | 0.96 | 1 |  | 34.5 | 1.45 | 0.62 | 0.98 | 1 | 32 | 1.7 |  | 0.63 | 1 | 1
| 2400 | 40.5 |  | 1.01 | 0.67 | 1 |  | 1 |  | 38 | 1.22 | 0.67 | 1 | 1 |  | 35.5 | 1.45 | 0.69 | 1 | 1 | 33.1 | 1.71 |  | 0.69 | 1 | 1
71°F | 1600 | 40.1 |  | 1.01 | 0.25 | 0.54 |  | 0.81 |  | 37.6 | 1.22 | 0.22 | 0.54 | 0.83 |  | 35.2 | 1.45 | 0.2 | 0.54 | 0.84 | 32.8 | 1.7 |  | 0.18 | 0.54 | 0.87
| 2000 | 41.5 |  | 1.01 | 0.26 | 0.59 |  | 0.9 |  | 39 | 1.22 | 0.24 | 0.6 | 0.92 |  | 36.5 | 1.45 | 0.22 | 0.6 | 0.94 | 34 | 1.71 |  | 0.19 | 0.61 | 0.97
| 2400 | 42.7 |  | 1.01 | 0.27 | 0.65 |  | 0.98 |  | 40 | 1.22 | 0.25 | 0.66 | 1 |  | 37.4 | 1.45 | 0.24 | 0.67 | 1 | 34.9 | 1.72 |  | 0.22 | 0.68 | 1
NOTE - Compressor operating at maximum capacity.
15 TON - LCM180U4M/V (TWO COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 3600 | 133.7 |  | 5.69 | 0.72 | 0.85 |  | 0.96 |  | 127.1 | 6.4 | 0.73 | 0.86 | 0.97 |  | 120.2 | 7.24 | 0.73 | 0.87 | 0.98 | 112.1 | 8.16 |  | 0.74 | 0.89 | 0.99
| 4500 | 140.7 |  | 5.71 | 0.76 | 0.9 |  | 0.99 |  | 133.6 | 6.44 | 0.77 | 0.92 | 1 |  | 126.5 | 7.28 | 0.78 | 0.94 | 1 | 118.9 | 8.21 |  | 0.79 | 0.95 | 1
| 5400 | 146.5 |  | 5.73 | 0.8 | 0.95 |  | 1 |  | 139.5 | 6.46 | 0.81 | 0.97 | 1 |  | 132.1 | 7.31 | 0.83 | 0.98 | 1 | 124.6 | 8.25 |  | 0.84 | 0.99 | 1
67°F | 3600 | 141.4 |  | 5.72 | 0.58 | 0.7 |  | 0.82 |  | 134.7 | 6.44 | 0.58 | 0.71 | 0.83 |  | 127.6 | 7.28 | 0.58 | 0.71 | 0.84 | 120 | 8.22 |  | 0.58 | 0.72 | 0.86
| 4500 | 149.4 |  | 5.74 | 0.61 | 0.74 |  | 0.87 |  | 142.2 | 6.48 | 0.61 | 0.75 | 0.89 |  | 134.4 | 7.32 | 0.61 | 0.76 | 0.91 | 126.3 | 8.27 |  | 0.62 | 0.77 | 0.93
| 5400 | 155.1 |  | 5.76 | 0.63 | 0.78 |  | 0.93 |  | 147.5 | 6.5 | 0.63 | 0.8 | 0.94 |  | 139.4 | 7.35 | 0.64 | 0.81 | 0.96 | 130.9 | 8.3 |  | 0.64 | 0.82 | 0.98
71°F | 3600 | 148.7 |  | 5.74 | 0.45 | 0.56 |  | 0.68 |  | 141.6 | 6.47 | 0.44 | 0.57 | 0.69 |  | 134.2 | 7.32 | 0.44 | 0.57 | 0.7 | 126.5 | 8.27 |  | 0.44 | 0.57 | 0.71
| 4500 | 157 |  | 5.77 | 0.46 | 0.6 |  | 0.72 |  | 149.6 | 6.51 | 0.46 | 0.6 | 0.73 |  | 141.8 | 7.36 | 0.45 | 0.6 | 0.74 | 133.4 | 8.31 |  | 0.45 | 0.61 | 0.75
| 5400 | 163.3 |  | 5.78 | 0.47 | 0.62 |  | 0.76 |  | 155.4 | 6.53 | 0.46 | 0.63 | 0.78 |  | 147.1 | 7.39 | 0.46 | 0.63 | 0.79 | 138.4 | 8.34 |  | 0.46 | 0.64 | 0.81
NOTE - Compressors operating at maximum capacity.
15 TON - LCM180U4M/V (THREE COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 85°F | [7 empty] | 95°F | [5 empty] | 105°F |  |  |  |  | 115°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 4800 | 178.2 |  | 10.21 | 0.71 | 0.84 |  | 0.95 |  | 167.4 | 11.49 | 0.72 | 0.85 | 0.97 |  | 156.1 | 12.93 | 0.74 | 0.87 | 0.99 | 143.8 | 14.51 |  | 0.75 | 0.9 | 1
| 6000 | 188.3 |  | 10.26 | 0.77 | 0.9 |  | 1 |  | 176.5 | 11.55 | 0.78 | 0.92 | 1 |  | 164.2 | 12.99 | 0.8 | 0.95 | 1 | 151.6 | 14.58 |  | 0.81 | 0.97 | 1
| 7200 | 195.4 |  | 10.31 | 0.81 | 0.96 |  | 1 |  | 183.6 | 11.6 | 0.83 | 0.98 | 1 |  | 171.5 | 13.05 | 0.85 | 0.99 | 1 | 159.2 | 14.64 |  | 0.87 | 1 | 1
67°F | 4800 | 187.1 |  | 10.27 | 0.56 | 0.69 |  | 0.81 |  | 175.2 | 11.55 | 0.56 | 0.71 | 0.83 |  | 163.2 | 12.98 | 0.56 | 0.72 | 0.84 | 150.8 | 14.57 |  | 0.56 | 0.73 | 0.87
| 6000 | 196.3 |  | 10.32 | 0.6 | 0.76 |  | 0.87 |  | 184.4 | 11.61 | 0.61 | 0.76 | 0.89 |  | 172.1 | 13.05 | 0.61 | 0.77 | 0.92 | 159 | 14.64 |  | 0.62 | 0.79 | 0.94
| 7200 | 204.1 |  | 10.36 | 0.63 | 0.79 |  | 0.93 |  | 191.6 | 11.66 | 0.64 | 0.8 | 0.95 |  | 178.6 | 13.1 | 0.64 | 0.82 | 0.98 | 164.7 | 14.69 |  | 0.67 | 0.85 | 0.99
71°F | 4800 | 198.8 |  | 10.33 | 0.42 | 0.55 |  | 0.67 |  | 186.7 | 11.63 | 0.41 | 0.55 | 0.68 |  | 173.8 | 13.06 | 0.4 | 0.56 | 0.69 | 160.7 | 14.66 |  | 0.4 | 0.56 | 0.71
| 6000 | 208.4 |  | 10.38 | 0.43 | 0.59 |  | 0.73 |  | 195.5 | 11.68 | 0.43 | 0.59 | 0.74 |  | 182.1 | 13.12 | 0.42 | 0.6 | 0.76 | 168.2 | 14.73 |  | 0.42 | 0.6 | 0.78
| 7200 | 215.4 |  | 10.42 | 0.45 | 0.62 |  | 0.78 |  | 202.1 | 11.72 | 0.45 | 0.62 | 0.79 |  | 187.9 | 13.17 | 0.44 | 0.64 | 0.81 | 173.1 | 14.77 |  | 0.46 | 0.66 | 0.83
NOTE - Compressors operating at maximum capacity.
COOLING RATINGS
NOTE − For Temperatures and Capacities not shown in tables, see bulletin − Cooling Unit Rating Table Correction Factor Data in Miscellaneous Engineering Data section.
17.5 TON - LCM210U4M/V (ONE COMPRESSOR OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 1600 | 46.1 |  | 1.13 | 0.81 | 0.96 |  | 1 |  | 43.8 | 1.27 | 0.82 | 0.96 | 1 |  | 41.4 | 1.45 | 0.83 | 0.97 | 1 | 38.9 | 1.66 |  | 0.85 | 0.98 | 1
| 2000 | 48.1 |  | 1.13 | 0.87 | 0.98 |  | 1 |  | 45.8 | 1.27 | 0.89 | 0.99 | 1 |  | 43.4 | 1.45 | 0.9 | 1 | 1 | 41 | 1.66 |  | 0.91 | 1 | 1
| 2400 | 49.9 |  | 1.14 | 0.91 | 1 |  | 1 |  | 47.6 | 1.28 | 0.92 | 1 | 1 |  | 45.1 | 1.45 | 0.93 | 1 | 1 | 42.7 | 1.65 |  | 0.94 | 1 | 1
67°F | 1600 | 48.3 |  | 1.13 | 0.52 | 0.76 |  | 0.94 |  | 45.9 | 1.27 | 0.51 | 0.78 | 0.95 |  | 43.4 | 1.45 | 0.51 | 0.79 | 0.95 | 40.8 | 1.66 |  | 0.51 | 0.81 | 0.97
| 2000 | 50.2 |  | 1.14 | 0.55 | 0.83 |  | 0.97 |  | 47.6 | 1.28 | 0.55 | 0.85 | 0.98 |  | 45 | 1.45 | 0.56 | 0.87 | 0.99 | 42.4 | 1.66 |  | 0.57 | 0.9 | 0.99
| 2400 | 51.5 |  | 1.14 | 0.59 | 0.89 |  | 0.99 |  | 48.9 | 1.28 | 0.59 | 0.91 | 1 |  | 46.2 | 1.45 | 0.61 | 0.92 | 1 | 43.4 | 1.65 |  | 0.62 | 0.93 | 1
71°F | 1600 | 50.6 |  | 1.14 | 0.22 | 0.48 |  | 0.72 |  | 48.1 | 1.28 | 0.21 | 0.48 | 0.73 |  | 45.6 | 1.45 | 0.2 | 0.48 | 0.74 | 43 | 1.66 |  | 0.19 | 0.48 | 0.76
| 2000 | 52.4 |  | 1.14 | 0.23 | 0.52 |  | 0.79 |  | 49.9 | 1.28 | 0.22 | 0.52 | 0.81 |  | 47.2 | 1.45 | 0.2 | 0.53 | 0.82 | 44.5 | 1.65 |  | 0.2 | 0.54 | 0.85
| 2400 | 53.7 |  | 1.15 | 0.23 | 0.56 |  | 0.86 |  | 51.1 | 1.28 | 0.22 | 0.57 | 0.88 |  | 48.3 | 1.45 | 0.22 | 0.58 | 0.9 | 45.6 | 1.65 |  | 0.21 | 0.6 | 0.91
NOTE - Compressor operating at maximum capacity.
17.5 TON - LCM210U4M/V (TWO COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 2800 | 96.9 |  | 3.27 | 0.73 | 0.86 |  | 0.98 |  | 92.1 | 3.73 | 0.73 | 0.88 | 0.99 |  | 87.1 | 4.26 | 0.74 | 0.89 | 1 | 82.2 | 4.85 |  | 0.75 | 0.91 | 1
| 3500 | 102.4 |  | 3.27 | 0.77 | 0.93 |  | 1 |  | 97.2 | 3.74 | 0.78 | 0.94 | 1 |  | 92.1 | 4.27 | 0.79 | 0.96 | 1 | 87.1 | 4.86 |  | 0.81 | 0.98 | 1
| 4200 | 107.3 |  | 3.25 | 0.82 | 0.97 |  | 1 |  | 101.9 | 3.74 | 0.83 | 0.99 | 1 |  | 96.6 | 4.28 | 0.85 | 0.99 | 1 | 91.3 | 4.88 |  | 0.86 | 1 | 1
67°F | 2800 | 102.5 |  | 3.27 | 0.56 | 0.71 |  | 0.83 |  | 97.4 | 3.74 | 0.56 | 0.72 | 0.85 |  | 92.6 | 4.23 | 0.58 | 0.72 | 0.86 | 86.9 | 4.87 |  | 0.57 | 0.73 | 0.88
| 3500 | 108.1 |  | 3.27 | 0.59 | 0.75 |  | 0.89 |  | 102.4 | 3.75 | 0.6 | 0.76 | 0.91 |  | 97.3 | 4.24 | 0.6 | 0.78 | 0.93 | 91.1 | 4.88 |  | 0.61 | 0.79 | 0.95
| 4200 | 111.8 |  | 3.28 | 0.62 | 0.8 |  | 0.95 |  | 106 | 3.76 | 0.63 | 0.81 | 0.97 |  | 100.8 | 4.25 | 0.64 | 0.82 | 0.98 | 94.5 | 4.88 |  | 0.65 | 0.84 | 0.99
71°F | 2800 | 108 |  | 3.24 | 0.44 | 0.56 |  | 0.69 |  | 102.4 | 3.75 | 0.42 | 0.57 | 0.68 |  | 97.6 | 4.24 | 0.41 | 0.55 | 0.7 | 91.9 | 4.86 |  | 0.4 | 0.56 | 0.7
| 3500 | 113.9 |  | 3.25 | 0.42 | 0.58 |  | 0.73 |  | 108 | 3.76 | 0.42 | 0.59 | 0.74 |  | 102.7 | 4.25 | 0.42 | 0.6 | 0.75 | 97 | 4.87 |  | 0.42 | 0.6 | 0.77
| 4200 | 118.3 |  | 3.26 | 0.44 | 0.62 |  | 0.78 |  | 112.1 | 3.76 | 0.44 | 0.62 | 0.79 |  | 106.5 | 4.26 | 0.44 | 0.63 | 0.8 | 99.9 | 4.88 |  | 0.44 | 0.64 | 0.82
NOTE - Compressors operating at maximum capacity.
17.5 TON - LCM210U4M/V (THREE COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 4200 | 164 |  | 6.17 | 0.71 | 0.83 |  | 0.94 |  | 156.1 | 6.95 | 0.71 | 0.84 | 0.95 |  | 147.8 | 7.82 | 0.72 | 0.85 | 0.97 | 139.2 | 8.85 |  | 0.73 | 0.87 | 0.99
| 5250 | 172.6 |  | 6.21 | 0.74 | 0.89 |  | 1 |  | 164.3 | 6.98 | 0.77 | 0.9 | 1 |  | 155.6 | 7.85 | 0.78 | 0.92 | 1 | 146.6 | 8.85 |  | 0.79 | 0.94 | 1
| 6300 | 179.5 |  | 6.23 | 0.8 | 0.94 |  | 1 |  | 171 | 6.97 | 0.81 | 0.95 | 1 |  | 161.9 | 7.84 | 0.83 | 0.97 | 1 | 152.5 | 8.86 |  | 0.83 | 0.99 | 1
67°F | 4200 | 172.7 |  | 6.21 | 0.56 | 0.68 |  | 0.81 |  | 164.3 | 6.97 | 0.56 | 0.69 | 0.81 |  | 155.4 | 7.85 | 0.54 | 0.7 | 0.82 | 146.5 | 8.83 |  | 0.55 | 0.71 | 0.84
| 5250 | 181 |  | 6.22 | 0.59 | 0.73 |  | 0.86 |  | 171.9 | 6.99 | 0.58 | 0.74 | 0.87 |  | 162.3 | 7.88 | 0.59 | 0.75 | 0.89 | 153 | 8.86 |  | 0.6 | 0.76 | 0.91
| 6300 | 186.5 |  | 6.27 | 0.61 | 0.77 |  | 0.91 |  | 177.3 | 7.02 | 0.61 | 0.78 | 0.93 |  | 167.4 | 7.89 | 0.61 | 0.81 | 0.95 | 157.3 | 8.9 |  | 0.62 | 0.82 | 0.97
71°F | 4200 | 183.1 |  | 6.26 | 0.41 | 0.54 |  | 0.66 |  | 174.4 | 7.01 | 0.41 | 0.54 | 0.67 |  | 165 | 7.89 | 0.4 | 0.53 | 0.68 | 155.3 | 8.9 |  | 0.39 | 0.55 | 0.69
| 5250 | 191.1 |  | 6.29 | 0.42 | 0.56 |  | 0.7 |  | 181.8 | 7.03 | 0.41 | 0.57 | 0.71 |  | 171.8 | 7.91 | 0.41 | 0.57 | 0.74 | 161.6 | 8.92 |  | 0.41 | 0.59 | 0.75
| 6300 | 196.9 |  | 6.31 | 0.42 | 0.6 |  | 0.76 |  | 187.4 | 7.03 | 0.42 | 0.61 | 0.76 |  | 176.9 | 7.92 | 0.42 | 0.61 | 0.78 | 166.1 | 8.91 |  | 0.41 | 0.61 | 0.81
NOTE - Compressors operating at maximum capacity.
17.5 TON - LCM210U4M/V (FOUR COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 85°F | [7 empty] | 95°F | [5 empty] | 105°F |  |  |  |  | 115°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 5600 | 211.7 |  | 11.57 | 0.73 | 0.83 |  | 0.94 |  | 199.6 | 13.07 | 0.73 | 0.85 | 0.96 |  | 186.7 | 14.79 | 0.74 | 0.87 | 0.98 | 173.3 | 16.71 |  | 0.74 | 0.89 | 0.99
| 7000 | 223.8 |  | 11.61 | 0.75 | 0.89 |  | 1 |  | 210.7 | 13.12 | 0.76 | 0.91 | 1 |  | 197.2 | 14.84 | 0.78 | 0.93 | 1 | 183.3 | 16.76 |  | 0.81 | 0.96 | 1
| 8400 | 233.2 |  | 11.65 | 0.8 | 0.95 |  | 1 |  | 219.7 | 13.16 | 0.82 | 0.97 | 1 |  | 205.9 | 14.87 | 0.84 | 0.99 | 1 | 191.6 | 16.79 |  | 0.86 | 1 | 1
67°F | 5600 | 221.9 |  | 11.61 | 0.56 | 0.71 |  | 0.8 |  | 208.8 | 13.12 | 0.55 | 0.71 | 0.82 |  | 194.8 | 14.84 | 0.57 | 0.73 | 0.84 | 180.7 | 16.75 |  | 0.57 | 0.73 | 0.86
| 7000 | 232.6 |  | 11.65 | 0.59 | 0.75 |  | 0.87 |  | 218.8 | 13.16 | 0.6 | 0.76 | 0.88 |  | 204.5 | 14.87 | 0.61 | 0.77 | 0.9 | 189.7 | 16.78 |  | 0.63 | 0.78 | 0.93
| 8400 | 241.1 |  | 11.68 | 0.62 | 0.77 |  | 0.92 |  | 226.7 | 13.19 | 0.63 | 0.79 | 0.94 |  | 212 | 14.9 | 0.65 | 0.82 | 0.97 | 196.5 | 16.8 |  | 0.67 | 0.84 | 0.99
71°F | 5600 | 236.8 |  | 11.67 | 0.41 | 0.55 |  | 0.69 |  | 223 | 13.19 | 0.4 | 0.55 | 0.69 |  | 208.7 | 14.9 | 0.39 | 0.55 | 0.7 | 192.9 | 16.8 |  | 0.4 | 0.57 | 0.71
| 7000 | 247.4 |  | 11.71 | 0.43 | 0.59 |  | 0.73 |  | 232.6 | 13.22 | 0.42 | 0.59 | 0.74 |  | 216.9 | 14.93 | 0.44 | 0.61 | 0.74 | 200 | 16.83 |  | 0.45 | 0.63 | 0.76
| 8400 | 254.7 |  | 11.74 | 0.45 | 0.62 |  | 0.76 |  | 239.1 | 13.25 | 0.46 | 0.63 | 0.78 |  | 222.6 | 14.95 | 0.48 | 0.65 | 0.8 | 206 | 16.84 |  | 0.47 | 0.67 | 0.82
NOTE - Compressors operating at maximum capacity.
COOLING RATINGS
NOTE − For Temperatures and Capacities not shown in tables, see bulletin − Cooling Unit Rating Table Correction Factor Data in Miscellaneous Engineering Data section.
20 TON - LCM240U4M/V (ONE COMPRESSOR OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 1600 | 51.6 |  | 1.76 | 0.8 | 0.93 |  | 0.99 |  | 49.4 | 1.98 | 0.8 | 0.93 | 0.99 |  | 46.6 | 2.28 | 0.8 | 0.94 | 0.99 | 43.5 | 2.63 |  | 0.81 | 0.95 | 1
| 2000 | 54.4 |  | 1.75 | 0.84 | 0.95 |  | 1 |  | 51.9 | 1.97 | 0.85 | 0.96 | 1 |  | 49 | 2.28 | 0.85 | 0.96 | 1 | 45.9 | 2.63 |  | 0.86 | 0.97 | 1
| 2400 | 56.5 |  | 1.74 | 0.87 | 0.97 |  | 1 |  | 54 | 1.97 | 0.88 | 0.98 | 1 |  | 51.1 | 2.28 | 0.88 | 0.99 | 1 | 47.9 | 2.64 |  | 0.89 | 0.99 | 1
67°F | 1600 | 54.5 |  | 1.75 | 0.52 | 0.74 |  | 0.9 |  | 52 | 1.97 | 0.51 | 0.75 | 0.9 |  | 49.2 | 2.28 | 0.5 | 0.75 | 0.91 | 46.1 | 2.63 |  | 0.49 | 0.76 | 0.92
| 2000 | 57.3 |  | 1.73 | 0.54 | 0.8 |  | 0.93 |  | 54.7 | 1.97 | 0.53 | 0.81 | 0.94 |  | 51.6 | 2.28 | 0.53 | 0.82 | 0.95 | 48.3 | 2.64 |  | 0.53 | 0.83 | 0.95
| 2400 | 59.3 |  | 1.72 | 0.57 | 0.84 |  | 0.96 |  | 56.6 | 1.97 | 0.57 | 0.85 | 0.96 |  | 53.4 | 2.28 | 0.56 | 0.86 | 0.97 | 50 | 2.64 |  | 0.57 | 0.87 | 0.98
71°F | 1600 | 57.5 |  | 1.73 | 0.24 | 0.47 |  | 0.69 |  | 54.9 | 1.97 | 0.22 | 0.47 | 0.69 |  | 52 | 2.28 | 0.2 | 0.46 | 0.7 | 48.8 | 2.64 |  | 0.18 | 0.45 | 0.71
| 2000 | 60.3 |  | 1.72 | 0.24 | 0.5 |  | 0.74 |  | 57.6 | 1.96 | 0.22 | 0.5 | 0.75 |  | 54.5 | 2.28 | 0.2 | 0.5 | 0.77 | 51.1 | 2.64 |  | 0.18 | 0.49 | 0.78
| 2400 | 62.5 |  | 1.71 | 0.24 | 0.53 |  | 0.8 |  | 59.5 | 1.96 | 0.22 | 0.53 | 0.81 |  | 56.3 | 2.28 | 0.21 | 0.53 | 0.83 | 52.8 | 2.64 |  | 0.19 | 0.54 | 0.84
NOTE - Compressor operating at maximum capacity.
20 TON - LCM240U4M/V (TWO COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 3200 | 113.6 |  | 4.19 | 0.74 | 0.87 |  | 0.96 |  | 107.7 | 4.73 | 0.73 | 0.88 | 0.97 |  | 101.3 | 5.36 | 0.75 | 0.9 | 0.98 | 94.7 | 6.06 |  | 0.76 | 0.91 | 0.99
| 4000 | 119 |  | 4.21 | 0.79 | 0.92 |  | 1 |  | 112.7 | 4.77 | 0.8 | 0.93 | 1 |  | 105.9 | 5.4 | 0.81 | 0.94 | 1 | 99.3 | 6.09 |  | 0.83 | 0.95 | 1
| 4800 | 123.1 |  | 4.24 | 0.82 | 0.96 |  | 1 |  | 116.6 | 4.79 | 0.83 | 0.96 | 1 |  | 110.1 | 5.4 | 0.84 | 0.98 | 1 | 103.2 | 6.11 |  | 0.87 | 0.99 | 1
67°F | 3200 | 119.8 |  | 4.21 | 0.53 | 0.71 |  | 0.84 |  | 113.6 | 4.76 | 0.54 | 0.7 | 0.85 |  | 106.8 | 5.38 | 0.53 | 0.72 | 0.86 | 99.8 | 6.09 |  | 0.54 | 0.72 | 0.88
| 4000 | 124.8 |  | 4.23 | 0.57 | 0.75 |  | 0.89 |  | 117.9 | 4.79 | 0.56 | 0.76 | 0.9 |  | 110.9 | 5.41 | 0.56 | 0.78 | 0.92 | 103.6 | 6.12 |  | 0.56 | 0.8 | 0.94
| 4800 | 128.2 |  | 4.25 | 0.59 | 0.8 |  | 0.93 |  | 121.2 | 4.8 | 0.59 | 0.81 | 0.95 |  | 114 | 5.42 | 0.59 | 0.82 | 0.96 | 106.5 | 6.13 |  | 0.6 | 0.84 | 0.97
71°F | 3200 | 126.5 |  | 4.25 | 0.36 | 0.51 |  | 0.67 |  | 119.8 | 4.8 | 0.35 | 0.52 | 0.67 |  | 112.9 | 5.42 | 0.34 | 0.51 | 0.69 | 105.6 | 6.12 |  | 0.33 | 0.51 | 0.7
| 4000 | 131.3 |  | 4.28 | 0.35 | 0.54 |  | 0.72 |  | 124 | 4.82 | 0.35 | 0.55 | 0.73 |  | 116.8 | 5.44 | 0.35 | 0.55 | 0.75 | 109.3 | 6.13 |  | 0.33 | 0.56 | 0.75
| 4800 | 134.4 |  | 4.3 | 0.35 | 0.58 |  | 0.77 |  | 127.1 | 4.84 | 0.35 | 0.58 | 0.79 |  | 119.5 | 5.45 | 0.35 | 0.59 | 0.81 | 111.8 | 6.14 |  | 0.34 | 0.59 | 0.83
NOTE - Compressors operating at maximum capacity.
20 TON - LCM240U4M/V (THREE COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 4800 | 182.5 |  | 6.82 | 0.74 | 0.85 |  | 0.94 |  | 173 | 7.77 | 0.75 | 0.85 | 0.95 |  | 163.1 | 8.8 | 0.74 | 0.87 | 0.96 | 153 | 9.96 |  | 0.76 | 0.87 | 0.97
| 6000 | 192.5 |  | 6.87 | 0.78 | 0.89 |  | 0.97 |  | 182.8 | 7.81 | 0.79 | 0.9 | 0.98 |  | 172.5 | 8.85 | 0.8 | 0.92 | 0.99 | 162.1 | 9.99 |  | 0.81 | 0.93 | 1
| 7200 | 200.7 |  | 6.91 | 0.82 | 0.93 |  | 1 |  | 190.5 | 7.85 | 0.83 | 0.94 | 1 |  | 180.1 | 8.88 | 0.83 | 0.95 | 1 | 169.1 | 10.03 |  | 0.85 | 0.96 | 1
67°F | 4800 | 193.9 |  | 6.88 | 0.57 | 0.7 |  | 0.82 |  | 183.8 | 7.82 | 0.56 | 0.7 | 0.83 |  | 172.9 | 8.85 | 0.57 | 0.71 | 0.84 | 161.7 | 9.99 |  | 0.56 | 0.73 | 0.85
| 6000 | 202.5 |  | 6.93 | 0.6 | 0.75 |  | 0.87 |  | 191.3 | 7.85 | 0.59 | 0.77 | 0.88 |  | 179.6 | 8.88 | 0.6 | 0.77 | 0.89 | 168.4 | 10.02 |  | 0.6 | 0.79 | 0.9
| 7200 | 208.1 |  | 6.96 | 0.61 | 0.8 |  | 0.91 |  | 197 | 7.88 | 0.62 | 0.8 | 0.92 |  | 185.5 | 8.91 | 0.63 | 0.82 | 0.93 | 173.9 | 10.04 |  | 0.64 | 0.83 | 0.95
71°F | 4800 | 205.1 |  | 6.94 | 0.41 | 0.55 |  | 0.67 |  | 194.5 | 7.88 | 0.42 | 0.54 | 0.67 |  | 183.5 | 8.9 | 0.4 | 0.54 | 0.69 | 171.9 | 10.04 |  | 0.38 | 0.55 | 0.69
| 6000 | 214 |  | 6.99 | 0.42 | 0.57 |  | 0.72 |  | 196.9 | 7.99 | 0.42 | 0.6 | 0.73 |  | 191.1 | 8.94 | 0.38 | 0.59 | 0.75 | 179 | 10.07 |  | 0.38 | 0.58 | 0.76
| 7200 | 220.2 |  | 7.02 | 0.44 | 0.6 |  | 0.78 |  | 208.5 | 7.94 | 0.44 | 0.62 | 0.78 |  | 196.2 | 8.95 | 0.4 | 0.63 | 0.79 | 183.7 | 10.09 |  | 0.39 | 0.62 | 0.82
NOTE - Compressors operating at maximum capacity.
20 TON - LCM240U4M/V (FOUR COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 85°F | [7 empty] | 95°F | [5 empty] | 105°F |  |  |  |  | 115°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 6400 | 242.5 |  | 13.9 | 0.73 | 0.83 |  | 0.94 |  | 228.2 | 15.64 | 0.74 | 0.84 | 0.95 |  | 213.2 | 17.55 | 0.74 | 0.86 | 0.97 | 197.4 | 19.66 |  | 0.76 | 0.88 | 0.99
| 8000 | 257.4 |  | 14.01 | 0.76 | 0.89 |  | 0.99 |  | 241.8 | 15.75 | 0.78 | 0.9 | 1 |  | 225.6 | 17.67 | 0.78 | 0.92 | 1 | 209.1 | 19.78 |  | 0.8 | 0.95 | 1
| 9600 | 268.1 |  | 14.1 | 0.8 | 0.94 |  | 1 |  | 252.3 | 15.84 | 0.82 | 0.96 | 1 |  | 235.9 | 17.76 | 0.84 | 0.98 | 1 | 219.2 | 19.88 |  | 0.85 | 0.99 | 1
67°F | 6400 | 255.7 |  | 14.02 | 0.56 | 0.7 |  | 0.8 |  | 239.7 | 15.75 | 0.57 | 0.71 | 0.82 |  | 223.2 | 17.66 | 0.57 | 0.72 | 0.83 | 206.2 | 19.77 |  | 0.57 | 0.74 | 0.85
| 8000 | 268 |  | 14.11 | 0.61 | 0.75 |  | 0.86 |  | 251.7 | 15.84 | 0.61 | 0.77 | 0.88 |  | 234.8 | 17.76 | 0.62 | 0.77 | 0.9 | 217.3 | 19.88 |  | 0.62 | 0.78 | 0.92
| 9600 | 278 |  | 14.18 | 0.63 | 0.79 |  | 0.91 |  | 261.2 | 15.92 | 0.64 | 0.79 | 0.93 |  | 243.7 | 17.84 | 0.64 | 0.81 | 0.95 | 225.9 | 19.96 |  | 0.66 | 0.83 | 0.98
71°F | 6400 | 272.9 |  | 14.17 | 0.42 | 0.56 |  | 0.68 |  | 256.7 | 15.9 | 0.41 | 0.56 | 0.69 |  | 239.6 | 17.83 | 0.4 | 0.55 | 0.7 | 221.8 | 19.94 |  | 0.4 | 0.56 | 0.71
| 8000 | 286.1 |  | 14.26 | 0.43 | 0.59 |  | 0.73 |  | 268.6 | 16 | 0.42 | 0.6 | 0.74 |  | 251.1 | 17.93 | 0.42 | 0.59 | 0.74 | 231.9 | 20.04 |  | 0.43 | 0.6 | 0.76
| 9600 | 294.9 |  | 14.32 | 0.45 | 0.63 |  | 0.77 |  | 276.6 | 16.06 | 0.44 | 0.63 | 0.78 |  | 258.1 | 17.99 | 0.45 | 0.64 | 0.8 | 237.8 | 20.1 |  | 0.47 | 0.66 | 0.81
NOTE - Compressors operating at maximum capacity.
COOLING RATINGS
NOTE − For Temperatures and Capacities not shown in tables, see bulletin − Cooling Unit Rating Table Correction Factor Data in Miscellaneous Engineering Data section.
25 TON - LCM300U4M/V (ONE COMPRESSOR OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 2000 | 57.9 |  | 1.84 | 0.8 | 0.94 |  | 0.99 |  | 55.3 | 2.07 | 0.81 | 0.94 | 1 |  | 52.3 | 2.39 | 0.82 | 0.95 | 1 | 48.9 | 2.76 |  | 0.83 | 0.96 | 1
| 2500 | 60.7 |  | 1.83 | 0.86 | 0.96 |  | 1 |  | 58 | 2.07 | 0.86 | 0.97 | 1 |  | 54.9 | 2.39 | 0.87 | 0.98 | 1 | 51.6 | 2.77 |  | 0.88 | 0.98 | 1
| 3000 | 63.1 |  | 1.82 | 0.88 | 0.98 |  | 1 |  | 60.4 | 2.06 | 0.89 | 0.99 | 1 |  | 57.2 | 2.39 | 0.9 | 0.99 | 1 | 53.8 | 2.77 |  | 0.9 | 1 | 1
67°F | 2000 | 60.9 |  | 1.83 | 0.51 | 0.75 |  | 0.91 |  | 58.3 | 2.07 | 0.51 | 0.76 | 0.92 |  | 55.2 | 2.39 | 0.5 | 0.77 | 0.93 | 51.7 | 2.77 |  | 0.5 | 0.78 | 0.94
| 2500 | 63.8 |  | 1.81 | 0.54 | 0.81 |  | 0.94 |  | 60.9 | 2.06 | 0.54 | 0.82 | 0.95 |  | 57.7 | 2.39 | 0.54 | 0.84 | 0.96 | 54 | 2.77 |  | 0.54 | 0.85 | 0.97
| 3000 | 66 |  | 1.8 | 0.57 | 0.86 |  | 0.97 |  | 63 | 2.06 | 0.58 | 0.87 | 0.97 |  | 59.5 | 2.39 | 0.58 | 0.87 | 0.98 | 55.6 | 2.77 |  | 0.58 | 0.88 | 0.99
71°F | 2000 | 64.2 |  | 1.82 | 0.23 | 0.47 |  | 0.7 |  | 61.4 | 2.06 | 0.21 | 0.47 | 0.7 |  | 58.2 | 2.39 | 0.19 | 0.46 | 0.71 | 54.7 | 2.77 |  | 0.18 | 0.46 | 0.73
| 2500 | 67.1 |  | 1.8 | 0.23 | 0.51 |  | 0.76 |  | 64.2 | 2.05 | 0.21 | 0.5 | 0.77 |  | 60.7 | 2.39 | 0.2 | 0.5 | 0.79 | 57 | 2.77 |  | 0.18 | 0.51 | 0.8
| 3000 | 69.2 |  | 1.79 | 0.23 | 0.54 |  | 0.82 |  | 66.1 | 2.05 | 0.22 | 0.54 | 0.83 |  | 62.6 | 2.39 | 0.21 | 0.55 | 0.85 | 58.7 | 2.77 |  | 0.19 | 0.55 | 0.86
NOTE - Compressor operating at maximum capacity.
25 TON - LCM300U4M/V (TWO COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 4000 | 131.3 |  | 5.21 | 0.73 | 0.86 |  | 0.98 |  | 125.2 | 5.83 | 0.73 | 0.87 | 0.99 |  | 118.6 | 6.61 | 0.74 | 0.88 | 1 | 111.1 | 7.51 |  | 0.75 | 0.9 | 1
| 5000 | 138.4 |  | 5.21 | 0.77 | 0.92 |  | 1 |  | 132.2 | 5.86 | 0.78 | 0.93 | 1 |  | 125.2 | 6.64 | 0.79 | 0.95 | 1 | 117.8 | 7.56 |  | 0.8 | 0.96 | 1
| 6000 | 144.6 |  | 5.22 | 0.81 | 0.96 |  | 1 |  | 138 | 5.88 | 0.82 | 0.97 | 1 |  | 131 | 6.67 | 0.83 | 0.98 | 1 | 123.4 | 7.59 |  | 0.85 | 0.99 | 1
67°F | 4000 | 139.4 |  | 5.21 | 0.58 | 0.71 |  | 0.83 |  | 132.8 | 5.86 | 0.58 | 0.71 | 0.84 |  | 125.6 | 6.64 | 0.58 | 0.72 | 0.85 | 117.9 | 7.55 |  | 0.58 | 0.73 | 0.87
| 5000 | 146.1 |  | 5.22 | 0.6 | 0.75 |  | 0.89 |  | 139.3 | 5.88 | 0.61 | 0.76 | 0.9 |  | 131.6 | 6.68 | 0.61 | 0.77 | 0.92 | 123.2 | 7.58 |  | 0.6 | 0.78 | 0.94
| 6000 | 151.1 |  | 5.24 | 0.62 | 0.79 |  | 0.94 |  | 143.7 | 5.9 | 0.62 | 0.8 | 0.95 |  | 135.4 | 6.69 | 0.62 | 0.81 | 0.97 | 127.4 | 7.62 |  | 0.63 | 0.83 | 0.98
71°F | 4000 | 147.2 |  | 5.21 | 0.43 | 0.56 |  | 0.69 |  | 140.1 | 5.87 | 0.43 | 0.57 | 0.69 |  | 132.7 | 6.67 | 0.43 | 0.57 | 0.7 | 124.7 | 7.59 |  | 0.41 | 0.57 | 0.71
| 5000 | 154.2 |  | 5.23 | 0.45 | 0.6 |  | 0.73 |  | 146.9 | 5.9 | 0.42 | 0.6 | 0.74 |  | 139.1 | 6.71 | 0.43 | 0.6 | 0.75 | 130.8 | 7.63 |  | 0.4 | 0.59 | 0.76
| 6000 | 159.6 |  | 5.24 | 0.43 | 0.62 |  | 0.77 |  | 151.7 | 5.91 | 0.43 | 0.61 | 0.78 |  | 143.7 | 6.72 | 0.43 | 0.61 | 0.8 | 134.8 | 7.65 |  | 0.43 | 0.64 | 0.81
NOTE - Compressors operating at maximum capacity.
25 TON - LCM300U4M/V (THREE COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 65°F | [7 empty] | 75°F | [5 empty] | 85°F |  |  |  |  | 95°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 5600 | 218.9 |  | 9.6 | 0.7 | 0.82 |  | 0.93 |  | 208.5 | 10.77 | 0.69 | 0.82 | 0.94 |  | 197.2 | 12.14 | 0.7 | 0.85 | 0.96 | 185.5 | 13.67 |  | 0.72 | 0.86 | 0.97
| 7000 | 230.5 |  | 9.64 | 0.73 | 0.87 |  | 0.98 |  | 219.4 | 10.83 | 0.75 | 0.89 | 0.99 |  | 207.4 | 12.2 | 0.75 | 0.91 | 1 | 195.2 | 13.75 |  | 0.76 | 0.92 | 1
| 8400 | 239 |  | 9.67 | 0.77 | 0.94 |  | 1 |  | 227.9 | 10.87 | 0.78 | 0.94 | 1 |  | 215.7 | 12.26 | 0.79 | 0.95 | 1 | 203.4 | 13.81 |  | 0.82 | 0.97 | 1
67°F | 5600 | 231.9 |  | 9.65 | 0.55 | 0.67 |  | 0.78 |  | 220.9 | 10.85 | 0.55 | 0.67 | 0.79 |  | 208.9 | 12.22 | 0.54 | 0.69 | 0.82 | 196.6 | 13.77 |  | 0.54 | 0.69 | 0.83
| 7000 | 243.2 |  | 9.7 | 0.57 | 0.71 |  | 0.85 |  | 231.6 | 10.9 | 0.57 | 0.71 | 0.85 |  | 218.9 | 12.28 | 0.56 | 0.73 | 0.88 | 205.9 | 13.84 |  | 0.58 | 0.74 | 0.88
| 8400 | 251.4 |  | 9.72 | 0.58 | 0.75 |  | 0.9 |  | 239.2 | 10.93 | 0.6 | 0.75 | 0.91 |  | 226 | 12.32 | 0.59 | 0.77 | 0.93 | 212.4 | 13.88 |  | 0.61 | 0.79 | 0.95
71°F | 5600 | 246.5 |  | 9.72 | 0.41 | 0.53 |  | 0.64 |  | 234.7 | 10.93 | 0.4 | 0.54 | 0.65 |  | 222.5 | 12.33 | 0.4 | 0.54 | 0.66 | 209.6 | 13.87 |  | 0.39 | 0.53 | 0.67
| 7000 | 258.3 |  | 9.75 | 0.41 | 0.55 |  | 0.69 |  | 245.4 | 10.98 | 0.41 | 0.56 | 0.69 |  | 232.4 | 12.39 | 0.4 | 0.56 | 0.7 | 218.7 | 13.95 |  | 0.4 | 0.56 | 0.71
| 8400 | 266.3 |  | 9.78 | 0.41 | 0.58 |  | 0.73 |  | 253.1 | 11.02 | 0.42 | 0.58 | 0.74 |  | 239.5 | 12.43 | 0.42 | 0.58 | 0.76 | 225 | 13.99 |  | 0.41 | 0.6 | 0.76
NOTE - Compressors operating at maximum capacity.
25 TON - LCM300U4M/V (FOUR COMPRESSORS OPERATING)
Entering Wet Bulb Tem- perature | Total Air Volume | Outdoor Air Temperature Entering Outdoor Coil
|  | 85°F | [7 empty] | 95°F | [5 empty] | 105°F |  |  |  |  | 115°F
|  | Total Cool Cap. |  | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  |  | Total Cool Cap. | Comp. Motor Input | Sensible To Total Ratio (S/T) |  |  | Total Cool Cap. | Comp. Motor Input |  | Sensible To Total Ratio (S/T)
[5 empty] | Dry Bulb | [6 empty] | Dry Bulb | [5 empty] | Dry Bulb | [5 empty] | Dry Bulb
| cfm | kBtuh |  | kW | 75°F | 80°F |  | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F |  | kBtuh | kW | 75°F | 80°F | 85°F | kBtuh | kW |  | 75°F | 80°F | 85°F
63°F | 7000 | 277.9 |  | 18.5 | 0.71 | 0.81 |  | 0.91 |  | 262 | 20.73 | 0.72 | 0.82 | 0.93 |  | 245.1 | 23.21 | 0.73 | 0.84 | 0.95 | 227.7 | 25.99 |  | 0.74 | 0.85 | 0.97
| 8500 | 292.3 |  | 18.65 | 0.76 | 0.86 |  | 0.96 |  | 275.7 | 20.88 | 0.76 | 0.87 | 0.98 |  | 258.2 | 23.37 | 0.78 | 0.89 | 0.99 | 239.5 | 26.14 |  | 0.78 | 0.91 | 1
| 10000 | 303.9 |  | 18.77 | 0.78 | 0.9 |  | 1 |  | 286.4 | 20.99 | 0.79 | 0.92 | 1 |  | 268.1 | 23.48 | 0.81 | 0.94 | 1 | 248.8 | 26.28 |  | 0.82 | 0.96 | 1
67°F | 7000 | 294.6 |  | 18.69 | 0.58 | 0.7 |  | 0.79 |  | 276.9 | 20.92 | 0.59 | 0.71 | 0.79 |  | 258.8 | 23.39 | 0.57 | 0.71 | 0.8 | 239.4 | 26.18 |  | 0.58 | 0.73 | 0.83
| 8500 | 307.1 |  | 18.82 | 0.65 | 0.74 |  | 0.83 |  | 288.7 | 21.05 | 0.6 | 0.75 | 0.85 |  | 269.8 | 23.54 | 0.62 | 0.75 | 0.86 | 250.2 | 26.31 |  | 0.64 | 0.77 | 0.88
| 10000 | 316.8 |  | 18.91 | 0.63 | 0.77 |  | 0.87 |  | 298.1 | 21.14 | 0.64 | 0.78 | 0.89 |  | 279.1 | 23.65 | 0.65 | 0.78 | 0.91 | 258.7 | 26.42 |  | 0.67 | 0.8 | 0.93
71°F | 7000 | 313.2 |  | 18.91 | 0.44 | 0.57 |  | 0.67 |  | 294.8 | 21.14 | 0.44 | 0.58 | 0.67 |  | 270.4 | 23.57 | 0.43 | 0.62 | 0.69 | 256.5 | 26.43 |  | 0.44 | 0.56 | 0.7
| 8500 | 326.3 |  | 19.05 | 0.44 | 0.59 |  | 0.72 |  | 304.8 | 21.25 | 0.45 | 0.59 | 0.72 |  | 287.6 | 23.79 | 0.46 | 0.6 | 0.74 | 266 | 26.57 |  | 0.47 | 0.62 | 0.74
| 10000 | 333.6 |  | 19.13 | 0.48 | 0.62 |  | 0.75 |  | 316.6 | 21.4 | 0.51 | 0.62 | 0.76 |  | 295.3 | 23.87 | 0.47 | 0.64 | 0.78 | 273.6 | 26.67 |  | 0.46 | 0.66 | 0.79
NOTE - Compressors operating at maximum capacity.