## Table 1
Degradation Coefficient (C_d)
IEER or SEER | 15.5
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 70 | 59 | 52.7218 | 70588 | 40235.16 | 4.153 | 1800 | 412.6122 |  | 1
65 | 70 | 59 | 52.7218 | 71637 | 45847.68 | 4.184 | 2100 | 564.8456 |  | 1
65 | 70 | 59 | 52.7218 | 74522 | 50674.96 | 4.232 | 2700 | 983.4264 |  | 1
65 | 75 | 59 | 38.6294 | 70630 | 48734.7 | 4.149 | 1800 | 412.6122 |  | 1
65 | 75 | 59 | 38.6294 | 71678 | 54475.28 | 4.18 | 2100 | 564.8456 |  | 1
65 | 75 | 59 | 38.6294 | 74563 | 59650.4 | 4.228 | 2700 | 983.4264 |  | 1
65 | 70 | 63 | 68.6866 | 71587 | 35793.5 | 4.149 | 1800 | 412.6122 |  | 1
65 | 70 | 63 | 68.6866 | 72636 | 40676.16 | 4.18 | 2100 | 564.8456 |  | 1
65 | 70 | 63 | 68.6866 | 75520 | 46067.2 | 4.228 | 2700 | 983.4264 |  | 1
65 | 75 | 63 | 52.1129 | 71628 | 44409.36 | 4.145 | 1800 | 412.6122 |  | 1
65 | 75 | 63 | 52.1129 | 72677 | 50147.13 | 4.176 | 2100 | 564.8456 |  | 1
65 | 75 | 63 | 52.1129 | 75562 | 55160.26 | 4.224 | 2700 | 983.4264 |  | 1
65 | 70 | 67 | 86.0167 | 73699 | 27268.63 | 4.14 | 1800 | 412.6122 |  | 1
65 | 70 | 67 | 86.0167 | 74748 | 32141.64 | 4.171 | 2100 | 564.8456 |  | 1
65 | 70 | 67 | 86.0167 | 77633 | 37263.84 | 4.219 | 2700 | 983.4264 |  | 1
65 | 75 | 67 | 66.7494 | 73741 | 36133.09 | 4.136 | 1800 | 412.6122 |  | 1
65 | 75 | 67 | 66.7494 | 74789 | 41881.84 | 4.168 | 2100 | 564.8456 |  | 1
65 | 75 | 67 | 66.7494 | 77674 | 46604.4 | 4.215 | 2700 | 983.4264 |  | 1
65 | 75 | 71 | 82.6659 | 76967 | 26938.45 | 4.176 | 1800 | 412.6122 |  | 1
65 | 75 | 71 | 82.6659 | 78016 | 32766.72 | 4.207 | 2100 | 564.8456 |  | 1
65 | 75 | 71 | 82.6659 | 80900 | 37214 | 4.255 | 2700 | 983.4264 |  | 1
75 | 70 | 59 | 52.7218 | 69955 | 40573.9 | 4.67 | 1800 | 400.0985 |  | 1
75 | 70 | 59 | 52.7218 | 71004 | 45442.56 | 4.701 | 2100 | 564.8456 |  | 1
75 | 70 | 59 | 52.7218 | 73889 | 50983.41 | 4.749 | 2700 | 983.4264 |  | 1
75 | 75 | 59 | 38.6294 | 69997 | 48997.9 | 4.667 | 1800 | 400.0985 |  | 1
75 | 75 | 59 | 38.6294 | 71045 | 54704.65 | 4.698 | 2100 | 564.8456 |  | 1
75 | 75 | 59 | 38.6294 | 73930 | 59883.3 | 4.746 | 2700 | 983.4264 |  | 1
75 | 70 | 63 | 68.6866 | 70954 | 35477 | 4.666 | 1800 | 412.6122 |  | 1
75 | 70 | 63 | 68.6866 | 72003 | 41041.71 | 4.697 | 2100 | 564.8456 |  | 1
75 | 70 | 63 | 68.6866 | 74887 | 45681.07 | 4.745 | 2700 | 983.4264 |  | 1
75 | 75 | 63 | 52.1129 | 70995 | 44726.85 | 4.663 | 1800 | 412.6122 |  | 1
75 | 75 | 63 | 52.1129 | 72044 | 49710.36 | 4.694 | 2100 | 564.8456 |  | 1
75 | 75 | 63 | 52.1129 | 74929 | 55447.46 | 4.742 | 2700 | 983.4264 |  | 1
75 | 70 | 67 | 86.0167 | 73066 | 27034.42 | 4.657 | 1800 | 412.6122 |  | 1
75 | 70 | 67 | 86.0167 | 74115 | 32610.6 | 4.688 | 2100 | 564.8456 |  | 1
75 | 70 | 67 | 86.0167 | 77000 | 36960 | 4.736 | 2700 | 983.4264 |  | 1
75 | 75 | 67 | 66.7494 | 73108 | 36554 | 4.654 | 1800 | 412.6122 |  | 1
75 | 75 | 67 | 66.7494 | 74156 | 41527.36 | 4.685 | 2100 | 564.8456 |  | 1
75 | 75 | 67 | 66.7494 | 77041 | 46995.01 | 4.733 | 2700 | 983.4264 |  | 1
75 | 75 | 71 | 82.6659 | 76334 | 27480.24 | 4.693 | 1800 | 412.6122 |  | 1
75 | 75 | 71 | 82.6659 | 77383 | 33274.69 | 4.725 | 2100 | 564.8456 |  | 1
75 | 75 | 71 | 82.6659 | 80267 | 37725.49 | 4.772 | 2700 | 983.4264 |  | 1
85 | 70 | 59 | 52.7218 | 68109 | 40865.4 | 5.248 | 1800 | 400.0985 |  | 1
85 | 70 | 59 | 52.7218 | 69158 | 46335.86 | 5.279 | 2100 | 555.5945 |  | 1
85 | 70 | 59 | 52.7218 | 72042 | 51149.82 | 5.327 | 2700 | 983.4264 |  | 1
85 | 75 | 59 | 38.6294 | 68150 | 49068 | 5.245 | 1800 | 400.0985 |  | 1
85 | 75 | 59 | 38.6294 | 69199 | 69199 | 5.276 | 2100 | 555.5945 |  | 1
85 | 75 | 59 | 38.6294 | 72084 | 72084 | 5.323 | 2700 | 983.4264 |  | 1
85 | 70 | 63 | 68.6866 | 69108 | 36627.24 | 5.244 | 1800 | 400.0985 |  | 1
85 | 70 | 63 | 68.6866 | 70156 | 41392.04 | 5.275 | 2100 | 564.8456 |  | 1
85 | 70 | 63 | 68.6866 | 73041 | 46746.24 | 5.323 | 2700 | 983.4264 |  | 1
85 | 75 | 63 | 52.1129 | 69149 | 44946.85 | 5.24 | 1800 | 400.0985 |  | 1
85 | 75 | 63 | 52.1129 | 70198 | 50542.56 | 5.272 | 2100 | 555.5945 |  | 1
85 | 75 | 63 | 52.1129 | 73082 | 55542.32 | 5.319 | 2700 | 983.4264 |  | 1
85 | 70 | 67 | 86.0167 | 71220 | 28488 | 5.235 | 1800 | 412.6122 |  | 1
85 | 70 | 67 | 86.0167 | 72269 | 33243.74 | 5.266 | 2100 | 564.8456 |  | 1
85 | 70 | 67 | 86.0167 | 75153 | 38328.03 | 5.314 | 2700 | 983.4264 |  | 1
85 | 75 | 67 | 66.7494 | 71261 | 37055.72 | 5.232 | 1800 | 412.6122 |  | 1
85 | 75 | 67 | 66.7494 | 72310 | 42662.9 | 5.263 | 2100 | 564.8456 |  | 1
85 | 75 | 67 | 66.7494 | 75195 | 47372.85 | 5.31 | 2700 | 983.4264 |  | 1
85 | 75 | 71 | 82.6659 | 74488 | 28305.44 | 5.271 | 1800 | 412.6122 |  | 1
85 | 75 | 71 | 82.6659 | 75536 | 33991.2 | 5.302 | 2100 | 564.8456 |  | 1
85 | 75 | 71 | 82.6659 | 78421 | 38426.29 | 5.35 | 2700 | 983.4264 |  | 1
95 | 70 | 59 | 52.7218 | 64932 | 40257.84 | 5.873 | 1800 | 400.0985 |  | 1
95 | 70 | 59 | 52.7218 | 65981 | 45526.89 | 5.904 | 2100 | 555.5945 |  | 1
95 | 70 | 59 | 52.7218 | 68866 | 68866 | 5.952 | 2700 | 979.0808 |  | 1
95 | 75 | 59 | 38.6294 | 64974 | 64974 | 5.87 | 1800 | 400.0985 |  | 1
95 | 75 | 59 | 38.6294 | 66022 | 66022 | 5.901 | 2100 | 555.5945 |  | 1
95 | 75 | 59 | 38.6294 | 68907 | 68907 | 5.949 | 2700 | 979.0808 |  | 1
95 | 70 | 63 | 68.6866 | 65931 | 36262.05 | 5.869 | 1800 | 400.0985 |  | 1
95 | 70 | 63 | 68.6866 | 66980 | 40857.8 | 5.9 | 2100 | 555.5945 |  | 1
95 | 70 | 63 | 68.6866 | 69864 | 46110.24 | 5.948 | 2700 | 979.0808 |  | 1
95 | 75 | 63 | 52.1129 | 65972 | 44201.24 | 5.866 | 1800 | 400.0985 |  | 1
95 | 75 | 63 | 52.1129 | 67021 | 49595.54 | 5.897 | 2100 | 555.5945 |  | 1
95 | 75 | 63 | 52.1129 | 69906 | 54526.68 | 5.944 | 2700 | 979.0808 |  | 1
95 | 70 | 67 | 86.0167 | 68043 | 28578.06 | 5.86 | 1800 | 400.0985 |  | 1
95 | 70 | 67 | 86.0167 | 69092 | 33164.16 | 5.891 | 2100 | 555.5945 |  | 1
95 | 70 | 67 | 86.0167 | 71977 | 38147.81 | 5.939 | 2700 | 983.4264 |  | 1
95 | 75 | 67 | 66.7494 | 68085 | 36765.9 | 5.857 | 1800 | 400.0985 |  | 1
95 | 75 | 67 | 66.7494 | 69133 | 42171.13 | 5.888 | 2100 | 555.5945 |  | 1
95 | 75 | 67 | 66.7494 | 72018 | 46811.7 | 5.936 | 2700 | 983.4264 |  | 1
95 | 75 | 71 | 82.6659 | 71311 | 28524.4 | 5.896 | 1800 | 412.6122 |  | 1
95 | 75 | 71 | 82.6659 | 72360 | 34009.2 | 5.928 | 2100 | 564.8456 |  | 1
95 | 75 | 71 | 82.6659 | 75244 | 38374.44 | 5.975 | 2700 | 983.4264 |  | 1
105 | 70 | 59 | 52.7218 | 61050 | 39072 | 6.572 | 1800 | 400.0985 |  | 1
105 | 70 | 59 | 52.7218 | 62099 | 62099 | 6.603 | 2100 | 555.5945 |  | 1
105 | 70 | 59 | 52.7218 | 64983 | 64983 | 6.65 | 2700 | 979.0808 |  | 1
105 | 75 | 59 | 38.6294 | 61091 | 61091 | 6.568 | 1800 | 400.0985 |  | 1
105 | 75 | 59 | 38.6294 | 62140 | 62140 | 6.599 | 2100 | 555.5945 |  | 1
105 | 75 | 59 | 38.6294 | 65025 | 65025 | 6.647 | 2700 | 979.0808 |  | 1
105 | 70 | 63 | 68.6866 | 62049 | 35367.93 | 6.567 | 1800 | 400.0985 |  | 1
105 | 70 | 63 | 68.6866 | 63098 | 39751.74 | 6.599 | 2100 | 555.5945 |  | 1
105 | 70 | 63 | 68.6866 | 65982 | 44867.76 | 6.646 | 2700 | 979.0808 |  | 1
105 | 75 | 63 | 52.1129 | 62090 | 42842.1 | 6.564 | 1800 | 400.0985 |  | 1
105 | 75 | 63 | 52.1129 | 63139 | 47985.64 | 6.595 | 2100 | 555.5945 |  | 1
105 | 75 | 63 | 52.1129 | 66023 | 52818.4 | 6.643 | 2700 | 979.0808 |  | 1
105 | 70 | 67 | 86.0167 | 64161 | 28230.84 | 6.559 | 1800 | 400.0985 |  | 1
105 | 70 | 67 | 86.0167 | 65210 | 32605 | 6.59 | 2100 | 555.5945 |  | 1
105 | 70 | 67 | 86.0167 | 68094 | 37451.7 | 6.637 | 2700 | 979.0808 |  | 1
105 | 75 | 67 | 66.7494 | 64202 | 35953.12 | 6.555 | 1800 | 400.0985 |  | 1
105 | 75 | 67 | 66.7494 | 65251 | 41108.13 | 6.586 | 2100 | 555.5945 |  | 1
105 | 75 | 67 | 66.7494 | 68136 | 45651.12 | 6.634 | 2700 | 979.0808 |  | 1
105 | 75 | 71 | 82.6659 | 67429 | 28320.18 | 6.595 | 1800 | 400.0985 |  | 1
105 | 75 | 71 | 82.6659 | 68477 | 33553.73 | 6.626 | 2100 | 555.5945 |  | 1
105 | 75 | 71 | 82.6659 | 71362 | 37821.86 | 6.674 | 2700 | 983.4264 |  | 1
115 | 70 | 59 | 52.7218 | 57506 | 57506 | 7.391 | 1800 | 400.0985 |  | 1
115 | 70 | 59 | 52.7218 | 58555 | 58555 | 7.422 | 2100 | 555.5945 |  | 1
115 | 70 | 59 | 52.7218 | 61439 | 61439 | 7.47 | 2700 | 979.0808 |  | 1
115 | 75 | 59 | 38.6294 | 57547 | 57547 | 7.388 | 1800 | 400.0985 |  | 1
115 | 75 | 59 | 38.6294 | 58596 | 58596 | 7.419 | 2100 | 555.5945 |  | 1
115 | 75 | 59 | 38.6294 | 61480 | 61480 | 7.467 | 2700 | 979.0808 |  | 1
115 | 70 | 63 | 68.6866 | 58505 | 36273.1 | 7.387 | 1800 | 400.0985 |  | 1
115 | 70 | 63 | 68.6866 | 59553 | 40496.04 | 7.418 | 2100 | 555.5945 |  | 1
115 | 70 | 63 | 68.6866 | 62438 | 45579.74 | 7.466 | 2700 | 979.0808 |  | 1
115 | 75 | 63 | 52.1129 | 58546 | 43324.04 | 7.384 | 1800 | 400.0985 |  | 1
115 | 75 | 63 | 52.1129 | 59594 | 48271.14 | 7.415 | 2100 | 555.5945 |  | 1
115 | 75 | 63 | 52.1129 | 62479 | 62479 | 7.462 | 2700 | 979.0808 |  | 1
115 | 70 | 67 | 86.0167 | 60617 | 29702.33 | 7.378 | 1800 | 400.0985 |  | 1
115 | 70 | 67 | 86.0167 | 61666 | 33916.3 | 7.409 | 2100 | 555.5945 |  | 1
115 | 70 | 67 | 86.0167 | 64550 | 38730 | 7.457 | 2700 | 979.0808 |  | 1
115 | 75 | 67 | 66.7494 | 60658 | 37001.38 | 7.375 | 1800 | 400.0985 |  | 1
115 | 75 | 67 | 66.7494 | 61707 | 41960.76 | 7.406 | 2100 | 555.5945 |  | 1
115 | 75 | 67 | 66.7494 | 64591 | 46505.52 | 7.454 | 2700 | 979.0808 |  | 1
115 | 75 | 71 | 82.6659 | 63885 | 30025.95 | 7.414 | 1800 | 400.0985 |  | 1
115 | 75 | 71 | 82.6659 | 64933 | 35063.82 | 7.445 | 2100 | 555.5945 |  | 1
115 | 75 | 71 | 82.6659 | 67818 | 39334.44 | 7.493 | 2700 | 979.0808 |  | 1
65 | 80 | 59 | 27.7402 | 70996 | 57506.76 | 4.152 | 1800 | 412.6122 |  | 1
65 | 80 | 59 | 27.7402 | 72045 | 63399.6 | 4.183 | 2100 | 564.8456 |  | 1
65 | 80 | 59 | 27.7402 | 74929 | 74929 | 4.231 | 2700 | 983.4264 |  | 1
65 | 85 | 59 | 19.3387 | 72187 | 72187 | 4.162 | 1800 | 412.6122 |  | 1
65 | 85 | 59 | 19.3387 | 73236 | 73236 | 4.193 | 2100 | 564.8456 |  | 1
65 | 85 | 59 | 19.3387 | 76121 | 76121 | 4.241 | 2700 | 983.4264 |  | 1
65 | 80 | 63 | 39.1676 | 71995 | 53276.3 | 4.148 | 1800 | 412.6122 |  | 1
65 | 80 | 63 | 39.1676 | 73043 | 59164.83 | 4.179 | 2100 | 564.8456 |  | 1
65 | 80 | 63 | 39.1676 | 75928 | 64538.8 | 4.227 | 2700 | 983.4264 |  | 1
65 | 85 | 63 | 29.0563 | 73186 | 61476.24 | 4.158 | 1800 | 412.6122 |  | 1
65 | 85 | 63 | 29.0563 | 74235 | 66811.5 | 4.189 | 2100 | 564.8456 |  | 1
65 | 85 | 63 | 29.0563 | 77119 | 73263.05 | 4.237 | 2700 | 983.4264 |  | 1
65 | 80 | 67 | 51.5724 | 74107 | 45205.27 | 4.139 | 1800 | 412.6122 |  | 1
65 | 80 | 67 | 51.5724 | 75156 | 51106.08 | 4.17 | 2100 | 564.8456 |  | 1
65 | 80 | 67 | 51.5724 | 78040 | 56188.8 | 4.218 | 2700 | 983.4264 |  | 1
65 | 85 | 67 | 39.6049 | 75298 | 53461.58 | 4.149 | 1800 | 412.6122 |  | 1
65 | 85 | 67 | 39.6049 | 76347 | 59550.66 | 4.18 | 2100 | 564.8456 |  | 1
65 | 85 | 67 | 39.6049 | 79232 | 64970.24 | 4.228 | 2700 | 983.4264 |  | 1
65 | 80 | 71 | 65.0618 | 77333 | 36346.51 | 4.179 | 1800 | 412.6122 |  | 1
65 | 80 | 71 | 65.0618 | 78382 | 42326.28 | 4.21 | 2100 | 564.8456 |  | 1
65 | 80 | 71 | 65.0618 | 81267 | 47134.86 | 4.258 | 2700 | 983.4264 |  | 1
65 | 85 | 71 | 51.076 | 78525 | 44759.25 | 4.189 | 1800 | 412.6122 |  | 1
65 | 85 | 71 | 51.076 | 79573 | 50926.72 | 4.22 | 2100 | 564.8456 |  | 1
65 | 85 | 71 | 51.076 | 82458 | 56071.44 | 4.268 | 2700 | 983.4264 |  | 1
75 | 80 | 59 | 27.7402 | 70363 | 70363 | 4.67 | 1800 | 400.0985 |  | 1
75 | 80 | 59 | 27.7402 | 71412 | 71412 | 4.701 | 2100 | 564.8456 |  | 1
75 | 80 | 59 | 27.7402 | 74296 | 74296 | 4.748 | 2700 | 983.4264 |  | 1
75 | 85 | 59 | 19.3387 | 71554 | 71554 | 4.679 | 1800 | 412.6122 |  | 1
75 | 85 | 59 | 19.3387 | 72603 | 72603 | 4.711 | 2100 | 564.8456 |  | 1
75 | 85 | 59 | 19.3387 | 75488 | 75488 | 4.758 | 2700 | 983.4264 |  | 1
75 | 80 | 63 | 39.1676 | 71362 | 53521.5 | 4.665 | 1800 | 412.6122 |  | 1
75 | 80 | 63 | 39.1676 | 72410 | 58652.1 | 4.697 | 2100 | 564.8456 |  | 1
75 | 80 | 63 | 39.1676 | 75295 | 64753.7 | 4.744 | 2700 | 983.4264 |  | 1
75 | 85 | 63 | 29.0563 | 72553 | 60944.52 | 4.675 | 1800 | 412.6122 |  | 1
75 | 85 | 63 | 29.0563 | 73602 | 66977.82 | 4.707 | 2100 | 564.8456 |  | 1
75 | 85 | 63 | 29.0563 | 76486 | 76486 | 4.754 | 2700 | 983.4264 |  | 1
75 | 80 | 67 | 51.5724 | 73474 | 45553.88 | 4.657 | 1800 | 412.6122 |  | 1
75 | 80 | 67 | 51.5724 | 74523 | 50675.64 | 4.688 | 2100 | 564.8456 |  | 1
75 | 80 | 67 | 51.5724 | 77407 | 56507.11 | 4.736 | 2700 | 983.4264 |  | 1
75 | 85 | 67 | 39.6049 | 74665 | 53012.15 | 4.667 | 1800 | 412.6122 |  | 1
75 | 85 | 67 | 39.6049 | 75714 | 59056.92 | 4.698 | 2100 | 564.8456 |  | 1
75 | 85 | 67 | 39.6049 | 78599 | 64451.18 | 4.745 | 2700 | 983.4264 |  | 1
75 | 80 | 71 | 65.0618 | 76700 | 36816 | 4.696 | 1800 | 412.6122 |  | 1
75 | 80 | 71 | 65.0618 | 77749 | 42761.95 | 4.727 | 2100 | 564.8456 |  | 1
75 | 80 | 71 | 65.0618 | 80634 | 47574.06 | 4.775 | 2700 | 983.4264 |  | 1
75 | 85 | 71 | 51.076 | 77892 | 45177.36 | 4.706 | 1800 | 412.6122 |  | 1
75 | 85 | 71 | 51.076 | 78941 | 50522.24 | 4.737 | 2100 | 564.8456 |  | 1
75 | 85 | 71 | 51.076 | 81825 | 56459.25 | 4.785 | 2700 | 983.4264 |  | 1
85 | 80 | 59 | 27.7402 | 68517 | 68517 | 5.247 | 1800 | 400.0985 |  | 1
85 | 80 | 59 | 27.7402 | 69565 | 69565 | 5.278 | 2100 | 555.5945 |  | 1
85 | 80 | 59 | 27.7402 | 72450 | 72450 | 5.326 | 2700 | 983.4264 |  | 1
85 | 85 | 59 | 19.3387 | 69708 | 69708 | 5.257 | 1800 | 400.0985 |  | 1
85 | 85 | 59 | 19.3387 | 70757 | 70757 | 5.288 | 2100 | 564.8456 |  | 1
85 | 85 | 59 | 19.3387 | 73641 | 73641 | 5.336 | 2700 | 983.4264 |  | 1
85 | 80 | 63 | 39.1676 | 69515 | 53526.55 | 5.243 | 1800 | 400.0985 |  | 1
85 | 80 | 63 | 39.1676 | 70564 | 59273.76 | 5.274 | 2100 | 564.8456 |  | 1
85 | 80 | 63 | 39.1676 | 73449 | 64635.12 | 5.322 | 2700 | 983.4264 |  | 1
85 | 85 | 63 | 29.0563 | 70707 | 61515.09 | 5.253 | 1800 | 412.6122 |  | 1
85 | 85 | 63 | 29.0563 | 71755 | 71755 | 5.284 | 2100 | 564.8456 |  | 1
85 | 85 | 63 | 29.0563 | 74640 | 74640 | 5.332 | 2700 | 983.4264 |  | 1
85 | 80 | 67 | 51.5724 | 71628 | 45841.92 | 5.234 | 1800 | 412.6122 |  | 1
85 | 80 | 67 | 51.5724 | 72676 | 51599.96 | 5.265 | 2100 | 564.8456 |  | 1
85 | 80 | 67 | 51.5724 | 75561 | 56670.75 | 5.313 | 2700 | 983.4264 |  | 1
85 | 85 | 67 | 39.6049 | 72819 | 53886.06 | 5.244 | 1800 | 412.6122 |  | 1
85 | 85 | 67 | 39.6049 | 73868 | 59833.08 | 5.275 | 2100 | 564.8456 |  | 1
85 | 85 | 67 | 39.6049 | 76752 | 65239.2 | 5.323 | 2700 | 983.4264 |  | 1
85 | 80 | 71 | 65.0618 | 74854 | 37427 | 5.274 | 1800 | 412.6122 |  | 1
85 | 80 | 71 | 65.0618 | 75903 | 43264.71 | 5.305 | 2100 | 564.8456 |  | 1
85 | 80 | 71 | 65.0618 | 78787 | 48060.07 | 5.353 | 2700 | 983.4264 |  | 1
85 | 85 | 71 | 51.076 | 76045 | 45627 | 5.284 | 1800 | 412.6122 |  | 1
85 | 85 | 71 | 51.076 | 77094 | 51652.98 | 5.315 | 2100 | 564.8456 |  | 1
85 | 85 | 71 | 51.076 | 79979 | 56785.09 | 5.363 | 2700 | 983.4264 |  | 1
95 | 80 | 59 | 27.7402 | 65340 | 65340 | 5.872 | 1800 | 400.0985 |  | 1
95 | 80 | 59 | 27.7402 | 66389 | 66389 | 5.904 | 2100 | 555.5945 |  | 1
95 | 80 | 59 | 27.7402 | 69273 | 69273 | 5.951 | 2700 | 979.0808 |  | 1
95 | 85 | 59 | 19.3387 | 66531 | 66531 | 5.882 | 1800 | 400.0985 |  | 1
95 | 85 | 59 | 19.3387 | 67580 | 67580 | 5.913 | 2100 | 555.5945 |  | 1
95 | 85 | 59 | 19.3387 | 70465 | 70465 | 5.961 | 2700 | 979.0808 |  | 1
95 | 80 | 63 | 39.1676 | 66339 | 52407.81 | 5.868 | 1800 | 400.0985 |  | 1
95 | 80 | 63 | 39.1676 | 67387 | 57952.82 | 5.899 | 2100 | 555.5945 |  | 1
95 | 80 | 63 | 39.1676 | 70272 | 70272 | 5.947 | 2700 | 979.0808 |  | 1
95 | 85 | 63 | 29.0563 | 67530 | 67530 | 5.878 | 1800 | 400.0985 |  | 1
95 | 85 | 63 | 29.0563 | 68579 | 68579 | 5.909 | 2100 | 555.5945 |  | 1
95 | 85 | 63 | 29.0563 | 71463 | 71463 | 5.957 | 2700 | 983.4264 |  | 1
95 | 80 | 67 | 51.5724 | 68451 | 45177.66 | 5.859 | 1800 | 400.0985 |  | 1
95 | 80 | 67 | 51.5724 | 69500 | 50735 | 5.891 | 2100 | 555.5945 |  | 1
95 | 80 | 67 | 51.5724 | 72384 | 55735.68 | 5.938 | 2700 | 983.4264 |  | 1
95 | 85 | 67 | 39.6049 | 69642 | 52927.92 | 5.869 | 1800 | 400.0985 |  | 1
95 | 85 | 67 | 39.6049 | 70691 | 57966.62 | 5.901 | 2100 | 564.8456 |  | 1
95 | 85 | 67 | 39.6049 | 73576 | 64011.12 | 5.948 | 2700 | 983.4264 |  | 1
95 | 80 | 71 | 65.0618 | 71677 | 37272.04 | 5.899 | 1800 | 412.6122 |  | 1
95 | 80 | 71 | 65.0618 | 72726 | 42908.34 | 5.93 | 2100 | 564.8456 |  | 1
95 | 80 | 71 | 65.0618 | 75611 | 47634.93 | 5.978 | 2700 | 983.4264 |  | 1
95 | 85 | 71 | 51.076 | 72869 | 45178.78 | 5.909 | 1800 | 412.6122 |  | 1
95 | 85 | 71 | 51.076 | 73917 | 51002.73 | 5.94 | 2100 | 564.8456 |  | 1
95 | 85 | 71 | 51.076 | 76802 | 56065.46 | 5.988 | 2700 | 983.4264 |  | 1
105 | 80 | 59 | 27.7402 | 61458 | 61458 | 6.571 | 1800 | 400.0985 |  | 1
105 | 80 | 59 | 27.7402 | 62506 | 62506 | 6.602 | 2100 | 555.5945 |  | 1
105 | 80 | 59 | 27.7402 | 65391 | 65391 | 6.65 | 2700 | 979.0808 |  | 1
105 | 85 | 59 | 19.3387 | 62649 | 62649 | 6.581 | 1800 | 400.0985 |  | 1
105 | 85 | 59 | 19.3387 | 63698 | 63698 | 6.612 | 2100 | 555.5945 |  | 1
105 | 85 | 59 | 19.3387 | 66582 | 66582 | 6.66 | 2700 | 979.0808 |  | 1
105 | 80 | 63 | 39.1676 | 62456 | 50589.36 | 6.567 | 1800 | 400.0985 |  | 1
105 | 80 | 63 | 39.1676 | 63505 | 63505 | 6.598 | 2100 | 555.5945 |  | 1
105 | 80 | 63 | 39.1676 | 66390 | 66390 | 6.646 | 2700 | 979.0808 |  | 1
105 | 85 | 63 | 29.0563 | 63648 | 63648 | 6.577 | 1800 | 400.0985 |  | 1
105 | 85 | 63 | 29.0563 | 64696 | 64696 | 6.608 | 2100 | 555.5945 |  | 1
105 | 85 | 63 | 29.0563 | 67581 | 67581 | 6.656 | 2700 | 979.0808 |  | 1
105 | 80 | 67 | 51.5724 | 64569 | 43906.92 | 6.558 | 1800 | 400.0985 |  | 1
105 | 80 | 67 | 51.5724 | 65617 | 49212.75 | 6.589 | 2100 | 555.5945 |  | 1
105 | 80 | 67 | 51.5724 | 68502 | 54116.58 | 6.637 | 2700 | 979.0808 |  | 1
105 | 85 | 67 | 39.6049 | 65760 | 51292.8 | 6.568 | 1800 | 400.0985 |  | 1
105 | 85 | 67 | 39.6049 | 66809 | 56119.56 | 6.599 | 2100 | 555.5945 |  | 1
105 | 85 | 67 | 39.6049 | 69693 | 62026.77 | 6.647 | 2700 | 979.0808 |  | 1
105 | 80 | 71 | 65.0618 | 67795 | 36609.3 | 6.598 | 1800 | 400.0985 |  | 1
105 | 80 | 71 | 65.0618 | 68844 | 41994.84 | 6.629 | 2100 | 555.5945 |  | 1
105 | 80 | 71 | 65.0618 | 71728 | 46623.2 | 6.676 | 2700 | 983.4264 |  | 1
105 | 85 | 71 | 51.076 | 68986 | 44151.04 | 6.607 | 1800 | 400.0985 |  | 1
105 | 85 | 71 | 51.076 | 70035 | 49724.85 | 6.639 | 2100 | 555.5945 |  | 1
105 | 85 | 71 | 51.076 | 72920 | 54690 | 6.686 | 2700 | 983.4264 |  | 1
115 | 80 | 59 | 27.7402 | 57913 | 57913 | 7.39 | 1800 | 400.0985 |  | 1
115 | 80 | 59 | 27.7402 | 58962 | 58962 | 7.422 | 2100 | 555.5945 |  | 1
115 | 80 | 59 | 27.7402 | 61847 | 61847 | 7.469 | 2700 | 979.0808 |  | 1
115 | 85 | 59 | 19.3387 | 59105 | 59105 | 7.4 | 1800 | 400.0985 |  | 1
115 | 85 | 59 | 19.3387 | 60154 | 60154 | 7.431 | 2100 | 555.5945 |  | 1
115 | 85 | 59 | 19.3387 | 63038 | 63038 | 7.479 | 2700 | 979.0808 |  | 1
115 | 80 | 63 | 39.1676 | 58912 | 58912 | 7.386 | 1800 | 400.0985 |  | 1
115 | 80 | 63 | 39.1676 | 59961 | 59961 | 7.417 | 2100 | 555.5945 |  | 1
115 | 80 | 63 | 39.1676 | 62845 | 62845 | 7.465 | 2700 | 979.0808 |  | 1
115 | 85 | 63 | 29.0563 | 60104 | 60104 | 7.396 | 1800 | 400.0985 |  | 1
115 | 85 | 63 | 29.0563 | 61152 | 61152 | 7.427 | 2100 | 555.5945 |  | 1
115 | 85 | 63 | 29.0563 | 64037 | 64037 | 7.475 | 2700 | 979.0808 |  | 1
115 | 80 | 67 | 51.5724 | 61024 | 44547.52 | 7.377 | 1800 | 400.0985 |  | 1
115 | 80 | 67 | 51.5724 | 62073 | 49658.4 | 7.409 | 2100 | 555.5945 |  | 1
115 | 80 | 67 | 51.5724 | 64958 | 54564.72 | 7.456 | 2700 | 979.0808 |  | 1
115 | 85 | 67 | 39.6049 | 62216 | 51639.28 | 7.387 | 1800 | 400.0985 |  | 1
115 | 85 | 67 | 39.6049 | 63264 | 56558.02 | 7.418 | 2100 | 555.5945 |  | 1
115 | 85 | 67 | 39.6049 | 66149 | 66149 | 7.466 | 2700 | 979.0808 |  | 1
115 | 80 | 71 | 65.0618 | 64251 | 37908.09 | 7.417 | 1800 | 400.0985 |  | 1
115 | 80 | 71 | 65.0618 | 65300 | 43098 | 7.448 | 2100 | 555.5945 |  | 1
115 | 80 | 71 | 65.0618 | 68184 | 47728.8 | 7.496 | 2700 | 979.0808 |  | 1
115 | 85 | 71 | 51.076 | 65442 | 45154.98 | 7.427 | 1800 | 400.0985 |  | 1
115 | 85 | 71 | 51.076 | 66491 | 50333.69 | 7.458 | 2100 | 555.5945 |  | 1
115 | 85 | 71 | 51.076 | 69375 | 55500 | 7.506 | 2700 | 979.0808 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 2
Degradation Coefficient (C_d)
IEER or SEER | 17
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 70 | 59 | 52.72 | 91600 | 55876 | 5.25 | 2625 | 545.9553 |  | 2
65 | 70 | 59 | 52.72 | 92800 | 62176 | 5.28 | 3000 | 829.352 |  | 2
65 | 70 | 59 | 52.72 | 94200 | 65940 | 5.31 | 3375 | 1091.9106 |  | 2
65 | 75 | 59 | 38.63 | 91600 | 67784 | 5.24 | 2625 | 545.9553 |  | 2
65 | 75 | 59 | 38.63 | 92800 | 74240 | 5.27 | 3000 | 829.352 |  | 2
65 | 75 | 59 | 38.63 | 94300 | 78269 | 5.3 | 3375 | 1091.9106 |  | 2
65 | 70 | 63 | 68.69 | 92900 | 49237 | 5.24 | 2625 | 545.9553 |  | 2
65 | 70 | 63 | 68.69 | 94100 | 55519 | 5.27 | 3000 | 829.352 |  | 2
65 | 70 | 63 | 68.69 | 95500 | 60165 | 5.3 | 3375 | 1091.9106 |  | 2
65 | 75 | 63 | 52.11 | 92900 | 61314 | 5.24 | 2625 | 545.9553 |  | 2
65 | 75 | 63 | 52.11 | 94100 | 67752 | 5.27 | 3000 | 829.352 |  | 2
65 | 75 | 63 | 52.11 | 95600 | 71700 | 5.3 | 3375 | 1091.9106 |  | 2
65 | 70 | 67 | 86.02 | 95600 | 38240 | 5.23 | 2625 | 545.9553 |  | 2
65 | 70 | 67 | 86.02 | 96800 | 44528 | 5.26 | 3000 | 829.352 |  | 2
65 | 70 | 67 | 86.02 | 98200 | 48118 | 5.29 | 3375 | 1091.9106 |  | 2
65 | 75 | 67 | 66.75 | 95600 | 49712 | 5.23 | 2625 | 545.9553 |  | 2
65 | 75 | 67 | 66.75 | 96800 | 56144 | 5.26 | 3000 | 829.352 |  | 2
65 | 75 | 67 | 66.75 | 98300 | 60946 | 5.29 | 3375 | 1091.9106 |  | 2
65 | 75 | 71 | 82.67 | 99800 | 39920 | 5.3 | 2625 | 545.9553 |  | 2
65 | 75 | 71 | 82.67 | 101000 | 40400 | 5.3 | 3000 | 829.352 |  | 2
65 | 75 | 71 | 82.67 | 102500 | 51250 | 5.3 | 3375 | 1091.9106 |  | 2
75 | 70 | 59 | 52.72 | 90700 | 55327 | 5.86 | 2625 | 545.9553 |  | 2
75 | 70 | 59 | 52.72 | 91900 | 61573 | 5.9 | 3000 | 829.352 |  | 2
75 | 70 | 59 | 52.72 | 93400 | 66314 | 5.92 | 3375 | 1091.9106 |  | 2
75 | 75 | 59 | 38.63 | 90800 | 90800 | 5.86 | 2625 | 545.9553 |  | 2
75 | 75 | 59 | 38.63 | 92000 | 92000 | 5.89 | 3000 | 829.352 |  | 2
75 | 75 | 59 | 38.63 | 93400 | 93400 | 5.92 | 3375 | 1091.9106 |  | 2
75 | 70 | 63 | 68.69 | 92000 | 49680 | 5.86 | 2625 | 545.9553 |  | 2
75 | 70 | 63 | 68.69 | 93200 | 55920 | 5.89 | 3000 | 829.352 |  | 2
75 | 70 | 63 | 68.69 | 94700 | 59661 | 5.92 | 3375 | 1091.9106 |  | 2
75 | 75 | 63 | 52.11 | 92100 | 61707 | 5.86 | 2625 | 545.9553 |  | 2
75 | 75 | 63 | 52.11 | 93300 | 68109 | 5.89 | 3000 | 829.352 |  | 2
75 | 75 | 63 | 52.11 | 94700 | 71972 | 5.91 | 3375 | 1091.9106 |  | 2
75 | 70 | 67 | 86.02 | 94800 | 37920 | 5.85 | 2625 | 545.9553 |  | 2
75 | 70 | 67 | 86.02 | 96000 | 44160 | 5.88 | 3000 | 829.352 |  | 2
75 | 70 | 67 | 86.02 | 97400 | 48700 | 5.91 | 3375 | 1091.9106 |  | 2
75 | 75 | 67 | 66.75 | 94800 | 50244 | 5.84 | 2625 | 545.9553 |  | 2
75 | 75 | 67 | 66.75 | 96000 | 56640 | 5.88 | 3000 | 829.352 |  | 2
75 | 75 | 67 | 66.75 | 97500 | 60450 | 5.9 | 3375 | 1091.9106 |  | 2
75 | 75 | 71 | 82.67 | 99000 | 39600 | 5.9 | 2625 | 545.9553 |  | 2
75 | 75 | 71 | 82.67 | 100200 | 40080 | 5.9 | 3000 | 829.352 |  | 2
75 | 75 | 71 | 82.67 | 101700 | 50850 | 6 | 3375 | 1091.9106 |  | 2
85 | 70 | 59 | 52.72 | 88400 | 56576 | 6.55 | 2625 | 545.9553 |  | 2
85 | 70 | 59 | 52.72 | 89600 | 62720 | 6.58 | 3000 | 829.352 |  | 2
85 | 70 | 59 | 52.72 | 91000 | 91000 | 6.61 | 3375 | 1091.9106 |  | 2
85 | 75 | 59 | 38.63 | 88400 | 88400 | 6.55 | 2625 | 545.9553 |  | 2
85 | 75 | 59 | 38.63 | 89600 | 89600 | 6.58 | 3000 | 829.352 |  | 2
85 | 75 | 59 | 38.63 | 91100 | 91100 | 6.61 | 3375 | 1091.9106 |  | 2
85 | 70 | 63 | 68.69 | 89600 | 50176 | 6.55 | 2625 | 545.9553 |  | 2
85 | 70 | 63 | 68.69 | 90900 | 56358 | 6.58 | 3000 | 829.352 |  | 2
85 | 70 | 63 | 68.69 | 92300 | 60918 | 6.61 | 3375 | 1091.9106 |  | 2
85 | 75 | 63 | 52.11 | 89700 | 61893 | 6.54 | 2625 | 545.9553 |  | 2
85 | 75 | 63 | 52.11 | 90900 | 68175 | 6.58 | 3000 | 829.352 |  | 2
85 | 75 | 63 | 52.11 | 92300 | 72917 | 6.6 | 3375 | 1091.9106 |  | 2
85 | 70 | 67 | 86.02 | 92400 | 39732 | 6.54 | 2625 | 545.9553 |  | 2
85 | 70 | 67 | 86.02 | 93600 | 45864 | 6.57 | 3000 | 829.352 |  | 2
85 | 70 | 67 | 86.02 | 95000 | 49400 | 6.6 | 3375 | 1091.9106 |  | 2
85 | 75 | 67 | 66.75 | 92400 | 51744 | 6.53 | 2625 | 545.9553 |  | 2
85 | 75 | 67 | 66.75 | 93600 | 58032 | 6.57 | 3000 | 829.352 |  | 2
85 | 75 | 67 | 66.75 | 95100 | 61815 | 6.59 | 3375 | 1091.9106 |  | 2
85 | 75 | 71 | 82.67 | 96600 | 38640 | 6.6 | 2625 | 545.9553 |  | 2
85 | 75 | 71 | 82.67 | 97800 | 48900 | 6.6 | 3000 | 829.352 |  | 2
85 | 75 | 71 | 82.67 | 99300 | 49650 | 6.6 | 3375 | 1091.9106 |  | 2
95 | 70 | 59 | 52.72 | 84200 | 84200 | 7.3 | 2625 | 545.9553 |  | 2
95 | 70 | 59 | 52.72 | 85400 | 85400 | 7.33 | 3000 | 829.352 |  | 2
95 | 70 | 59 | 52.72 | 86900 | 86900 | 7.36 | 3375 | 1091.9106 |  | 2
95 | 75 | 59 | 38.63 | 84300 | 84300 | 7.29 | 2625 | 545.9553 |  | 2
95 | 75 | 59 | 38.63 | 85500 | 85500 | 7.33 | 3000 | 829.352 |  | 2
95 | 75 | 59 | 38.63 | 86900 | 86900 | 7.35 | 3375 | 1091.9106 |  | 2
95 | 70 | 63 | 68.69 | 85500 | 49590 | 7.29 | 2625 | 545.9553 |  | 2
95 | 70 | 63 | 68.69 | 86700 | 55488 | 7.33 | 3000 | 829.352 |  | 2
95 | 70 | 63 | 68.69 | 88200 | 59976 | 7.35 | 3375 | 1091.9106 |  | 2
95 | 75 | 63 | 52.11 | 85600 | 60776 | 7.29 | 2625 | 545.9553 |  | 2
95 | 75 | 63 | 52.11 | 86800 | 66836 | 7.32 | 3000 | 829.352 |  | 2
95 | 75 | 63 | 52.11 | 88200 | 71442 | 7.35 | 3375 | 1091.9106 |  | 2
95 | 70 | 67 | 86.02 | 88300 | 39735 | 7.28 | 2625 | 545.9553 |  | 2
95 | 70 | 67 | 86.02 | 89500 | 45645 | 7.31 | 3000 | 829.352 |  | 2
95 | 70 | 67 | 86.02 | 90900 | 49086 | 7.34 | 3375 | 1091.9106 |  | 2
95 | 75 | 67 | 66.75 | 88300 | 51214 | 7.28 | 2625 | 545.9553 |  | 2
95 | 75 | 67 | 66.75 | 89500 | 57280 | 7.31 | 3000 | 829.352 |  | 2
95 | 75 | 67 | 66.75 | 91000 | 60970 | 7.34 | 3375 | 1091.9106 |  | 2
95 | 75 | 71 | 82.67 | 92500 | 37000 | 7.3 | 2625 | 545.9553 |  | 2
95 | 75 | 71 | 82.67 | 93700 | 46850 | 7.4 | 3000 | 829.352 |  | 2
95 | 75 | 71 | 82.67 | 95100 | 47550 | 7.4 | 3375 | 1091.9106 |  | 2
105 | 70 | 59 | 52.72 | 79200 | 79200 | 8.13 | 2625 | 545.9553 |  | 2
105 | 70 | 59 | 52.72 | 80400 | 80400 | 8.16 | 3000 | 829.352 |  | 2
105 | 70 | 59 | 52.72 | 81900 | 81900 | 8.19 | 3375 | 1091.9106 |  | 2
105 | 75 | 59 | 38.63 | 79300 | 79300 | 8.13 | 2625 | 545.9553 |  | 2
105 | 75 | 59 | 38.63 | 80500 | 80500 | 8.16 | 3000 | 829.352 |  | 2
105 | 75 | 59 | 38.63 | 81900 | 81900 | 8.19 | 3375 | 1091.9106 |  | 2
105 | 70 | 63 | 68.69 | 80500 | 48300 | 8.13 | 2625 | 545.9553 |  | 2
105 | 70 | 63 | 68.69 | 81700 | 53922 | 8.16 | 3000 | 829.352 |  | 2
105 | 70 | 63 | 68.69 | 83200 | 58240 | 8.18 | 3375 | 1091.9106 |  | 2
105 | 75 | 63 | 52.11 | 80600 | 58838 | 8.12 | 2625 | 545.9553 |  | 2
105 | 75 | 63 | 52.11 | 81800 | 81800 | 8.15 | 3000 | 829.352 |  | 2
105 | 75 | 63 | 52.11 | 83200 | 83200 | 8.18 | 3375 | 1091.9106 |  | 2
105 | 70 | 67 | 86.02 | 83200 | 39104 | 8.12 | 2625 | 545.9553 |  | 2
105 | 70 | 67 | 86.02 | 84400 | 44732 | 8.15 | 3000 | 829.352 |  | 2
105 | 70 | 67 | 86.02 | 85900 | 48104 | 8.17 | 3375 | 1091.9106 |  | 2
105 | 75 | 67 | 66.75 | 83300 | 49980 | 8.11 | 2625 | 545.9553 |  | 2
105 | 75 | 67 | 66.75 | 84500 | 55770 | 8.14 | 3000 | 829.352 |  | 2
105 | 75 | 67 | 66.75 | 85900 | 59271 | 8.17 | 3375 | 1091.9106 |  | 2
105 | 75 | 71 | 82.67 | 87500 | 43750 | 8.2 | 2625 | 545.9553 |  | 2
105 | 75 | 71 | 82.67 | 88700 | 44350 | 8.2 | 3000 | 829.352 |  | 2
105 | 75 | 71 | 82.67 | 90100 | 45050 | 8.2 | 3375 | 1091.9106 |  | 2
115 | 70 | 59 | 52.72 | 74600 | 74600 | 9.11 | 2625 | 545.9553 |  | 2
115 | 70 | 59 | 52.72 | 75800 | 75800 | 9.14 | 3000 | 829.352 |  | 2
115 | 70 | 59 | 52.72 | 77300 | 77300 | 9.17 | 3375 | 1091.9106 |  | 2
115 | 75 | 59 | 38.63 | 74700 | 74700 | 9.1 | 2625 | 545.9553 |  | 2
115 | 75 | 59 | 38.63 | 75900 | 75900 | 9.14 | 3000 | 829.352 |  | 2
115 | 75 | 59 | 38.63 | 77300 | 77300 | 9.16 | 3375 | 1091.9106 |  | 2
115 | 70 | 63 | 68.69 | 75900 | 50094 | 9.1 | 2625 | 545.9553 |  | 2
115 | 70 | 63 | 68.69 | 77100 | 55512 | 9.13 | 3000 | 829.352 |  | 2
115 | 70 | 63 | 68.69 | 78600 | 78600 | 9.16 | 3375 | 1091.9106 |  | 2
115 | 75 | 63 | 52.11 | 76000 | 76000 | 9.1 | 2625 | 545.9553 |  | 2
115 | 75 | 63 | 52.11 | 77200 | 77200 | 9.13 | 3000 | 829.352 |  | 2
115 | 75 | 63 | 52.11 | 78600 | 78600 | 9.16 | 3375 | 1091.9106 |  | 2
115 | 70 | 67 | 86.02 | 78700 | 40924 | 9.09 | 2625 | 545.9553 |  | 2
115 | 70 | 67 | 86.02 | 79900 | 46342 | 9.12 | 3000 | 829.352 |  | 2
115 | 70 | 67 | 86.02 | 81300 | 49593 | 9.15 | 3375 | 1091.9106 |  | 2
115 | 75 | 67 | 66.75 | 78700 | 51155 | 9.09 | 2625 | 545.9553 |  | 2
115 | 75 | 67 | 66.75 | 79900 | 56729 | 9.12 | 3000 | 829.352 |  | 2
115 | 75 | 67 | 66.75 | 81400 | 60236 | 9.15 | 3375 | 1091.9106 |  | 2
115 | 75 | 71 | 82.67 | 82900 | 41450 | 9.1 | 2625 | 545.9553 |  | 2
115 | 75 | 71 | 82.67 | 84100 | 50460 | 9.2 | 3000 | 829.352 |  | 2
115 | 75 | 71 | 82.67 | 85500 | 51300 | 9.2 | 3375 | 1091.9106 |  | 2
65 | 80 | 59 | 27.74 | 92100 | 92100 | 5.25 | 2625 | 545.9553 |  | 2
65 | 80 | 59 | 27.74 | 93300 | 93300 | 5.28 | 3000 | 829.352 |  | 2
65 | 80 | 59 | 27.74 | 94700 | 94700 | 5.31 | 3375 | 1091.9106 |  | 2
65 | 85 | 59 | 19.34 | 93600 | 93600 | 5.26 | 2625 | 545.9553 |  | 2
65 | 85 | 59 | 19.34 | 94800 | 94800 | 5.29 | 3000 | 829.352 |  | 2
65 | 85 | 59 | 19.34 | 96300 | 96300 | 5.32 | 3375 | 1091.9106 |  | 2
65 | 80 | 63 | 39.17 | 93400 | 73786 | 5.24 | 2625 | 545.9553 |  | 2
65 | 80 | 63 | 39.17 | 94600 | 80410 | 5.27 | 3000 | 829.352 |  | 2
65 | 80 | 63 | 39.17 | 96000 | 84480 | 5.3 | 3375 | 1091.9106 |  | 2
65 | 85 | 63 | 29.06 | 94900 | 84461 | 5.25 | 2625 | 545.9553 |  | 2
65 | 85 | 63 | 29.06 | 96100 | 91295 | 5.29 | 3000 | 829.352 |  | 2
65 | 85 | 63 | 29.06 | 97600 | 95648 | 5.31 | 3375 | 1091.9106 |  | 2
65 | 80 | 67 | 51.57 | 96100 | 62465 | 5.23 | 2625 | 545.9553 |  | 2
65 | 80 | 67 | 51.57 | 97300 | 69083 | 5.26 | 3000 | 829.352 |  | 2
65 | 80 | 67 | 51.57 | 98800 | 73112 | 5.29 | 3375 | 1091.9106 |  | 2
65 | 85 | 67 | 39.6 | 97700 | 73275 | 5.24 | 2625 | 545.9553 |  | 2
65 | 85 | 67 | 39.6 | 98900 | 80109 | 5.27 | 3000 | 829.352 |  | 2
65 | 85 | 67 | 39.6 | 100300 | 85255 | 5.3 | 3375 | 1091.9106 |  | 2
65 | 80 | 71 | 65.06 | 100300 | 50150 | 5.3 | 2625 | 545.9553 |  | 2
65 | 80 | 71 | 65.06 | 101500 | 60900 | 5.3 | 3000 | 829.352 |  | 2
65 | 80 | 71 | 65.06 | 102900 | 61740 | 5.3 | 3375 | 1091.9106 |  | 2
65 | 85 | 71 | 51.08 | 101800 | 61080 | 5.3 | 2625 | 545.9553 |  | 2
65 | 85 | 71 | 51.08 | 103000 | 72100 | 5.3 | 3000 | 829.352 |  | 2
65 | 85 | 71 | 51.08 | 104500 | 73150 | 5.3 | 3375 | 1091.9106 |  | 2
75 | 80 | 59 | 27.74 | 91300 | 91300 | 5.86 | 2625 | 545.9553 |  | 2
75 | 80 | 59 | 27.74 | 92500 | 92500 | 5.9 | 3000 | 829.352 |  | 2
75 | 80 | 59 | 27.74 | 93900 | 93900 | 5.92 | 3375 | 1091.9106 |  | 2
75 | 85 | 59 | 19.34 | 92800 | 92800 | 5.87 | 2625 | 545.9553 |  | 2
75 | 85 | 59 | 19.34 | 94000 | 94000 | 5.91 | 3000 | 829.352 |  | 2
75 | 85 | 59 | 19.34 | 95500 | 95500 | 5.93 | 3375 | 1091.9106 |  | 2
75 | 80 | 63 | 39.17 | 92600 | 73154 | 5.86 | 2625 | 545.9553 |  | 2
75 | 80 | 63 | 39.17 | 93800 | 79730 | 5.89 | 3000 | 829.352 |  | 2
75 | 80 | 63 | 39.17 | 95200 | 84728 | 5.92 | 3375 | 1091.9106 |  | 2
75 | 85 | 63 | 29.06 | 94100 | 94100 | 5.87 | 2625 | 545.9553 |  | 2
75 | 85 | 63 | 29.06 | 95300 | 95300 | 5.9 | 3000 | 829.352 |  | 2
75 | 85 | 63 | 29.06 | 96800 | 96800 | 5.93 | 3375 | 1091.9106 |  | 2
75 | 80 | 67 | 51.57 | 95300 | 62898 | 5.85 | 2625 | 545.9553 |  | 2
75 | 80 | 67 | 51.57 | 96500 | 69480 | 5.88 | 3000 | 829.352 |  | 2
75 | 80 | 67 | 51.57 | 97900 | 73425 | 5.91 | 3375 | 1091.9106 |  | 2
75 | 85 | 67 | 39.6 | 96800 | 73568 | 5.86 | 2625 | 545.9553 |  | 2
75 | 85 | 67 | 39.6 | 98000 | 80360 | 5.89 | 3000 | 829.352 |  | 2
75 | 85 | 67 | 39.6 | 99500 | 84575 | 5.92 | 3375 | 1091.9106 |  | 2
75 | 80 | 71 | 65.06 | 99500 | 49750 | 5.9 | 2625 | 545.9553 |  | 2
75 | 80 | 71 | 65.06 | 100700 | 60420 | 5.9 | 3000 | 829.352 |  | 2
75 | 80 | 71 | 65.06 | 102100 | 61260 | 6 | 3375 | 1091.9106 |  | 2
75 | 85 | 71 | 51.08 | 101000 | 60600 | 5.9 | 2625 | 545.9553 |  | 2
75 | 85 | 71 | 51.08 | 102200 | 71540 | 5.9 | 3000 | 829.352 |  | 2
75 | 85 | 71 | 51.08 | 103700 | 72590 | 6 | 3375 | 1091.9106 |  | 2
85 | 80 | 59 | 27.74 | 88900 | 88900 | 6.55 | 2625 | 545.9553 |  | 2
85 | 80 | 59 | 27.74 | 90100 | 90100 | 6.58 | 3000 | 829.352 |  | 2
85 | 80 | 59 | 27.74 | 91500 | 91500 | 6.61 | 3375 | 1091.9106 |  | 2
85 | 85 | 59 | 19.34 | 90400 | 90400 | 6.56 | 2625 | 545.9553 |  | 2
85 | 85 | 59 | 19.34 | 91600 | 91600 | 6.6 | 3000 | 829.352 |  | 2
85 | 85 | 59 | 19.34 | 93100 | 93100 | 6.62 | 3375 | 1091.9106 |  | 2
85 | 80 | 63 | 39.17 | 90200 | 73964 | 6.55 | 2625 | 545.9553 |  | 2
85 | 80 | 63 | 39.17 | 91400 | 80432 | 6.58 | 3000 | 829.352 |  | 2
85 | 80 | 63 | 39.17 | 92800 | 92800 | 6.61 | 3375 | 1091.9106 |  | 2
85 | 85 | 63 | 29.06 | 91700 | 91700 | 6.56 | 2625 | 545.9553 |  | 2
85 | 85 | 63 | 29.06 | 92900 | 92900 | 6.59 | 3000 | 829.352 |  | 2
85 | 85 | 63 | 29.06 | 94400 | 94400 | 6.62 | 3375 | 1091.9106 |  | 2
85 | 80 | 67 | 51.57 | 92900 | 63172 | 6.54 | 2625 | 545.9553 |  | 2
85 | 80 | 67 | 51.57 | 94100 | 69634 | 6.57 | 3000 | 829.352 |  | 2
85 | 80 | 67 | 51.57 | 95600 | 74568 | 6.6 | 3375 | 1091.9106 |  | 2
85 | 85 | 67 | 39.6 | 94500 | 73710 | 6.55 | 2625 | 545.9553 |  | 2
85 | 85 | 67 | 39.6 | 95700 | 80388 | 6.58 | 3000 | 829.352 |  | 2
85 | 85 | 67 | 39.6 | 97100 | 85448 | 6.61 | 3375 | 1091.9106 |  | 2
85 | 80 | 71 | 65.06 | 97100 | 48550 | 6.6 | 2625 | 545.9553 |  | 2
85 | 80 | 71 | 65.06 | 98300 | 58980 | 6.6 | 3000 | 829.352 |  | 2
85 | 80 | 71 | 65.06 | 99700 | 59820 | 6.6 | 3375 | 1091.9106 |  | 2
85 | 85 | 71 | 51.08 | 98600 | 59160 | 6.6 | 2625 | 545.9553 |  | 2
85 | 85 | 71 | 51.08 | 99800 | 69860 | 6.6 | 3000 | 829.352 |  | 2
85 | 85 | 71 | 51.08 | 101300 | 70910 | 6.7 | 3375 | 1091.9106 |  | 2
95 | 80 | 59 | 27.74 | 84800 | 84800 | 7.3 | 2625 | 545.9553 |  | 2
95 | 80 | 59 | 27.74 | 86000 | 86000 | 7.33 | 3000 | 829.352 |  | 2
95 | 80 | 59 | 27.74 | 87400 | 87400 | 7.36 | 3375 | 1091.9106 |  | 2
95 | 85 | 59 | 19.34 | 86300 | 86300 | 7.31 | 2625 | 545.9553 |  | 2
95 | 85 | 59 | 19.34 | 87500 | 87500 | 7.34 | 3000 | 829.352 |  | 2
95 | 85 | 59 | 19.34 | 89000 | 89000 | 7.37 | 3375 | 1091.9106 |  | 2
95 | 80 | 63 | 39.17 | 86100 | 86100 | 7.29 | 2625 | 545.9553 |  | 2
95 | 80 | 63 | 39.17 | 87300 | 87300 | 7.32 | 3000 | 829.352 |  | 2
95 | 80 | 63 | 39.17 | 88700 | 88700 | 7.35 | 3375 | 1091.9106 |  | 2
95 | 85 | 63 | 29.06 | 87600 | 87600 | 7.3 | 2625 | 545.9553 |  | 2
95 | 85 | 63 | 29.06 | 88800 | 88800 | 7.34 | 3000 | 829.352 |  | 2
95 | 85 | 63 | 29.06 | 90300 | 90300 | 7.36 | 3375 | 1091.9106 |  | 2
95 | 80 | 67 | 51.57 | 88800 | 62160 | 7.28 | 2625 | 545.9553 |  | 2
95 | 80 | 67 | 51.57 | 90000 | 68400 | 7.31 | 3000 | 829.352 |  | 2
95 | 80 | 67 | 51.57 | 91400 | 73120 | 7.34 | 3375 | 1091.9106 |  | 2
95 | 85 | 67 | 39.6 | 90300 | 72240 | 7.29 | 2625 | 545.9553 |  | 2
95 | 85 | 67 | 39.6 | 91500 | 78690 | 7.33 | 3000 | 829.352 |  | 2
95 | 85 | 67 | 39.6 | 93000 | 83700 | 7.35 | 3375 | 1091.9106 |  | 2
95 | 80 | 71 | 65.06 | 93000 | 55800 | 7.3 | 2625 | 545.9553 |  | 2
95 | 80 | 71 | 65.06 | 94200 | 56520 | 7.4 | 3000 | 829.352 |  | 2
95 | 80 | 71 | 65.06 | 95600 | 66920 | 7.4 | 3375 | 1091.9106 |  | 2
95 | 85 | 71 | 51.08 | 94500 | 66150 | 7.3 | 2625 | 545.9553 |  | 2
95 | 85 | 71 | 51.08 | 95700 | 66990 | 7.4 | 3000 | 829.352 |  | 2
95 | 85 | 71 | 51.08 | 97200 | 77760 | 7.4 | 3375 | 1091.9106 |  | 2
105 | 80 | 59 | 27.74 | 79700 | 79700 | 8.13 | 2625 | 545.9553 |  | 2
105 | 80 | 59 | 27.74 | 80900 | 80900 | 8.16 | 3000 | 829.352 |  | 2
105 | 80 | 59 | 27.74 | 82400 | 82400 | 8.19 | 3375 | 1091.9106 |  | 2
105 | 85 | 59 | 19.34 | 81300 | 81300 | 8.14 | 2625 | 545.9553 |  | 2
105 | 85 | 59 | 19.34 | 82500 | 82500 | 8.17 | 3000 | 829.352 |  | 2
105 | 85 | 59 | 19.34 | 83900 | 83900 | 8.2 | 3375 | 1091.9106 |  | 2
105 | 80 | 63 | 39.17 | 81000 | 81000 | 8.12 | 2625 | 545.9553 |  | 2
105 | 80 | 63 | 39.17 | 82200 | 82200 | 8.16 | 3000 | 829.352 |  | 2
105 | 80 | 63 | 39.17 | 83700 | 83700 | 8.18 | 3375 | 1091.9106 |  | 2
105 | 85 | 63 | 29.06 | 82600 | 82600 | 8.14 | 2625 | 545.9553 |  | 2
105 | 85 | 63 | 29.06 | 83800 | 83800 | 8.17 | 3000 | 829.352 |  | 2
105 | 85 | 63 | 29.06 | 85200 | 85200 | 8.2 | 3375 | 1091.9106 |  | 2
105 | 80 | 67 | 51.57 | 83800 | 60336 | 8.11 | 2625 | 545.9553 |  | 2
105 | 80 | 67 | 51.57 | 85000 | 66300 | 8.15 | 3000 | 829.352 |  | 2
105 | 80 | 67 | 51.57 | 86400 | 70848 | 8.17 | 3375 | 1091.9106 |  | 2
105 | 85 | 67 | 39.6 | 85300 | 85300 | 8.13 | 2625 | 545.9553 |  | 2
105 | 85 | 67 | 39.6 | 86500 | 86500 | 8.16 | 3000 | 829.352 |  | 2
105 | 85 | 67 | 39.6 | 88000 | 88000 | 8.19 | 3375 | 1091.9106 |  | 2
105 | 80 | 71 | 65.06 | 87900 | 52740 | 8.2 | 2625 | 545.9553 |  | 2
105 | 80 | 71 | 65.06 | 89200 | 53520 | 8.2 | 3000 | 829.352 |  | 2
105 | 80 | 71 | 65.06 | 90600 | 63420 | 8.2 | 3375 | 1091.9106 |  | 2
105 | 85 | 71 | 51.08 | 89500 | 62650 | 8.2 | 2625 | 545.9553 |  | 2
105 | 85 | 71 | 51.08 | 90700 | 63490 | 8.2 | 3000 | 829.352 |  | 2
105 | 85 | 71 | 51.08 | 92100 | 73680 | 8.2 | 3375 | 1091.9106 |  | 2
115 | 80 | 59 | 27.74 | 75200 | 75200 | 9.11 | 2625 | 545.9553 |  | 2
115 | 80 | 59 | 27.74 | 76400 | 76400 | 9.14 | 3000 | 829.352 |  | 2
115 | 80 | 59 | 27.74 | 77800 | 77800 | 9.17 | 3375 | 1091.9106 |  | 2
115 | 85 | 59 | 19.34 | 76700 | 76700 | 9.12 | 2625 | 545.9553 |  | 2
115 | 85 | 59 | 19.34 | 77900 | 77900 | 9.15 | 3000 | 829.352 |  | 2
115 | 85 | 59 | 19.34 | 79300 | 79300 | 9.18 | 3375 | 1091.9106 |  | 2
115 | 80 | 63 | 39.17 | 76400 | 76400 | 9.1 | 2625 | 545.9553 |  | 2
115 | 80 | 63 | 39.17 | 77600 | 77600 | 9.13 | 3000 | 829.352 |  | 2
115 | 80 | 63 | 39.17 | 79100 | 79100 | 9.16 | 3375 | 1091.9106 |  | 2
115 | 85 | 63 | 29.06 | 78000 | 78000 | 9.11 | 2625 | 545.9553 |  | 2
115 | 85 | 63 | 29.06 | 79200 | 79200 | 9.15 | 3000 | 829.352 |  | 2
115 | 85 | 63 | 29.06 | 80600 | 80600 | 9.17 | 3375 | 1091.9106 |  | 2
115 | 80 | 67 | 51.57 | 79200 | 60984 | 9.09 | 2625 | 545.9553 |  | 2
115 | 80 | 67 | 51.57 | 80400 | 66732 | 9.12 | 3000 | 829.352 |  | 2
115 | 80 | 67 | 51.57 | 81800 | 81800 | 9.15 | 3375 | 1091.9106 |  | 2
115 | 85 | 67 | 39.6 | 80700 | 80700 | 9.1 | 2625 | 545.9553 |  | 2
115 | 85 | 67 | 39.6 | 81900 | 81900 | 9.14 | 3000 | 829.352 |  | 2
115 | 85 | 67 | 39.6 | 83400 | 83400 | 9.16 | 3375 | 1091.9106 |  | 2
115 | 80 | 71 | 65.06 | 83400 | 50040 | 9.1 | 2625 | 545.9553 |  | 2
115 | 80 | 71 | 65.06 | 84600 | 59220 | 9.2 | 3000 | 829.352 |  | 2
115 | 80 | 71 | 65.06 | 86000 | 60200 | 9.2 | 3375 | 1091.9106 |  | 2
115 | 85 | 71 | 51.08 | 84900 | 59430 | 9.2 | 2625 | 545.9553 |  | 2
115 | 85 | 71 | 51.08 | 86100 | 68880 | 9.2 | 3000 | 829.352 |  | 2
115 | 85 | 71 | 51.08 | 87500 | 70000 | 9.2 | 3375 | 1091.9106 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 3
Degradation Coefficient (C_d)
IEER or SEER | 17
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 70 | 59 | 52.72 | 105100 | 68315 | 6.06 | 3100 | 706.4078 |  | 2
65 | 70 | 59 | 52.72 | 106400 | 72352 | 6.09 | 3400 | 866.8603 |  | 2
65 | 70 | 59 | 52.72 | 108500 | 74865 | 6.12 | 3825 | 1162.7598 |  | 2
65 | 75 | 59 | 38.63 | 105200 | 82056 | 6.06 | 3100 | 706.4078 |  | 2
65 | 75 | 59 | 38.63 | 106400 | 85120 | 6.08 | 3400 | 866.8603 |  | 2
65 | 75 | 59 | 38.63 | 108500 | 88970 | 6.11 | 3825 | 1162.7598 |  | 2
65 | 70 | 63 | 68.69 | 106600 | 61828 | 6.06 | 3100 | 720.9944 |  | 2
65 | 70 | 63 | 68.69 | 107800 | 64680 | 6.08 | 3400 | 866.8603 |  | 2
65 | 70 | 63 | 68.69 | 109900 | 68138 | 6.11 | 3825 | 1162.7598 |  | 2
65 | 75 | 63 | 52.11 | 106700 | 74690 | 6.05 | 3100 | 720.9944 |  | 2
65 | 75 | 63 | 52.11 | 107900 | 78767 | 6.08 | 3400 | 866.8603 |  | 2
65 | 75 | 63 | 52.11 | 110000 | 82500 | 6.11 | 3825 | 1162.7598 |  | 2
65 | 70 | 67 | 86.02 | 109700 | 48268 | 6.05 | 3100 | 720.9944 |  | 2
65 | 70 | 67 | 86.02 | 110900 | 52123 | 6.07 | 3400 | 866.8603 |  | 2
65 | 70 | 67 | 86.02 | 113000 | 55370 | 6.1 | 3825 | 1162.7598 |  | 2
65 | 75 | 67 | 66.75 | 109800 | 62586 | 6.04 | 3100 | 720.9944 |  | 2
65 | 75 | 67 | 66.75 | 111000 | 66600 | 6.06 | 3400 | 866.8603 |  | 2
65 | 75 | 67 | 66.75 | 113100 | 68991 | 6.09 | 3825 | 1162.7598 |  | 2
65 | 75 | 71 | 82.67 | 114500 | 45800 | 6.1 | 3100 | 720.9944 |  | 2
65 | 75 | 71 | 82.67 | 115700 | 57850 | 6.1 | 3400 | 866.8603 |  | 2
65 | 75 | 71 | 82.67 | 117800 | 58900 | 6.1 | 3825 | 1162.7598 |  | 2
75 | 70 | 59 | 52.72 | 104200 | 68772 | 6.76 | 3100 | 706.4078 |  | 2
75 | 70 | 59 | 52.72 | 105400 | 71672 | 6.78 | 3400 | 850.1899 |  | 2
75 | 70 | 59 | 52.72 | 107500 | 75250 | 6.81 | 3825 | 1162.7598 |  | 2
75 | 75 | 59 | 38.63 | 104300 | 104300 | 6.75 | 3100 | 706.4078 |  | 2
75 | 75 | 59 | 38.63 | 105500 | 105500 | 6.78 | 3400 | 850.1899 |  | 2
75 | 75 | 59 | 38.63 | 107600 | 107600 | 6.81 | 3825 | 1162.7598 |  | 2
75 | 70 | 63 | 68.69 | 105700 | 61306 | 6.75 | 3100 | 720.9944 |  | 2
75 | 70 | 63 | 68.69 | 106900 | 65209 | 6.78 | 3400 | 866.8603 |  | 2
75 | 70 | 63 | 68.69 | 109000 | 68670 | 6.81 | 3825 | 1162.7598 |  | 2
75 | 75 | 63 | 52.11 | 105700 | 75047 | 6.75 | 3100 | 720.9944 |  | 2
75 | 75 | 63 | 52.11 | 107000 | 79180 | 6.77 | 3400 | 866.8603 |  | 2
75 | 75 | 63 | 52.11 | 109100 | 81825 | 6.8 | 3825 | 1162.7598 |  | 2
75 | 70 | 67 | 86.02 | 108800 | 48960 | 6.74 | 3100 | 720.9944 |  | 2
75 | 70 | 67 | 86.02 | 110000 | 52800 | 6.76 | 3400 | 866.8603 |  | 2
75 | 70 | 67 | 86.02 | 112100 | 54929 | 6.79 | 3825 | 1162.7598 |  | 2
75 | 75 | 67 | 66.75 | 108800 | 63104 | 6.74 | 3100 | 720.9944 |  | 2
75 | 75 | 67 | 66.75 | 110100 | 66060 | 6.76 | 3400 | 866.8603 |  | 2
75 | 75 | 67 | 66.75 | 112200 | 69564 | 6.79 | 3825 | 1162.7598 |  | 2
75 | 75 | 71 | 82.67 | 113600 | 45440 | 6.8 | 3100 | 720.9944 |  | 2
75 | 75 | 71 | 82.67 | 114800 | 57400 | 6.8 | 3400 | 866.8603 |  | 2
75 | 75 | 71 | 82.67 | 116900 | 58450 | 6.8 | 3825 | 1162.7598 |  | 2
85 | 70 | 59 | 52.72 | 101500 | 69020 | 7.53 | 3100 | 706.4078 |  | 2
85 | 70 | 59 | 52.72 | 102700 | 72917 | 7.56 | 3400 | 850.1899 |  | 2
85 | 70 | 59 | 52.72 | 104800 | 104800 | 7.59 | 3825 | 1148.1732 |  | 2
85 | 75 | 59 | 38.63 | 101600 | 101600 | 7.53 | 3100 | 706.4078 |  | 2
85 | 75 | 59 | 38.63 | 102800 | 102800 | 7.55 | 3400 | 850.1899 |  | 2
85 | 75 | 59 | 38.63 | 104900 | 104900 | 7.58 | 3825 | 1148.1732 |  | 2
85 | 70 | 63 | 68.69 | 103000 | 62830 | 7.53 | 3100 | 706.4078 |  | 2
85 | 70 | 63 | 68.69 | 104200 | 65646 | 7.55 | 3400 | 850.1899 |  | 2
85 | 70 | 63 | 68.69 | 106300 | 69095 | 7.58 | 3825 | 1162.7598 |  | 2
85 | 75 | 63 | 52.11 | 103000 | 75190 | 7.52 | 3100 | 706.4078 |  | 2
85 | 75 | 63 | 52.11 | 104300 | 79268 | 7.55 | 3400 | 850.1899 |  | 2
85 | 75 | 63 | 52.11 | 106400 | 82992 | 7.58 | 3825 | 1162.7598 |  | 2
85 | 70 | 67 | 86.02 | 106100 | 49867 | 7.52 | 3100 | 720.9944 |  | 2
85 | 70 | 67 | 86.02 | 107300 | 53650 | 7.54 | 3400 | 866.8603 |  | 2
85 | 70 | 67 | 86.02 | 109400 | 56888 | 7.57 | 3825 | 1162.7598 |  | 2
85 | 75 | 67 | 66.75 | 106100 | 63660 | 7.51 | 3100 | 720.9944 |  | 2
85 | 75 | 67 | 66.75 | 107400 | 67662 | 7.54 | 3400 | 866.8603 |  | 2
85 | 75 | 67 | 66.75 | 109500 | 70080 | 7.57 | 3825 | 1162.7598 |  | 2
85 | 75 | 71 | 82.67 | 110900 | 55450 | 7.6 | 3100 | 720.9944 |  | 2
85 | 75 | 71 | 82.67 | 112100 | 56050 | 7.6 | 3400 | 866.8603 |  | 2
85 | 75 | 71 | 82.67 | 114200 | 57100 | 7.6 | 3825 | 1162.7598 |  | 2
95 | 70 | 59 | 52.72 | 96800 | 96800 | 8.37 | 3100 | 706.4078 |  | 2
95 | 70 | 59 | 52.72 | 98100 | 98100 | 8.4 | 3400 | 850.1899 |  | 2
95 | 70 | 59 | 52.72 | 100200 | 100200 | 8.43 | 3825 | 1148.1732 |  | 2
95 | 75 | 59 | 38.63 | 96900 | 96900 | 8.37 | 3100 | 706.4078 |  | 2
95 | 75 | 59 | 38.63 | 98100 | 98100 | 8.39 | 3400 | 850.1899 |  | 2
95 | 75 | 59 | 38.63 | 100200 | 100200 | 8.42 | 3825 | 1148.1732 |  | 2
95 | 70 | 63 | 68.69 | 98300 | 61929 | 8.37 | 3100 | 706.4078 |  | 2
95 | 70 | 63 | 68.69 | 99500 | 64675 | 8.39 | 3400 | 850.1899 |  | 2
95 | 70 | 63 | 68.69 | 101600 | 68072 | 8.42 | 3825 | 1148.1732 |  | 2
95 | 75 | 63 | 52.11 | 98400 | 73800 | 8.36 | 3100 | 706.4078 |  | 2
95 | 75 | 63 | 52.11 | 99600 | 77688 | 8.39 | 3400 | 850.1899 |  | 2
95 | 75 | 63 | 52.11 | 101700 | 81360 | 8.42 | 3825 | 1148.1732 |  | 2
95 | 70 | 67 | 86.02 | 101400 | 49686 | 8.36 | 3100 | 706.4078 |  | 2
95 | 70 | 67 | 86.02 | 102600 | 53352 | 8.38 | 3400 | 850.1899 |  | 2
95 | 70 | 67 | 86.02 | 104700 | 56538 | 8.41 | 3825 | 1148.1732 |  | 2
95 | 75 | 67 | 66.75 | 101500 | 62930 | 8.35 | 3100 | 706.4078 |  | 2
95 | 75 | 67 | 66.75 | 102700 | 66755 | 8.38 | 3400 | 850.1899 |  | 2
95 | 75 | 67 | 66.75 | 104800 | 69168 | 8.41 | 3825 | 1148.1732 |  | 2
95 | 75 | 71 | 82.67 | 106200 | 53100 | 8.4 | 3100 | 720.9944 |  | 2
95 | 75 | 71 | 82.67 | 107400 | 53700 | 8.4 | 3400 | 866.8603 |  | 2
95 | 75 | 71 | 82.67 | 109500 | 54750 | 8.5 | 3825 | 1162.7598 |  | 2
105 | 70 | 59 | 52.72 | 91100 | 91100 | 9.31 | 3100 | 706.4078 |  | 2
105 | 70 | 59 | 52.72 | 92400 | 92400 | 9.34 | 3400 | 850.1899 |  | 2
105 | 70 | 59 | 52.72 | 94500 | 94500 | 9.37 | 3825 | 1148.1732 |  | 2
105 | 75 | 59 | 38.63 | 91200 | 91200 | 9.31 | 3100 | 706.4078 |  | 2
105 | 75 | 59 | 38.63 | 92400 | 92400 | 9.33 | 3400 | 850.1899 |  | 2
105 | 75 | 59 | 38.63 | 94500 | 94500 | 9.36 | 3825 | 1148.1732 |  | 2
105 | 70 | 63 | 68.69 | 92600 | 60190 | 9.31 | 3100 | 706.4078 |  | 2
105 | 70 | 63 | 68.69 | 93800 | 62846 | 9.33 | 3400 | 850.1899 |  | 2
105 | 70 | 63 | 68.69 | 95900 | 66171 | 9.36 | 3825 | 1148.1732 |  | 2
105 | 75 | 63 | 52.11 | 92700 | 71379 | 9.3 | 3100 | 706.4078 |  | 2
105 | 75 | 63 | 52.11 | 93900 | 75120 | 9.33 | 3400 | 850.1899 |  | 2
105 | 75 | 63 | 52.11 | 96000 | 96000 | 9.36 | 3825 | 1148.1732 |  | 2
105 | 70 | 67 | 86.02 | 95700 | 48807 | 9.29 | 3100 | 706.4078 |  | 2
105 | 70 | 67 | 86.02 | 96900 | 52326 | 9.32 | 3400 | 850.1899 |  | 2
105 | 70 | 67 | 86.02 | 99000 | 55440 | 9.35 | 3825 | 1148.1732 |  | 2
105 | 75 | 67 | 66.75 | 95800 | 61312 | 9.29 | 3100 | 706.4078 |  | 2
105 | 75 | 67 | 66.75 | 97000 | 64990 | 9.31 | 3400 | 850.1899 |  | 2
105 | 75 | 67 | 66.75 | 99100 | 67388 | 9.34 | 3825 | 1148.1732 |  | 2
105 | 75 | 71 | 82.67 | 100500 | 50250 | 9.3 | 3100 | 706.4078 |  | 2
105 | 75 | 71 | 82.67 | 101700 | 50850 | 9.4 | 3400 | 850.1899 |  | 2
105 | 75 | 71 | 82.67 | 103800 | 51900 | 9.4 | 3825 | 1148.1732 |  | 2
115 | 70 | 59 | 52.72 | 85900 | 85900 | 10.41 | 3100 | 706.4078 |  | 2
115 | 70 | 59 | 52.72 | 87200 | 87200 | 10.44 | 3400 | 850.1899 |  | 2
115 | 70 | 59 | 52.72 | 89300 | 89300 | 10.47 | 3825 | 1148.1732 |  | 2
115 | 75 | 59 | 38.63 | 86000 | 86000 | 10.41 | 3100 | 706.4078 |  | 2
115 | 75 | 59 | 38.63 | 87200 | 87200 | 10.43 | 3400 | 850.1899 |  | 2
115 | 75 | 59 | 38.63 | 89300 | 89300 | 10.46 | 3825 | 1148.1732 |  | 2
115 | 70 | 63 | 68.69 | 87400 | 61180 | 10.41 | 3100 | 706.4078 |  | 2
115 | 70 | 63 | 68.69 | 88600 | 63792 | 10.43 | 3400 | 850.1899 |  | 2
115 | 70 | 63 | 68.69 | 90700 | 90700 | 10.46 | 3825 | 1148.1732 |  | 2
115 | 75 | 63 | 52.11 | 87500 | 87500 | 10.4 | 3100 | 706.4078 |  | 2
115 | 75 | 63 | 52.11 | 88700 | 88700 | 10.43 | 3400 | 850.1899 |  | 2
115 | 75 | 63 | 52.11 | 90800 | 90800 | 10.46 | 3825 | 1148.1732 |  | 2
115 | 70 | 67 | 86.02 | 90500 | 50680 | 10.4 | 3100 | 706.4078 |  | 2
115 | 70 | 67 | 86.02 | 91700 | 54103 | 10.42 | 3400 | 850.1899 |  | 2
115 | 70 | 67 | 86.02 | 93800 | 57218 | 10.45 | 3825 | 1148.1732 |  | 2
115 | 75 | 67 | 66.75 | 90600 | 62514 | 10.39 | 3100 | 706.4078 |  | 2
115 | 75 | 67 | 66.75 | 91800 | 66096 | 10.41 | 3400 | 850.1899 |  | 2
115 | 75 | 67 | 66.75 | 93900 | 68547 | 10.44 | 3825 | 1148.1732 |  | 2
115 | 75 | 71 | 82.67 | 95300 | 57180 | 10.4 | 3100 | 706.4078 |  | 2
115 | 75 | 71 | 82.67 | 96500 | 57900 | 10.5 | 3400 | 850.1899 |  | 2
115 | 75 | 71 | 82.67 | 98600 | 59160 | 10.5 | 3825 | 1148.1732 |  | 2
65 | 80 | 59 | 27.74 | 105700 | 105700 | 6.06 | 3100 | 720.9944 |  | 2
65 | 80 | 59 | 27.74 | 107000 | 107000 | 6.09 | 3400 | 866.8603 |  | 2
65 | 80 | 59 | 27.74 | 109100 | 109100 | 6.12 | 3825 | 1162.7598 |  | 2
65 | 85 | 59 | 19.34 | 107500 | 107500 | 6.08 | 3100 | 720.9944 |  | 2
65 | 85 | 59 | 19.34 | 108700 | 108700 | 6.1 | 3400 | 866.8603 |  | 2
65 | 85 | 59 | 19.34 | 110800 | 110800 | 6.13 | 3825 | 1162.7598 |  | 2
65 | 80 | 63 | 39.17 | 107200 | 87904 | 6.06 | 3100 | 720.9944 |  | 2
65 | 80 | 63 | 39.17 | 108400 | 92140 | 6.08 | 3400 | 866.8603 |  | 2
65 | 80 | 63 | 39.17 | 110500 | 96135 | 6.11 | 3825 | 1162.7598 |  | 2
65 | 85 | 63 | 29.06 | 108900 | 100188 | 6.07 | 3100 | 720.9944 |  | 2
65 | 85 | 63 | 29.06 | 110200 | 104690 | 6.09 | 3400 | 866.8603 |  | 2
65 | 85 | 63 | 29.06 | 112300 | 108931 | 6.12 | 3825 | 1162.7598 |  | 2
65 | 80 | 67 | 51.57 | 110300 | 76107 | 6.04 | 3100 | 720.9944 |  | 2
65 | 80 | 67 | 51.57 | 111500 | 80280 | 6.07 | 3400 | 866.8603 |  | 2
65 | 80 | 67 | 51.57 | 113600 | 84064 | 6.1 | 3825 | 1162.7598 |  | 2
65 | 85 | 67 | 39.6 | 112000 | 88480 | 6.06 | 3100 | 720.9944 |  | 2
65 | 85 | 67 | 39.6 | 113300 | 92906 | 6.08 | 3400 | 866.8603 |  | 2
65 | 85 | 67 | 39.6 | 115400 | 95782 | 6.11 | 3825 | 1162.7598 |  | 2
65 | 80 | 71 | 65.06 | 115000 | 69000 | 6.1 | 3100 | 720.9944 |  | 2
65 | 80 | 71 | 65.06 | 116300 | 69780 | 6.1 | 3400 | 866.8603 |  | 2
65 | 80 | 71 | 65.06 | 118400 | 71040 | 6.2 | 3825 | 1162.7598 |  | 2
65 | 85 | 71 | 51.08 | 116800 | 81760 | 6.1 | 3100 | 720.9944 |  | 2
65 | 85 | 71 | 51.08 | 118000 | 82600 | 6.1 | 3400 | 866.8603 |  | 2
65 | 85 | 71 | 51.08 | 120100 | 84070 | 6.2 | 3825 | 1162.7598 |  | 2
75 | 80 | 59 | 27.74 | 104800 | 104800 | 6.76 | 3100 | 706.4078 |  | 2
75 | 80 | 59 | 27.74 | 106000 | 106000 | 6.78 | 3400 | 866.8603 |  | 2
75 | 80 | 59 | 27.74 | 108100 | 108100 | 6.81 | 3825 | 1162.7598 |  | 2
75 | 85 | 59 | 19.34 | 106600 | 106600 | 6.77 | 3100 | 720.9944 |  | 2
75 | 85 | 59 | 19.34 | 107800 | 107800 | 6.79 | 3400 | 866.8603 |  | 2
75 | 85 | 59 | 19.34 | 109900 | 109900 | 6.82 | 3825 | 1162.7598 |  | 2
75 | 80 | 63 | 39.17 | 106300 | 88229 | 6.75 | 3100 | 720.9944 |  | 2
75 | 80 | 63 | 39.17 | 107500 | 92450 | 6.78 | 3400 | 866.8603 |  | 2
75 | 80 | 63 | 39.17 | 109600 | 95352 | 6.81 | 3825 | 1162.7598 |  | 2
75 | 85 | 63 | 29.06 | 108000 | 108000 | 6.76 | 3100 | 720.9944 |  | 2
75 | 85 | 63 | 29.06 | 109300 | 109300 | 6.79 | 3400 | 866.8603 |  | 2
75 | 85 | 63 | 29.06 | 111300 | 111300 | 6.82 | 3825 | 1162.7598 |  | 2
75 | 80 | 67 | 51.57 | 109400 | 76580 | 6.74 | 3100 | 720.9944 |  | 2
75 | 80 | 67 | 51.57 | 110600 | 80738 | 6.76 | 3400 | 866.8603 |  | 2
75 | 80 | 67 | 51.57 | 112700 | 83398 | 6.79 | 3825 | 1162.7598 |  | 2
75 | 85 | 67 | 39.6 | 111100 | 88880 | 6.75 | 3100 | 720.9944 |  | 2
75 | 85 | 67 | 39.6 | 112400 | 92168 | 6.78 | 3400 | 866.8603 |  | 2
75 | 85 | 67 | 39.6 | 114400 | 96096 | 6.81 | 3825 | 1162.7598 |  | 2
75 | 80 | 71 | 65.06 | 114100 | 68460 | 6.8 | 3100 | 720.9944 |  | 2
75 | 80 | 71 | 65.06 | 115300 | 69180 | 6.8 | 3400 | 866.8603 |  | 2
75 | 80 | 71 | 65.06 | 117400 | 70440 | 6.8 | 3825 | 1162.7598 |  | 2
75 | 85 | 71 | 51.08 | 115900 | 81130 | 6.8 | 3100 | 720.9944 |  | 2
75 | 85 | 71 | 51.08 | 117100 | 81970 | 6.8 | 3400 | 866.8603 |  | 2
75 | 85 | 71 | 51.08 | 119200 | 83440 | 6.9 | 3825 | 1162.7598 |  | 2
85 | 80 | 59 | 27.74 | 102100 | 102100 | 7.53 | 3100 | 706.4078 |  | 2
85 | 80 | 59 | 27.74 | 103300 | 103300 | 7.56 | 3400 | 850.1899 |  | 2
85 | 80 | 59 | 27.74 | 105400 | 105400 | 7.59 | 3825 | 1148.1732 |  | 2
85 | 85 | 59 | 19.34 | 103800 | 103800 | 7.55 | 3100 | 706.4078 |  | 2
85 | 85 | 59 | 19.34 | 105100 | 105100 | 7.57 | 3400 | 850.1899 |  | 2
85 | 85 | 59 | 19.34 | 107200 | 107200 | 7.6 | 3825 | 1162.7598 |  | 2
85 | 80 | 63 | 39.17 | 103600 | 88060 | 7.53 | 3100 | 706.4078 |  | 2
85 | 80 | 63 | 39.17 | 104800 | 92224 | 7.55 | 3400 | 850.1899 |  | 2
85 | 80 | 63 | 39.17 | 106900 | 106900 | 7.58 | 3825 | 1162.7598 |  | 2
85 | 85 | 63 | 29.06 | 105300 | 105300 | 7.54 | 3100 | 706.4078 |  | 2
85 | 85 | 63 | 29.06 | 106600 | 106600 | 7.56 | 3400 | 866.8603 |  | 2
85 | 85 | 63 | 29.06 | 108600 | 108600 | 7.59 | 3825 | 1162.7598 |  | 2
85 | 80 | 67 | 51.57 | 106700 | 76824 | 7.52 | 3100 | 720.9944 |  | 2
85 | 80 | 67 | 51.57 | 107900 | 80925 | 7.54 | 3400 | 866.8603 |  | 2
85 | 80 | 67 | 51.57 | 110000 | 84700 | 7.57 | 3825 | 1162.7598 |  | 2
85 | 85 | 67 | 39.6 | 108400 | 88888 | 7.53 | 3100 | 720.9944 |  | 2
85 | 85 | 67 | 39.6 | 109700 | 93245 | 7.55 | 3400 | 866.8603 |  | 2
85 | 85 | 67 | 39.6 | 111700 | 96062 | 7.58 | 3825 | 1162.7598 |  | 2
85 | 80 | 71 | 65.06 | 111400 | 66840 | 7.6 | 3100 | 720.9944 |  | 2
85 | 80 | 71 | 65.06 | 112600 | 67560 | 7.6 | 3400 | 866.8603 |  | 2
85 | 80 | 71 | 65.06 | 114700 | 68820 | 7.6 | 3825 | 1162.7598 |  | 2
85 | 85 | 71 | 51.08 | 113100 | 79170 | 7.6 | 3100 | 720.9944 |  | 2
85 | 85 | 71 | 51.08 | 114400 | 80080 | 7.6 | 3400 | 866.8603 |  | 2
85 | 85 | 71 | 51.08 | 116500 | 81550 | 7.6 | 3825 | 1162.7598 |  | 2
95 | 80 | 59 | 27.74 | 97400 | 97400 | 8.37 | 3100 | 706.4078 |  | 2
95 | 80 | 59 | 27.74 | 98700 | 98700 | 8.4 | 3400 | 850.1899 |  | 2
95 | 80 | 59 | 27.74 | 100800 | 100800 | 8.43 | 3825 | 1148.1732 |  | 2
95 | 85 | 59 | 19.34 | 99200 | 99200 | 8.39 | 3100 | 706.4078 |  | 2
95 | 85 | 59 | 19.34 | 100400 | 100400 | 8.41 | 3400 | 850.1899 |  | 2
95 | 85 | 59 | 19.34 | 102500 | 102500 | 8.44 | 3825 | 1148.1732 |  | 2
95 | 80 | 63 | 39.17 | 98900 | 98900 | 8.37 | 3100 | 706.4078 |  | 2
95 | 80 | 63 | 39.17 | 100100 | 100100 | 8.39 | 3400 | 850.1899 |  | 2
95 | 80 | 63 | 39.17 | 102200 | 102200 | 8.42 | 3825 | 1148.1732 |  | 2
95 | 85 | 63 | 29.06 | 100600 | 100600 | 8.38 | 3100 | 706.4078 |  | 2
95 | 85 | 63 | 29.06 | 101900 | 101900 | 8.4 | 3400 | 850.1899 |  | 2
95 | 85 | 63 | 29.06 | 104000 | 104000 | 8.43 | 3825 | 1148.1732 |  | 2
95 | 80 | 67 | 51.57 | 102000 | 75480 | 8.36 | 3100 | 706.4078 |  | 2
95 | 80 | 67 | 51.57 | 103200 | 79464 | 8.38 | 3400 | 850.1899 |  | 2
95 | 80 | 67 | 51.57 | 105300 | 83187 | 8.41 | 3825 | 1148.1732 |  | 2
95 | 85 | 67 | 39.6 | 103700 | 87108 | 8.37 | 3100 | 706.4078 |  | 2
95 | 85 | 67 | 39.6 | 105000 | 91350 | 8.39 | 3400 | 850.1899 |  | 2
95 | 85 | 67 | 39.6 | 107100 | 94248 | 8.42 | 3825 | 1162.7598 |  | 2
95 | 80 | 71 | 65.06 | 106700 | 64020 | 8.4 | 3100 | 706.4078 |  | 2
95 | 80 | 71 | 65.06 | 108000 | 64800 | 8.4 | 3400 | 850.1899 |  | 2
95 | 80 | 71 | 65.06 | 110100 | 66060 | 8.5 | 3825 | 1162.7598 |  | 2
95 | 85 | 71 | 51.08 | 108500 | 75950 | 8.4 | 3100 | 706.4078 |  | 2
95 | 85 | 71 | 51.08 | 109700 | 76790 | 8.4 | 3400 | 850.1899 |  | 2
95 | 85 | 71 | 51.08 | 111800 | 78260 | 8.5 | 3825 | 1162.7598 |  | 2
105 | 80 | 59 | 27.74 | 91700 | 91700 | 9.31 | 3100 | 706.4078 |  | 2
105 | 80 | 59 | 27.74 | 93000 | 93000 | 9.33 | 3400 | 850.1899 |  | 2
105 | 80 | 59 | 27.74 | 95100 | 95100 | 9.36 | 3825 | 1148.1732 |  | 2
105 | 85 | 59 | 19.34 | 93500 | 93500 | 9.32 | 3100 | 706.4078 |  | 2
105 | 85 | 59 | 19.34 | 94700 | 94700 | 9.35 | 3400 | 850.1899 |  | 2
105 | 85 | 59 | 19.34 | 96800 | 96800 | 9.38 | 3825 | 1148.1732 |  | 2
105 | 80 | 63 | 39.17 | 93200 | 93200 | 9.31 | 3100 | 706.4078 |  | 2
105 | 80 | 63 | 39.17 | 94400 | 94400 | 9.33 | 3400 | 850.1899 |  | 2
105 | 80 | 63 | 39.17 | 96500 | 96500 | 9.36 | 3825 | 1148.1732 |  | 2
105 | 85 | 63 | 29.06 | 95000 | 95000 | 9.32 | 3100 | 706.4078 |  | 2
105 | 85 | 63 | 29.06 | 96200 | 96200 | 9.34 | 3400 | 850.1899 |  | 2
105 | 85 | 63 | 29.06 | 98300 | 98300 | 9.37 | 3825 | 1148.1732 |  | 2
105 | 80 | 67 | 51.57 | 96300 | 73188 | 9.29 | 3100 | 706.4078 |  | 2
105 | 80 | 67 | 51.57 | 97500 | 77025 | 9.32 | 3400 | 850.1899 |  | 2
105 | 80 | 67 | 51.57 | 99600 | 80676 | 9.35 | 3825 | 1148.1732 |  | 2
105 | 85 | 67 | 39.6 | 98100 | 84366 | 9.31 | 3100 | 706.4078 |  | 2
105 | 85 | 67 | 39.6 | 99300 | 99300 | 9.33 | 3400 | 850.1899 |  | 2
105 | 85 | 67 | 39.6 | 101400 | 101400 | 9.36 | 3825 | 1148.1732 |  | 2
105 | 80 | 71 | 65.06 | 101000 | 60600 | 9.3 | 3100 | 706.4078 |  | 2
105 | 80 | 71 | 65.06 | 102300 | 71610 | 9.4 | 3400 | 850.1899 |  | 2
105 | 80 | 71 | 65.06 | 104400 | 73080 | 9.4 | 3825 | 1148.1732 |  | 2
105 | 85 | 71 | 51.08 | 102800 | 71960 | 9.4 | 3100 | 706.4078 |  | 2
105 | 85 | 71 | 51.08 | 104000 | 72800 | 9.4 | 3400 | 850.1899 |  | 2
105 | 85 | 71 | 51.08 | 106100 | 84880 | 9.4 | 3825 | 1162.7598 |  | 2
115 | 80 | 59 | 27.74 | 86500 | 86500 | 10.41 | 3100 | 706.4078 |  | 2
115 | 80 | 59 | 27.74 | 87800 | 87800 | 10.44 | 3400 | 850.1899 |  | 2
115 | 80 | 59 | 27.74 | 89900 | 89900 | 10.47 | 3825 | 1148.1732 |  | 2
115 | 85 | 59 | 19.34 | 88300 | 88300 | 10.43 | 3100 | 706.4078 |  | 2
115 | 85 | 59 | 19.34 | 89500 | 89500 | 10.45 | 3400 | 850.1899 |  | 2
115 | 85 | 59 | 19.34 | 91600 | 91600 | 10.48 | 3825 | 1148.1732 |  | 2
115 | 80 | 63 | 39.17 | 88000 | 88000 | 10.41 | 3100 | 706.4078 |  | 2
115 | 80 | 63 | 39.17 | 89200 | 89200 | 10.43 | 3400 | 850.1899 |  | 2
115 | 80 | 63 | 39.17 | 91300 | 91300 | 10.46 | 3825 | 1148.1732 |  | 2
115 | 85 | 63 | 29.06 | 89700 | 89700 | 10.42 | 3100 | 706.4078 |  | 2
115 | 85 | 63 | 29.06 | 91000 | 91000 | 10.44 | 3400 | 850.1899 |  | 2
115 | 85 | 63 | 29.06 | 93100 | 93100 | 10.47 | 3825 | 1148.1732 |  | 2
115 | 80 | 67 | 51.57 | 91100 | 73791 | 10.39 | 3100 | 706.4078 |  | 2
115 | 80 | 67 | 51.57 | 92300 | 77532 | 10.42 | 3400 | 850.1899 |  | 2
115 | 80 | 67 | 51.57 | 94400 | 94400 | 10.45 | 3825 | 1148.1732 |  | 2
115 | 85 | 67 | 39.6 | 92800 | 92800 | 10.41 | 3100 | 706.4078 |  | 2
115 | 85 | 67 | 39.6 | 94100 | 94100 | 10.43 | 3400 | 850.1899 |  | 2
115 | 85 | 67 | 39.6 | 96200 | 96200 | 10.46 | 3825 | 1148.1732 |  | 2
115 | 80 | 71 | 65.06 | 95800 | 67060 | 10.4 | 3100 | 706.4078 |  | 2
115 | 80 | 71 | 65.06 | 97100 | 67970 | 10.5 | 3400 | 850.1899 |  | 2
115 | 80 | 71 | 65.06 | 99200 | 69440 | 10.5 | 3825 | 1148.1732 |  | 2
115 | 85 | 71 | 51.08 | 97600 | 78080 | 10.5 | 3100 | 706.4078 |  | 2
115 | 85 | 71 | 51.08 | 98800 | 79040 | 10.5 | 3400 | 850.1899 |  | 2
115 | 85 | 71 | 51.08 | 100900 | 80720 | 10.5 | 3825 | 1148.1732 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 4
Degradation Coefficient (C_d)
IEER or SEER | 17
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 70 | 59 | 52.72 | 118500 | 74655 | 6.8 | 3550 | 841.8547 |  | 2
65 | 70 | 59 | 52.72 | 120400 | 79464 | 6.84 | 4000 | 1200.2682 |  | 2
65 | 70 | 59 | 52.72 | 122900 | 82343 | 6.87 | 4500 | 1341.9665 |  | 2
65 | 75 | 59 | 38.63 | 118600 | 88950 | 6.8 | 3550 | 841.8547 |  | 2
65 | 75 | 59 | 38.63 | 120500 | 93990 | 6.83 | 4000 | 1200.2682 |  | 2
65 | 75 | 59 | 38.63 | 123000 | 97170 | 6.87 | 4500 | 1341.9665 |  | 2
65 | 70 | 63 | 68.69 | 120200 | 67312 | 6.79 | 3550 | 841.8547 |  | 2
65 | 70 | 63 | 68.69 | 122100 | 72039 | 6.83 | 4000 | 1200.2682 |  | 2
65 | 70 | 63 | 68.69 | 124600 | 74760 | 6.87 | 4500 | 1341.9665 |  | 2
65 | 75 | 63 | 52.11 | 120300 | 81804 | 6.79 | 3550 | 841.8547 |  | 2
65 | 75 | 63 | 52.11 | 122100 | 86691 | 6.83 | 4000 | 1200.2682 |  | 2
65 | 75 | 63 | 52.11 | 124700 | 89784 | 6.86 | 4500 | 1341.9665 |  | 2
65 | 70 | 67 | 86.02 | 123700 | 53191 | 6.78 | 3550 | 841.8547 |  | 2
65 | 70 | 67 | 86.02 | 125600 | 57776 | 6.82 | 4000 | 1200.2682 |  | 2
65 | 70 | 67 | 86.02 | 128100 | 60207 | 6.85 | 4500 | 1341.9665 |  | 2
65 | 75 | 67 | 66.75 | 123800 | 68090 | 6.78 | 3550 | 841.8547 |  | 2
65 | 75 | 67 | 66.75 | 125600 | 72848 | 6.81 | 4000 | 1200.2682 |  | 2
65 | 75 | 67 | 66.75 | 128200 | 75638 | 6.85 | 4500 | 1341.9665 |  | 2
65 | 75 | 71 | 82.67 | 129100 | 51640 | 6.8 | 3550 | 841.8547 |  | 2
65 | 75 | 71 | 82.67 | 131000 | 52400 | 6.9 | 4000 | 1200.2682 |  | 2
65 | 75 | 71 | 82.67 | 133500 | 66750 | 6.9 | 4500 | 1341.9665 |  | 2
75 | 70 | 59 | 52.72 | 117500 | 74025 | 7.62 | 3550 | 841.8547 |  | 2
75 | 70 | 59 | 52.72 | 119400 | 79998 | 7.66 | 4000 | 1200.2682 |  | 2
75 | 70 | 59 | 52.72 | 121900 | 82892 | 7.69 | 4500 | 1341.9665 |  | 2
75 | 75 | 59 | 38.63 | 117600 | 89376 | 7.61 | 3550 | 841.8547 |  | 2
75 | 75 | 59 | 38.63 | 119400 | 94326 | 7.65 | 4000 | 1200.2682 |  | 2
75 | 75 | 59 | 38.63 | 122000 | 122000 | 7.69 | 4500 | 1341.9665 |  | 2
75 | 70 | 63 | 68.69 | 119100 | 66696 | 7.61 | 3550 | 841.8547 |  | 2
75 | 70 | 63 | 68.69 | 121000 | 72600 | 7.65 | 4000 | 1200.2682 |  | 2
75 | 70 | 63 | 68.69 | 123600 | 75396 | 7.68 | 4500 | 1341.9665 |  | 2
75 | 75 | 63 | 52.11 | 119200 | 81056 | 7.61 | 3550 | 841.8547 |  | 2
75 | 75 | 63 | 52.11 | 121100 | 87192 | 7.64 | 4000 | 1200.2682 |  | 2
75 | 75 | 63 | 52.11 | 123600 | 90228 | 7.68 | 4500 | 1341.9665 |  | 2
75 | 70 | 67 | 86.02 | 122600 | 52718 | 7.6 | 3550 | 841.8547 |  | 2
75 | 70 | 67 | 86.02 | 124500 | 58515 | 7.64 | 4000 | 1200.2682 |  | 2
75 | 70 | 67 | 86.02 | 127000 | 60960 | 7.67 | 4500 | 1341.9665 |  | 2
75 | 75 | 67 | 66.75 | 122700 | 68712 | 7.59 | 3550 | 841.8547 |  | 2
75 | 75 | 67 | 66.75 | 124600 | 73514 | 7.63 | 4000 | 1200.2682 |  | 2
75 | 75 | 67 | 66.75 | 127100 | 76260 | 7.67 | 4500 | 1341.9665 |  | 2
75 | 75 | 71 | 82.67 | 128000 | 51200 | 7.7 | 3550 | 841.8547 |  | 2
75 | 75 | 71 | 82.67 | 129900 | 64950 | 7.7 | 4000 | 1200.2682 |  | 2
75 | 75 | 71 | 82.67 | 132500 | 66250 | 7.7 | 4500 | 1341.9665 |  | 2
85 | 70 | 59 | 52.72 | 114400 | 75504 | 8.53 | 3550 | 841.8547 |  | 2
85 | 70 | 59 | 52.72 | 116300 | 80247 | 8.57 | 4000 | 1200.2682 |  | 2
85 | 70 | 59 | 52.72 | 118800 | 83160 | 8.6 | 4500 | 1341.9665 |  | 2
85 | 75 | 59 | 38.63 | 114500 | 114500 | 8.53 | 3550 | 841.8547 |  | 2
85 | 75 | 59 | 38.63 | 116400 | 116400 | 8.56 | 4000 | 1200.2682 |  | 2
85 | 75 | 59 | 38.63 | 118900 | 118900 | 8.6 | 4500 | 1341.9665 |  | 2
85 | 70 | 63 | 68.69 | 116100 | 68499 | 8.53 | 3550 | 841.8547 |  | 2
85 | 70 | 63 | 68.69 | 118000 | 73160 | 8.56 | 4000 | 1200.2682 |  | 2
85 | 70 | 63 | 68.69 | 120500 | 75915 | 8.6 | 4500 | 1341.9665 |  | 2
85 | 75 | 63 | 52.11 | 116200 | 82502 | 8.52 | 3550 | 841.8547 |  | 2
85 | 75 | 63 | 52.11 | 118000 | 87320 | 8.56 | 4000 | 1200.2682 |  | 2
85 | 75 | 63 | 52.11 | 120600 | 90450 | 8.59 | 4500 | 1341.9665 |  | 2
85 | 70 | 67 | 86.02 | 119600 | 55016 | 8.51 | 3550 | 841.8547 |  | 2
85 | 70 | 67 | 86.02 | 121500 | 59535 | 8.55 | 4000 | 1200.2682 |  | 2
85 | 70 | 67 | 86.02 | 124000 | 62000 | 8.58 | 4500 | 1341.9665 |  | 2
85 | 75 | 67 | 66.75 | 119600 | 69368 | 8.51 | 3550 | 841.8547 |  | 2
85 | 75 | 67 | 66.75 | 121500 | 74115 | 8.54 | 4000 | 1200.2682 |  | 2
85 | 75 | 67 | 66.75 | 124100 | 76942 | 8.58 | 4500 | 1341.9665 |  | 2
85 | 75 | 71 | 82.67 | 125000 | 50000 | 8.6 | 3550 | 841.8547 |  | 2
85 | 75 | 71 | 82.67 | 126900 | 63450 | 8.6 | 4000 | 1200.2682 |  | 2
85 | 75 | 71 | 82.67 | 129400 | 64700 | 8.6 | 4500 | 1341.9665 |  | 2
95 | 70 | 59 | 52.72 | 109200 | 74256 | 9.52 | 3550 | 841.8547 |  | 2
95 | 70 | 59 | 52.72 | 111100 | 111100 | 9.56 | 4000 | 1200.2682 |  | 2
95 | 70 | 59 | 52.72 | 113600 | 113600 | 9.59 | 4500 | 1341.9665 |  | 2
95 | 75 | 59 | 38.63 | 109200 | 109200 | 9.52 | 3550 | 841.8547 |  | 2
95 | 75 | 59 | 38.63 | 111100 | 111100 | 9.55 | 4000 | 1200.2682 |  | 2
95 | 75 | 59 | 38.63 | 113700 | 113700 | 9.59 | 4500 | 1341.9665 |  | 2
95 | 70 | 63 | 68.69 | 110800 | 66480 | 9.52 | 3550 | 841.8547 |  | 2
95 | 70 | 63 | 68.69 | 112700 | 72128 | 9.55 | 4000 | 1200.2682 |  | 2
95 | 70 | 63 | 68.69 | 115200 | 74880 | 9.59 | 4500 | 1341.9665 |  | 2
95 | 75 | 63 | 52.11 | 110900 | 80957 | 9.51 | 3550 | 841.8547 |  | 2
95 | 75 | 63 | 52.11 | 112800 | 85728 | 9.55 | 4000 | 1200.2682 |  | 2
95 | 75 | 63 | 52.11 | 115300 | 88781 | 9.58 | 4500 | 1341.9665 |  | 2
95 | 70 | 67 | 86.02 | 114300 | 54864 | 9.5 | 3550 | 841.8547 |  | 2
95 | 70 | 67 | 86.02 | 116200 | 59262 | 9.54 | 4000 | 1200.2682 |  | 2
95 | 70 | 67 | 86.02 | 118700 | 61724 | 9.57 | 4500 | 1341.9665 |  | 2
95 | 75 | 67 | 66.75 | 114400 | 68640 | 9.5 | 3550 | 841.8547 |  | 2
95 | 75 | 67 | 66.75 | 116300 | 73269 | 9.53 | 4000 | 1200.2682 |  | 2
95 | 75 | 67 | 66.75 | 118800 | 76032 | 9.57 | 4500 | 1341.9665 |  | 2
95 | 75 | 71 | 82.67 | 119700 | 59850 | 9.6 | 3550 | 841.8547 |  | 2
95 | 75 | 71 | 82.67 | 121600 | 60800 | 9.6 | 4000 | 1200.2682 |  | 2
95 | 75 | 71 | 82.67 | 124100 | 62050 | 9.6 | 4500 | 1341.9665 |  | 2
105 | 70 | 59 | 52.72 | 102800 | 102800 | 10.63 | 3550 | 825.1844 |  | 2
105 | 70 | 59 | 52.72 | 104600 | 104600 | 10.66 | 4000 | 1179.4302 |  | 2
105 | 70 | 59 | 52.72 | 107200 | 107200 | 10.7 | 4500 | 1321.1285 |  | 2
105 | 75 | 59 | 38.63 | 102800 | 102800 | 10.62 | 3550 | 825.1844 |  | 2
105 | 75 | 59 | 38.63 | 104700 | 104700 | 10.66 | 4000 | 1179.4302 |  | 2
105 | 75 | 59 | 38.63 | 107200 | 107200 | 10.69 | 4500 | 1321.1285 |  | 2
105 | 70 | 63 | 68.69 | 104400 | 65772 | 10.62 | 3550 | 825.1844 |  | 2
105 | 70 | 63 | 68.69 | 106300 | 70158 | 10.66 | 4000 | 1200.2682 |  | 2
105 | 70 | 63 | 68.69 | 108800 | 72896 | 10.69 | 4500 | 1341.9665 |  | 2
105 | 75 | 63 | 52.11 | 104500 | 78375 | 10.61 | 3550 | 825.1844 |  | 2
105 | 75 | 63 | 52.11 | 106300 | 82914 | 10.65 | 4000 | 1200.2682 |  | 2
105 | 75 | 63 | 52.11 | 108900 | 86031 | 10.69 | 4500 | 1341.9665 |  | 2
105 | 70 | 67 | 86.02 | 107900 | 53950 | 10.61 | 3550 | 841.8547 |  | 2
105 | 70 | 67 | 86.02 | 109800 | 58194 | 10.64 | 4000 | 1200.2682 |  | 2
105 | 70 | 67 | 86.02 | 112300 | 60642 | 10.68 | 4500 | 1341.9665 |  | 2
105 | 75 | 67 | 66.75 | 108000 | 66960 | 10.6 | 3550 | 841.8547 |  | 2
105 | 75 | 67 | 66.75 | 109800 | 71370 | 10.64 | 4000 | 1200.2682 |  | 2
105 | 75 | 67 | 66.75 | 112400 | 74184 | 10.67 | 4500 | 1341.9665 |  | 2
105 | 75 | 71 | 82.67 | 113300 | 56650 | 10.7 | 3550 | 841.8547 |  | 2
105 | 75 | 71 | 82.67 | 115200 | 57600 | 10.7 | 4000 | 1200.2682 |  | 2
105 | 75 | 71 | 82.67 | 117700 | 58850 | 10.7 | 4500 | 1341.9665 |  | 2
115 | 70 | 59 | 52.72 | 96900 | 96900 | 11.92 | 3550 | 825.1844 |  | 2
115 | 70 | 59 | 52.72 | 98800 | 98800 | 11.96 | 4000 | 1179.4302 |  | 2
115 | 70 | 59 | 52.72 | 101300 | 101300 | 11.99 | 4500 | 1321.1285 |  | 2
115 | 75 | 59 | 38.63 | 97000 | 97000 | 11.92 | 3550 | 825.1844 |  | 2
115 | 75 | 59 | 38.63 | 98800 | 98800 | 11.95 | 4000 | 1179.4302 |  | 2
115 | 75 | 59 | 38.63 | 101400 | 101400 | 11.99 | 4500 | 1321.1285 |  | 2
115 | 70 | 63 | 68.69 | 98500 | 65995 | 11.92 | 3550 | 825.1844 |  | 2
115 | 70 | 63 | 68.69 | 100400 | 71284 | 11.95 | 4000 | 1179.4302 |  | 2
115 | 70 | 63 | 68.69 | 103000 | 74160 | 11.99 | 4500 | 1321.1285 |  | 2
115 | 75 | 63 | 52.11 | 98600 | 98600 | 11.91 | 3550 | 825.1844 |  | 2
115 | 75 | 63 | 52.11 | 100500 | 100500 | 11.95 | 4000 | 1179.4302 |  | 2
115 | 75 | 63 | 52.11 | 103000 | 103000 | 11.98 | 4500 | 1321.1285 |  | 2
115 | 70 | 67 | 86.02 | 102000 | 56100 | 11.9 | 3550 | 825.1844 |  | 2
115 | 70 | 67 | 86.02 | 103900 | 60262 | 11.94 | 4000 | 1179.4302 |  | 2
115 | 70 | 67 | 86.02 | 106400 | 62776 | 11.97 | 4500 | 1341.9665 |  | 2
115 | 75 | 67 | 66.75 | 102100 | 68407 | 11.9 | 3550 | 825.1844 |  | 2
115 | 75 | 67 | 66.75 | 104000 | 72800 | 11.93 | 4000 | 1179.4302 |  | 2
115 | 75 | 67 | 66.75 | 106500 | 75615 | 11.97 | 4500 | 1341.9665 |  | 2
115 | 75 | 71 | 82.67 | 107400 | 53700 | 12 | 3550 | 841.8547 |  | 2
115 | 75 | 71 | 82.67 | 109300 | 65580 | 12 | 4000 | 1200.2682 |  | 2
115 | 75 | 71 | 82.67 | 111900 | 67140 | 12 | 4500 | 1341.9665 |  | 2
65 | 80 | 59 | 27.74 | 119200 | 119200 | 6.8 | 3550 | 841.8547 |  | 2
65 | 80 | 59 | 27.74 | 121100 | 121100 | 6.84 | 4000 | 1200.2682 |  | 2
65 | 80 | 59 | 27.74 | 123600 | 123600 | 6.87 | 4500 | 1341.9665 |  | 2
65 | 85 | 59 | 19.34 | 121200 | 121200 | 6.82 | 3550 | 841.8547 |  | 2
65 | 85 | 59 | 19.34 | 123100 | 123100 | 6.85 | 4000 | 1200.2682 |  | 2
65 | 85 | 59 | 19.34 | 125600 | 125600 | 6.89 | 4500 | 1341.9665 |  | 2
65 | 80 | 63 | 39.17 | 120900 | 96720 | 6.79 | 3550 | 841.8547 |  | 2
65 | 80 | 63 | 39.17 | 122700 | 101841 | 6.83 | 4000 | 1200.2682 |  | 2
65 | 80 | 63 | 39.17 | 125300 | 105252 | 6.87 | 4500 | 1341.9665 |  | 2
65 | 85 | 63 | 29.06 | 122800 | 109292 | 6.81 | 3550 | 841.8547 |  | 2
65 | 85 | 63 | 29.06 | 124700 | 115971 | 6.85 | 4000 | 1200.2682 |  | 2
65 | 85 | 63 | 29.06 | 127200 | 119568 | 6.88 | 4500 | 1341.9665 |  | 2
65 | 80 | 67 | 51.57 | 124400 | 83348 | 6.78 | 3550 | 841.8547 |  | 2
65 | 80 | 67 | 51.57 | 126200 | 88340 | 6.82 | 4000 | 1200.2682 |  | 2
65 | 80 | 67 | 51.57 | 128800 | 91448 | 6.85 | 4500 | 1341.9665 |  | 2
65 | 85 | 67 | 39.6 | 126300 | 95988 | 6.8 | 3550 | 841.8547 |  | 2
65 | 85 | 67 | 39.6 | 128200 | 102560 | 6.83 | 4000 | 1200.2682 |  | 2
65 | 85 | 67 | 39.6 | 130700 | 105867 | 6.87 | 4500 | 1341.9665 |  | 2
65 | 80 | 71 | 65.06 | 129700 | 64850 | 6.8 | 3550 | 841.8547 |  | 2
65 | 80 | 71 | 65.06 | 131600 | 78960 | 6.9 | 4000 | 1200.2682 |  | 2
65 | 80 | 71 | 65.06 | 134100 | 80460 | 6.9 | 4500 | 1341.9665 |  | 2
65 | 85 | 71 | 51.08 | 131700 | 79020 | 6.9 | 3550 | 841.8547 |  | 2
65 | 85 | 71 | 51.08 | 133500 | 93450 | 6.9 | 4000 | 1200.2682 |  | 2
65 | 85 | 71 | 51.08 | 136100 | 95270 | 6.9 | 4500 | 1362.8045 |  | 2
75 | 80 | 59 | 27.74 | 118200 | 118200 | 7.62 | 3550 | 841.8547 |  | 2
75 | 80 | 59 | 27.74 | 120000 | 120000 | 7.65 | 4000 | 1200.2682 |  | 2
75 | 80 | 59 | 27.74 | 122600 | 122600 | 7.69 | 4500 | 1341.9665 |  | 2
75 | 85 | 59 | 19.34 | 120100 | 120100 | 7.63 | 3550 | 841.8547 |  | 2
75 | 85 | 59 | 19.34 | 122000 | 122000 | 7.67 | 4000 | 1200.2682 |  | 2
75 | 85 | 59 | 19.34 | 124500 | 124500 | 7.71 | 4500 | 1341.9665 |  | 2
75 | 80 | 63 | 39.17 | 119800 | 95840 | 7.61 | 3550 | 841.8547 |  | 2
75 | 80 | 63 | 39.17 | 121700 | 102228 | 7.65 | 4000 | 1200.2682 |  | 2
75 | 80 | 63 | 39.17 | 124200 | 105570 | 7.68 | 4500 | 1341.9665 |  | 2
75 | 85 | 63 | 29.06 | 121800 | 109620 | 7.63 | 3550 | 841.8547 |  | 2
75 | 85 | 63 | 29.06 | 123700 | 123700 | 7.66 | 4000 | 1200.2682 |  | 2
75 | 85 | 63 | 29.06 | 126200 | 126200 | 7.7 | 4500 | 1341.9665 |  | 2
75 | 80 | 67 | 51.57 | 123300 | 83844 | 7.6 | 3550 | 841.8547 |  | 2
75 | 80 | 67 | 51.57 | 125200 | 88892 | 7.63 | 4000 | 1200.2682 |  | 2
75 | 80 | 67 | 51.57 | 127700 | 91944 | 7.67 | 4500 | 1341.9665 |  | 2
75 | 85 | 67 | 39.6 | 125300 | 96481 | 7.61 | 3550 | 841.8547 |  | 2
75 | 85 | 67 | 39.6 | 127200 | 101760 | 7.65 | 4000 | 1200.2682 |  | 2
75 | 85 | 67 | 39.6 | 129700 | 105057 | 7.69 | 4500 | 1341.9665 |  | 2
75 | 80 | 71 | 65.06 | 128600 | 64300 | 7.7 | 3550 | 841.8547 |  | 2
75 | 80 | 71 | 65.06 | 130500 | 78300 | 7.7 | 4000 | 1200.2682 |  | 2
75 | 80 | 71 | 65.06 | 133100 | 79860 | 7.7 | 4500 | 1341.9665 |  | 2
75 | 85 | 71 | 51.08 | 130600 | 78360 | 7.7 | 3550 | 841.8547 |  | 2
75 | 85 | 71 | 51.08 | 132500 | 92750 | 7.7 | 4000 | 1200.2682 |  | 2
75 | 85 | 71 | 51.08 | 135000 | 94500 | 7.7 | 4500 | 1341.9665 |  | 2
85 | 80 | 59 | 27.74 | 115100 | 115100 | 8.53 | 3550 | 841.8547 |  | 2
85 | 80 | 59 | 27.74 | 117000 | 117000 | 8.57 | 4000 | 1200.2682 |  | 2
85 | 80 | 59 | 27.74 | 119500 | 119500 | 8.6 | 4500 | 1341.9665 |  | 2
85 | 85 | 59 | 19.34 | 117100 | 117100 | 8.55 | 3550 | 841.8547 |  | 2
85 | 85 | 59 | 19.34 | 119000 | 119000 | 8.58 | 4000 | 1200.2682 |  | 2
85 | 85 | 59 | 19.34 | 121500 | 121500 | 8.62 | 4500 | 1341.9665 |  | 2
85 | 80 | 63 | 39.17 | 116800 | 96944 | 8.53 | 3550 | 841.8547 |  | 2
85 | 80 | 63 | 39.17 | 118600 | 101996 | 8.56 | 4000 | 1200.2682 |  | 2
85 | 80 | 63 | 39.17 | 121200 | 105444 | 8.6 | 4500 | 1341.9665 |  | 2
85 | 85 | 63 | 29.06 | 118700 | 118700 | 8.54 | 3550 | 841.8547 |  | 2
85 | 85 | 63 | 29.06 | 120600 | 120600 | 8.58 | 4000 | 1200.2682 |  | 2
85 | 85 | 63 | 29.06 | 123100 | 123100 | 8.61 | 4500 | 1341.9665 |  | 2
85 | 80 | 67 | 51.57 | 120300 | 84210 | 8.51 | 3550 | 841.8547 |  | 2
85 | 80 | 67 | 51.57 | 122100 | 89133 | 8.55 | 4000 | 1200.2682 |  | 2
85 | 80 | 67 | 51.57 | 124700 | 92278 | 8.58 | 4500 | 1341.9665 |  | 2
85 | 85 | 67 | 39.6 | 122200 | 96538 | 8.53 | 3550 | 841.8547 |  | 2
85 | 85 | 67 | 39.6 | 124100 | 103003 | 8.56 | 4000 | 1200.2682 |  | 2
85 | 85 | 67 | 39.6 | 126600 | 106344 | 8.6 | 4500 | 1341.9665 |  | 2
85 | 80 | 71 | 65.06 | 125600 | 75360 | 8.6 | 3550 | 841.8547 |  | 2
85 | 80 | 71 | 65.06 | 127500 | 76500 | 8.6 | 4000 | 1200.2682 |  | 2
85 | 80 | 71 | 65.06 | 130000 | 78000 | 8.6 | 4500 | 1341.9665 |  | 2
85 | 85 | 71 | 51.08 | 127600 | 89320 | 8.6 | 3550 | 841.8547 |  | 2
85 | 85 | 71 | 51.08 | 129400 | 90580 | 8.6 | 4000 | 1200.2682 |  | 2
85 | 85 | 71 | 51.08 | 132000 | 92400 | 8.7 | 4500 | 1341.9665 |  | 2
95 | 80 | 59 | 27.74 | 109900 | 109900 | 9.52 | 3550 | 841.8547 |  | 2
95 | 80 | 59 | 27.74 | 111700 | 111700 | 9.56 | 4000 | 1200.2682 |  | 2
95 | 80 | 59 | 27.74 | 114300 | 114300 | 9.59 | 4500 | 1341.9665 |  | 2
95 | 85 | 59 | 19.34 | 111800 | 111800 | 9.54 | 3550 | 841.8547 |  | 2
95 | 85 | 59 | 19.34 | 113700 | 113700 | 9.57 | 4000 | 1200.2682 |  | 2
95 | 85 | 59 | 19.34 | 116200 | 116200 | 9.61 | 4500 | 1341.9665 |  | 2
95 | 80 | 63 | 39.17 | 111500 | 94775 | 9.51 | 3550 | 841.8547 |  | 2
95 | 80 | 63 | 39.17 | 113400 | 113400 | 9.55 | 4000 | 1200.2682 |  | 2
95 | 80 | 63 | 39.17 | 115900 | 115900 | 9.59 | 4500 | 1341.9665 |  | 2
95 | 85 | 63 | 29.06 | 113500 | 113500 | 9.53 | 3550 | 841.8547 |  | 2
95 | 85 | 63 | 29.06 | 115400 | 115400 | 9.57 | 4000 | 1200.2682 |  | 2
95 | 85 | 63 | 29.06 | 117900 | 117900 | 9.6 | 4500 | 1341.9665 |  | 2
95 | 80 | 67 | 51.57 | 115000 | 82800 | 9.5 | 3550 | 841.8547 |  | 2
95 | 80 | 67 | 51.57 | 116900 | 87675 | 9.54 | 4000 | 1200.2682 |  | 2
95 | 80 | 67 | 51.57 | 119400 | 90744 | 9.57 | 4500 | 1341.9665 |  | 2
95 | 85 | 67 | 39.6 | 117000 | 94770 | 9.52 | 3550 | 841.8547 |  | 2
95 | 85 | 67 | 39.6 | 118800 | 100980 | 9.55 | 4000 | 1200.2682 |  | 2
95 | 85 | 67 | 39.6 | 121400 | 104404 | 9.59 | 4500 | 1341.9665 |  | 2
95 | 80 | 71 | 65.06 | 120300 | 72180 | 9.6 | 3550 | 841.8547 |  | 2
95 | 80 | 71 | 65.06 | 122200 | 73320 | 9.6 | 4000 | 1200.2682 |  | 2
95 | 80 | 71 | 65.06 | 124700 | 74820 | 9.6 | 4500 | 1341.9665 |  | 2
95 | 85 | 71 | 51.08 | 122300 | 85610 | 9.6 | 3550 | 841.8547 |  | 2
95 | 85 | 71 | 51.08 | 124200 | 86940 | 9.6 | 4000 | 1200.2682 |  | 2
95 | 85 | 71 | 51.08 | 126700 | 88690 | 9.6 | 4500 | 1341.9665 |  | 2
105 | 80 | 59 | 27.74 | 103400 | 103400 | 10.62 | 3550 | 825.1844 |  | 2
105 | 80 | 59 | 27.74 | 105300 | 105300 | 10.66 | 4000 | 1179.4302 |  | 2
105 | 80 | 59 | 27.74 | 107800 | 107800 | 10.7 | 4500 | 1341.9665 |  | 2
105 | 85 | 59 | 19.34 | 105400 | 105400 | 10.64 | 3550 | 825.1844 |  | 2
105 | 85 | 59 | 19.34 | 107300 | 107300 | 10.68 | 4000 | 1200.2682 |  | 2
105 | 85 | 59 | 19.34 | 109800 | 109800 | 10.71 | 4500 | 1341.9665 |  | 2
105 | 80 | 63 | 39.17 | 105100 | 105100 | 10.62 | 3550 | 825.1844 |  | 2
105 | 80 | 63 | 39.17 | 107000 | 107000 | 10.65 | 4000 | 1200.2682 |  | 2
105 | 80 | 63 | 39.17 | 109500 | 109500 | 10.69 | 4500 | 1341.9665 |  | 2
105 | 85 | 63 | 29.06 | 107100 | 107100 | 10.63 | 3550 | 841.8547 |  | 2
105 | 85 | 63 | 29.06 | 108900 | 108900 | 10.67 | 4000 | 1200.2682 |  | 2
105 | 85 | 63 | 29.06 | 111500 | 111500 | 10.71 | 4500 | 1341.9665 |  | 2
105 | 80 | 67 | 51.57 | 108600 | 80364 | 10.6 | 3550 | 841.8547 |  | 2
105 | 80 | 67 | 51.57 | 110400 | 85008 | 10.64 | 4000 | 1200.2682 |  | 2
105 | 80 | 67 | 51.57 | 113000 | 88140 | 10.68 | 4500 | 1341.9665 |  | 2
105 | 85 | 67 | 39.6 | 110500 | 91715 | 10.62 | 3550 | 841.8547 |  | 2
105 | 85 | 67 | 39.6 | 112400 | 97788 | 10.66 | 4000 | 1200.2682 |  | 2
105 | 85 | 67 | 39.6 | 115000 | 115000 | 10.69 | 4500 | 1341.9665 |  | 2
105 | 80 | 71 | 65.06 | 113900 | 68340 | 10.7 | 3550 | 841.8547 |  | 2
105 | 80 | 71 | 65.06 | 115800 | 69480 | 10.7 | 4000 | 1200.2682 |  | 2
105 | 80 | 71 | 65.06 | 118300 | 70980 | 10.7 | 4500 | 1341.9665 |  | 2
105 | 85 | 71 | 51.08 | 115900 | 81130 | 10.7 | 3550 | 841.8547 |  | 2
105 | 85 | 71 | 51.08 | 117800 | 82460 | 10.7 | 4000 | 1200.2682 |  | 2
105 | 85 | 71 | 51.08 | 120300 | 84210 | 10.8 | 4500 | 1341.9665 |  | 2
115 | 80 | 59 | 27.74 | 97600 | 97600 | 11.92 | 3550 | 825.1844 |  | 2
115 | 80 | 59 | 27.74 | 99400 | 99400 | 11.96 | 4000 | 1179.4302 |  | 2
115 | 80 | 59 | 27.74 | 102000 | 102000 | 11.99 | 4500 | 1321.1285 |  | 2
115 | 85 | 59 | 19.34 | 99500 | 99500 | 11.94 | 3550 | 825.1844 |  | 2
115 | 85 | 59 | 19.34 | 101400 | 101400 | 11.97 | 4000 | 1179.4302 |  | 2
115 | 85 | 59 | 19.34 | 103900 | 103900 | 12.01 | 4500 | 1321.1285 |  | 2
115 | 80 | 63 | 39.17 | 99200 | 99200 | 11.91 | 3550 | 825.1844 |  | 2
115 | 80 | 63 | 39.17 | 101100 | 101100 | 11.95 | 4000 | 1179.4302 |  | 2
115 | 80 | 63 | 39.17 | 103600 | 103600 | 11.99 | 4500 | 1321.1285 |  | 2
115 | 85 | 63 | 29.06 | 101200 | 101200 | 11.93 | 3550 | 825.1844 |  | 2
115 | 85 | 63 | 29.06 | 103100 | 103100 | 11.97 | 4000 | 1179.4302 |  | 2
115 | 85 | 63 | 29.06 | 105600 | 105600 | 12 | 4500 | 1341.9665 |  | 2
115 | 80 | 67 | 51.57 | 102700 | 81133 | 11.9 | 3550 | 825.1844 |  | 2
115 | 80 | 67 | 51.57 | 104600 | 85772 | 11.94 | 4000 | 1179.4302 |  | 2
115 | 80 | 67 | 51.57 | 107100 | 88893 | 11.97 | 4500 | 1341.9665 |  | 2
115 | 85 | 67 | 39.6 | 104700 | 104700 | 11.92 | 3550 | 825.1844 |  | 2
115 | 85 | 67 | 39.6 | 106600 | 106600 | 11.95 | 4000 | 1200.2682 |  | 2
115 | 85 | 67 | 39.6 | 109100 | 109100 | 11.99 | 4500 | 1341.9665 |  | 2
115 | 80 | 71 | 65.06 | 108000 | 75600 | 12 | 3550 | 841.8547 |  | 2
115 | 80 | 71 | 65.06 | 109900 | 76930 | 12 | 4000 | 1200.2682 |  | 2
115 | 80 | 71 | 65.06 | 112500 | 78750 | 12 | 4500 | 1341.9665 |  | 2
115 | 85 | 71 | 51.08 | 110000 | 77000 | 12 | 3550 | 841.8547 |  | 2
115 | 85 | 71 | 51.08 | 111900 | 89520 | 12 | 4000 | 1200.2682 |  | 2
115 | 85 | 71 | 51.08 | 114400 | 91520 | 12 | 4500 | 1341.9665 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 5
Degradation Coefficient (C_d)
IEER or SEER | 16
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 70 | 59 | 52.72 | 141200 | 87544 | 8.31 | 3800 | 1081.4916 |  | 2
65 | 70 | 59 | 52.72 | 147600 | 97416 | 8.42 | 5000 | 1450.324 |  | 2
65 | 70 | 59 | 52.72 | 152300 | 95949 | 8.47 | 5625 | 1639.9497 |  | 2
65 | 75 | 59 | 38.63 | 141300 | 104562 | 8.3 | 3800 | 1081.4916 |  | 2
65 | 75 | 59 | 38.63 | 147700 | 115206 | 8.41 | 5000 | 1450.324 |  | 2
65 | 75 | 59 | 38.63 | 152400 | 114300 | 8.46 | 5625 | 1639.9497 |  | 2
65 | 70 | 63 | 68.69 | 143200 | 78760 | 8.3 | 3800 | 1081.4916 |  | 2
65 | 70 | 63 | 68.69 | 149600 | 88264 | 8.41 | 5000 | 1450.324 |  | 2
65 | 70 | 63 | 68.69 | 154300 | 86408 | 8.46 | 5625 | 1639.9497 |  | 2
65 | 75 | 63 | 52.11 | 143300 | 96011 | 8.3 | 3800 | 1081.4916 |  | 2
65 | 75 | 63 | 52.11 | 149700 | 106287 | 8.4 | 5000 | 1450.324 |  | 2
65 | 75 | 63 | 52.11 | 154300 | 104924 | 8.45 | 5625 | 1639.9497 |  | 2
65 | 70 | 67 | 86.02 | 147300 | 61866 | 8.28 | 3800 | 1081.4916 |  | 2
65 | 70 | 67 | 86.02 | 153800 | 70748 | 8.39 | 5000 | 1450.324 |  | 2
65 | 70 | 67 | 86.02 | 158400 | 69696 | 8.44 | 5625 | 1639.9497 |  | 2
65 | 75 | 67 | 66.75 | 147400 | 79596 | 8.28 | 3800 | 1081.4916 |  | 2
65 | 75 | 67 | 66.75 | 153900 | 89262 | 8.38 | 5000 | 1450.324 |  | 2
65 | 75 | 67 | 66.75 | 158500 | 88760 | 8.43 | 5625 | 1639.9497 |  | 2
65 | 75 | 71 | 82.67 | 153800 | 61520 | 8.4 | 3800 | 1081.4916 |  | 2
65 | 75 | 71 | 82.67 | 160200 | 80100 | 8.5 | 5000 | 1450.324 |  | 2
65 | 75 | 71 | 82.67 | 164900 | 65960 | 8.5 | 5625 | 1639.9497 |  | 2
75 | 70 | 59 | 52.72 | 140000 | 88200 | 9.37 | 3800 | 1081.4916 |  | 2
75 | 70 | 59 | 52.72 | 146400 | 98088 | 9.48 | 5000 | 1450.324 |  | 2
75 | 70 | 59 | 52.72 | 151100 | 96704 | 9.52 | 5625 | 1639.9497 |  | 2
75 | 75 | 59 | 38.63 | 140000 | 105000 | 9.36 | 3800 | 1081.4916 |  | 2
75 | 75 | 59 | 38.63 | 146500 | 115735 | 9.47 | 5000 | 1450.324 |  | 2
75 | 75 | 59 | 38.63 | 151100 | 151100 | 9.52 | 5625 | 1639.9497 |  | 2
75 | 70 | 63 | 68.69 | 141900 | 79464 | 9.36 | 3800 | 1081.4916 |  | 2
75 | 70 | 63 | 68.69 | 148400 | 89040 | 9.47 | 5000 | 1450.324 |  | 2
75 | 70 | 63 | 68.69 | 153000 | 87210 | 9.52 | 5625 | 1639.9497 |  | 2
75 | 75 | 63 | 52.11 | 142000 | 96560 | 9.35 | 3800 | 1081.4916 |  | 2
75 | 75 | 63 | 52.11 | 148400 | 106848 | 9.46 | 5000 | 1450.324 |  | 2
75 | 75 | 63 | 52.11 | 153100 | 105639 | 9.51 | 5625 | 1639.9497 |  | 2
75 | 70 | 67 | 86.02 | 146100 | 62823 | 9.34 | 3800 | 1081.4916 |  | 2
75 | 70 | 67 | 86.02 | 152500 | 71675 | 9.45 | 5000 | 1450.324 |  | 2
75 | 70 | 67 | 86.02 | 157200 | 69168 | 9.5 | 5625 | 1639.9497 |  | 2
75 | 75 | 67 | 66.75 | 146200 | 80410 | 9.34 | 3800 | 1081.4916 |  | 2
75 | 75 | 67 | 66.75 | 152600 | 90034 | 9.44 | 5000 | 1450.324 |  | 2
75 | 75 | 67 | 66.75 | 157300 | 88088 | 9.49 | 5625 | 1639.9497 |  | 2
75 | 75 | 71 | 82.67 | 152500 | 61000 | 9.4 | 3800 | 1081.4916 |  | 2
75 | 75 | 71 | 82.67 | 159000 | 79500 | 9.5 | 5000 | 1450.324 |  | 2
75 | 75 | 71 | 82.67 | 163600 | 65440 | 9.6 | 5625 | 1639.9497 |  | 2
85 | 70 | 59 | 52.72 | 136300 | 88595 | 10.55 | 3800 | 1081.4916 |  | 2
85 | 70 | 59 | 52.72 | 142800 | 98532 | 10.66 | 5000 | 1450.324 |  | 2
85 | 70 | 59 | 52.72 | 147400 | 97284 | 10.71 | 5625 | 1639.9497 |  | 2
85 | 75 | 59 | 38.63 | 136400 | 105028 | 10.55 | 3800 | 1081.4916 |  | 2
85 | 75 | 59 | 38.63 | 142800 | 142800 | 10.65 | 5000 | 1450.324 |  | 2
85 | 75 | 59 | 38.63 | 147500 | 147500 | 10.7 | 5625 | 1639.9497 |  | 2
85 | 70 | 63 | 68.69 | 138300 | 80214 | 10.54 | 3800 | 1081.4916 |  | 2
85 | 70 | 63 | 68.69 | 144700 | 89714 | 10.65 | 5000 | 1450.324 |  | 2
85 | 70 | 63 | 68.69 | 149400 | 88146 | 10.7 | 5625 | 1639.9497 |  | 2
85 | 75 | 63 | 52.11 | 138400 | 96880 | 10.54 | 3800 | 1081.4916 |  | 2
85 | 75 | 63 | 52.11 | 144800 | 107152 | 10.64 | 5000 | 1450.324 |  | 2
85 | 75 | 63 | 52.11 | 149500 | 106145 | 10.69 | 5625 | 1639.9497 |  | 2
85 | 70 | 67 | 86.02 | 142500 | 64125 | 10.53 | 3800 | 1081.4916 |  | 2
85 | 70 | 67 | 86.02 | 148900 | 72961 | 10.63 | 5000 | 1450.324 |  | 2
85 | 70 | 67 | 86.02 | 153500 | 70610 | 10.68 | 5625 | 1639.9497 |  | 2
85 | 75 | 67 | 66.75 | 142500 | 81225 | 10.52 | 3800 | 1081.4916 |  | 2
85 | 75 | 67 | 66.75 | 149000 | 90890 | 10.63 | 5000 | 1450.324 |  | 2
85 | 75 | 67 | 66.75 | 153600 | 90624 | 10.67 | 5625 | 1639.9497 |  | 2
85 | 75 | 71 | 82.67 | 148900 | 59560 | 10.6 | 3800 | 1081.4916 |  | 2
85 | 75 | 71 | 82.67 | 155300 | 77650 | 10.7 | 5000 | 1450.324 |  | 2
85 | 75 | 71 | 82.67 | 160000 | 80000 | 10.8 | 5625 | 1639.9497 |  | 2
95 | 70 | 59 | 52.72 | 130100 | 87167 | 11.83 | 3800 | 1062.7374 |  | 2
95 | 70 | 59 | 52.72 | 136500 | 136500 | 11.94 | 5000 | 1450.324 |  | 2
95 | 70 | 59 | 52.72 | 141200 | 141200 | 11.99 | 5625 | 1639.9497 |  | 2
95 | 75 | 59 | 38.63 | 130100 | 130100 | 11.83 | 3800 | 1062.7374 |  | 2
95 | 75 | 59 | 38.63 | 136600 | 136600 | 11.93 | 5000 | 1450.324 |  | 2
95 | 75 | 59 | 38.63 | 141200 | 141200 | 11.98 | 5625 | 1639.9497 |  | 2
95 | 70 | 63 | 68.69 | 132000 | 79200 | 11.82 | 3800 | 1062.7374 |  | 2
95 | 70 | 63 | 68.69 | 138500 | 88640 | 11.93 | 5000 | 1450.324 |  | 2
95 | 70 | 63 | 68.69 | 143100 | 87291 | 11.98 | 5625 | 1639.9497 |  | 2
95 | 75 | 63 | 52.11 | 132100 | 95112 | 11.82 | 3800 | 1062.7374 |  | 2
95 | 75 | 63 | 52.11 | 138500 | 105260 | 11.92 | 5000 | 1450.324 |  | 2
95 | 75 | 63 | 52.11 | 143200 | 104536 | 11.97 | 5625 | 1639.9497 |  | 2
95 | 70 | 67 | 86.02 | 136200 | 64014 | 11.81 | 3800 | 1081.4916 |  | 2
95 | 70 | 67 | 86.02 | 142600 | 72726 | 11.91 | 5000 | 1450.324 |  | 2
95 | 70 | 67 | 86.02 | 147300 | 70704 | 11.96 | 5625 | 1639.9497 |  | 2
95 | 75 | 67 | 66.75 | 136300 | 80417 | 11.8 | 3800 | 1081.4916 |  | 2
95 | 75 | 67 | 66.75 | 142700 | 89901 | 11.91 | 5000 | 1450.324 |  | 2
95 | 75 | 67 | 66.75 | 147400 | 88440 | 11.95 | 5625 | 1639.9497 |  | 2
95 | 75 | 71 | 82.67 | 142600 | 71300 | 11.9 | 3800 | 1081.4916 |  | 2
95 | 75 | 71 | 82.67 | 149100 | 74550 | 12 | 5000 | 1450.324 |  | 2
95 | 75 | 71 | 82.67 | 153700 | 76850 | 12 | 5625 | 1639.9497 |  | 2
105 | 70 | 59 | 52.72 | 122400 | 122400 | 13.26 | 3800 | 1062.7374 |  | 2
105 | 70 | 59 | 52.72 | 128800 | 128800 | 13.37 | 5000 | 1416.9832 |  | 2
105 | 70 | 59 | 52.72 | 133500 | 133500 | 13.42 | 5625 | 1604.5251 |  | 2
105 | 75 | 59 | 38.63 | 122500 | 122500 | 13.26 | 3800 | 1062.7374 |  | 2
105 | 75 | 59 | 38.63 | 128900 | 128900 | 13.36 | 5000 | 1416.9832 |  | 2
105 | 75 | 59 | 38.63 | 133600 | 133600 | 13.41 | 5625 | 1604.5251 |  | 2
105 | 70 | 63 | 68.69 | 124400 | 77128 | 13.25 | 3800 | 1062.7374 |  | 2
105 | 70 | 63 | 68.69 | 130800 | 86328 | 13.36 | 5000 | 1416.9832 |  | 2
105 | 70 | 63 | 68.69 | 135500 | 85365 | 13.41 | 5625 | 1639.9497 |  | 2
105 | 75 | 63 | 52.11 | 124500 | 92130 | 13.25 | 3800 | 1062.7374 |  | 2
105 | 75 | 63 | 52.11 | 130900 | 102102 | 13.35 | 5000 | 1416.9832 |  | 2
105 | 75 | 63 | 52.11 | 135500 | 101625 | 13.4 | 5625 | 1639.9497 |  | 2
105 | 70 | 67 | 86.02 | 128500 | 62965 | 13.24 | 3800 | 1062.7374 |  | 2
105 | 70 | 67 | 86.02 | 135000 | 71550 | 13.34 | 5000 | 1450.324 |  | 2
105 | 70 | 67 | 86.02 | 139600 | 69800 | 13.39 | 5625 | 1639.9497 |  | 2
105 | 75 | 67 | 66.75 | 128600 | 78446 | 13.23 | 3800 | 1062.7374 |  | 2
105 | 75 | 67 | 66.75 | 135100 | 87815 | 13.34 | 5000 | 1450.324 |  | 2
105 | 75 | 67 | 66.75 | 139700 | 86614 | 13.38 | 5625 | 1639.9497 |  | 2
105 | 75 | 71 | 82.67 | 135000 | 67500 | 13.3 | 3800 | 1081.4916 |  | 2
105 | 75 | 71 | 82.67 | 141400 | 70700 | 13.4 | 5000 | 1450.324 |  | 2
105 | 75 | 71 | 82.67 | 146100 | 73050 | 13.5 | 5625 | 1639.9497 |  | 2
115 | 70 | 59 | 52.72 | 115400 | 115400 | 14.94 | 3800 | 1062.7374 |  | 2
115 | 70 | 59 | 52.72 | 121900 | 121900 | 15.05 | 5000 | 1416.9832 |  | 2
115 | 70 | 59 | 52.72 | 126500 | 126500 | 15.1 | 5625 | 1604.5251 |  | 2
115 | 75 | 59 | 38.63 | 115500 | 115500 | 14.93 | 3800 | 1062.7374 |  | 2
115 | 75 | 59 | 38.63 | 121900 | 121900 | 15.04 | 5000 | 1416.9832 |  | 2
115 | 75 | 59 | 38.63 | 126600 | 126600 | 15.09 | 5625 | 1604.5251 |  | 2
115 | 70 | 63 | 68.69 | 117400 | 78658 | 14.93 | 3800 | 1062.7374 |  | 2
115 | 70 | 63 | 68.69 | 123800 | 87898 | 15.04 | 5000 | 1416.9832 |  | 2
115 | 70 | 63 | 68.69 | 128500 | 87380 | 15.09 | 5625 | 1604.5251 |  | 2
115 | 75 | 63 | 52.11 | 117500 | 92825 | 14.93 | 3800 | 1062.7374 |  | 2
115 | 75 | 63 | 52.11 | 123900 | 123900 | 15.03 | 5000 | 1416.9832 |  | 2
115 | 75 | 63 | 52.11 | 128600 | 128600 | 15.08 | 5625 | 1604.5251 |  | 2
115 | 70 | 67 | 86.02 | 121600 | 65664 | 14.91 | 3800 | 1062.7374 |  | 2
115 | 70 | 67 | 86.02 | 128000 | 74240 | 15.02 | 5000 | 1416.9832 |  | 2
115 | 70 | 67 | 86.02 | 132600 | 72930 | 15.07 | 5625 | 1604.5251 |  | 2
115 | 75 | 67 | 66.75 | 121600 | 80256 | 14.91 | 3800 | 1062.7374 |  | 2
115 | 75 | 67 | 66.75 | 128100 | 89670 | 15.01 | 5000 | 1416.9832 |  | 2
115 | 75 | 67 | 66.75 | 132700 | 88909 | 15.06 | 5625 | 1604.5251 |  | 2
115 | 75 | 71 | 82.67 | 128000 | 64000 | 15 | 3800 | 1062.7374 |  | 2
115 | 75 | 71 | 82.67 | 134400 | 80640 | 15.1 | 5000 | 1416.9832 |  | 2
115 | 75 | 71 | 82.67 | 139100 | 69550 | 15.1 | 5625 | 1639.9497 |  | 2
65 | 80 | 59 | 27.74 | 142000 | 122120 | 8.31 | 3800 | 1081.4916 |  | 2
65 | 80 | 59 | 27.74 | 148400 | 148400 | 8.42 | 5000 | 1450.324 |  | 2
65 | 80 | 59 | 27.74 | 153100 | 153100 | 8.46 | 5625 | 1639.9497 |  | 2
65 | 85 | 59 | 19.34 | 144400 | 144400 | 8.33 | 3800 | 1081.4916 |  | 2
65 | 85 | 59 | 19.34 | 150800 | 150800 | 8.44 | 5000 | 1450.324 |  | 2
65 | 85 | 59 | 19.34 | 155500 | 155500 | 8.48 | 5625 | 1639.9497 |  | 2
65 | 80 | 63 | 39.17 | 144000 | 113760 | 8.3 | 3800 | 1081.4916 |  | 2
65 | 80 | 63 | 39.17 | 150400 | 124832 | 8.41 | 5000 | 1450.324 |  | 2
65 | 80 | 63 | 39.17 | 155100 | 124080 | 8.46 | 5625 | 1639.9497 |  | 2
65 | 85 | 63 | 29.06 | 146300 | 128744 | 8.32 | 3800 | 1081.4916 |  | 2
65 | 85 | 63 | 29.06 | 152800 | 140576 | 8.43 | 5000 | 1450.324 |  | 2
65 | 85 | 63 | 29.06 | 157400 | 140086 | 8.48 | 5625 | 1639.9497 |  | 2
65 | 80 | 67 | 51.57 | 148100 | 97746 | 8.28 | 3800 | 1081.4916 |  | 2
65 | 80 | 67 | 51.57 | 154600 | 108220 | 8.39 | 5000 | 1450.324 |  | 2
65 | 80 | 67 | 51.57 | 159200 | 106664 | 8.44 | 5625 | 1639.9497 |  | 2
65 | 85 | 67 | 39.6 | 150500 | 114380 | 8.3 | 3800 | 1081.4916 |  | 2
65 | 85 | 67 | 39.6 | 156900 | 125520 | 8.41 | 5000 | 1450.324 |  | 2
65 | 85 | 67 | 39.6 | 161600 | 124432 | 8.46 | 5625 | 1639.9497 |  | 2
65 | 80 | 71 | 65.06 | 154500 | 77250 | 8.4 | 3800 | 1081.4916 |  | 2
65 | 80 | 71 | 65.06 | 160900 | 96540 | 8.5 | 5000 | 1450.324 |  | 2
65 | 80 | 71 | 65.06 | 165600 | 82800 | 8.5 | 5625 | 1639.9497 |  | 2
65 | 85 | 71 | 51.08 | 156900 | 94140 | 8.4 | 3800 | 1081.4916 |  | 2
65 | 85 | 71 | 51.08 | 163300 | 114310 | 8.5 | 5000 | 1450.324 |  | 2
65 | 85 | 71 | 51.08 | 167900 | 100740 | 8.5 | 5625 | 1639.9497 |  | 2
75 | 80 | 59 | 27.74 | 140800 | 140800 | 9.37 | 3800 | 1081.4916 |  | 2
75 | 80 | 59 | 27.74 | 147200 | 147200 | 9.48 | 5000 | 1450.324 |  | 2
75 | 80 | 59 | 27.74 | 151900 | 151900 | 9.52 | 5625 | 1639.9497 |  | 2
75 | 85 | 59 | 19.34 | 143100 | 143100 | 9.39 | 3800 | 1081.4916 |  | 2
75 | 85 | 59 | 19.34 | 149500 | 149500 | 9.5 | 5000 | 1450.324 |  | 2
75 | 85 | 59 | 19.34 | 154200 | 154200 | 9.54 | 5625 | 1639.9497 |  | 2
75 | 80 | 63 | 39.17 | 142700 | 112733 | 9.36 | 3800 | 1081.4916 |  | 2
75 | 80 | 63 | 39.17 | 149200 | 123836 | 9.47 | 5000 | 1450.324 |  | 2
75 | 80 | 63 | 39.17 | 153800 | 124578 | 9.52 | 5625 | 1639.9497 |  | 2
75 | 85 | 63 | 29.06 | 145100 | 129139 | 9.38 | 3800 | 1081.4916 |  | 2
75 | 85 | 63 | 29.06 | 151500 | 151500 | 9.49 | 5000 | 1450.324 |  | 2
75 | 85 | 63 | 29.06 | 156200 | 156200 | 9.54 | 5625 | 1639.9497 |  | 2
75 | 80 | 67 | 51.57 | 146900 | 98423 | 9.34 | 3800 | 1081.4916 |  | 2
75 | 80 | 67 | 51.57 | 153300 | 108843 | 9.45 | 5000 | 1450.324 |  | 2
75 | 80 | 67 | 51.57 | 158000 | 107440 | 9.5 | 5625 | 1639.9497 |  | 2
75 | 85 | 67 | 39.6 | 149200 | 113392 | 9.36 | 3800 | 1081.4916 |  | 2
75 | 85 | 67 | 39.6 | 155700 | 124560 | 9.47 | 5000 | 1450.324 |  | 2
75 | 85 | 67 | 39.6 | 160300 | 123431 | 9.52 | 5625 | 1639.9497 |  | 2
75 | 80 | 71 | 65.06 | 153300 | 76650 | 9.4 | 3800 | 1081.4916 |  | 2
75 | 80 | 71 | 65.06 | 159700 | 95820 | 9.5 | 5000 | 1450.324 |  | 2
75 | 80 | 71 | 65.06 | 164300 | 82150 | 9.6 | 5625 | 1639.9497 |  | 2
75 | 85 | 71 | 51.08 | 155600 | 93360 | 9.4 | 3800 | 1081.4916 |  | 2
75 | 85 | 71 | 51.08 | 162000 | 113400 | 9.6 | 5000 | 1450.324 |  | 2
75 | 85 | 71 | 51.08 | 166700 | 100020 | 9.6 | 5625 | 1639.9497 |  | 2
85 | 80 | 59 | 27.74 | 137100 | 137100 | 10.55 | 3800 | 1081.4916 |  | 2
85 | 80 | 59 | 27.74 | 143600 | 143600 | 10.66 | 5000 | 1450.324 |  | 2
85 | 80 | 59 | 27.74 | 148200 | 148200 | 10.71 | 5625 | 1639.9497 |  | 2
85 | 85 | 59 | 19.34 | 139500 | 139500 | 10.57 | 3800 | 1081.4916 |  | 2
85 | 85 | 59 | 19.34 | 145900 | 145900 | 10.68 | 5000 | 1450.324 |  | 2
85 | 85 | 59 | 19.34 | 150600 | 150600 | 10.73 | 5625 | 1639.9497 |  | 2
85 | 80 | 63 | 39.17 | 139100 | 114062 | 10.54 | 3800 | 1081.4916 |  | 2
85 | 80 | 63 | 39.17 | 145500 | 125130 | 10.65 | 5000 | 1450.324 |  | 2
85 | 80 | 63 | 39.17 | 150200 | 124666 | 10.7 | 5625 | 1639.9497 |  | 2
85 | 85 | 63 | 29.06 | 141400 | 141400 | 10.56 | 3800 | 1081.4916 |  | 2
85 | 85 | 63 | 29.06 | 147900 | 147900 | 10.67 | 5000 | 1450.324 |  | 2
85 | 85 | 63 | 29.06 | 152500 | 152500 | 10.72 | 5625 | 1639.9497 |  | 2
85 | 80 | 67 | 51.57 | 143300 | 98877 | 10.53 | 3800 | 1081.4916 |  | 2
85 | 80 | 67 | 51.57 | 149700 | 109281 | 10.63 | 5000 | 1450.324 |  | 2
85 | 80 | 67 | 51.57 | 154300 | 108010 | 10.68 | 5625 | 1639.9497 |  | 2
85 | 85 | 67 | 39.6 | 145600 | 115024 | 10.55 | 3800 | 1081.4916 |  | 2
85 | 85 | 67 | 39.6 | 152000 | 126160 | 10.65 | 5000 | 1450.324 |  | 2
85 | 85 | 67 | 39.6 | 156700 | 125360 | 10.7 | 5625 | 1639.9497 |  | 2
85 | 80 | 71 | 65.06 | 149600 | 89760 | 10.6 | 3800 | 1081.4916 |  | 2
85 | 80 | 71 | 65.06 | 156100 | 93660 | 10.7 | 5000 | 1450.324 |  | 2
85 | 80 | 71 | 65.06 | 160700 | 96420 | 10.8 | 5625 | 1639.9497 |  | 2
85 | 85 | 71 | 51.08 | 152000 | 106400 | 10.6 | 3800 | 1081.4916 |  | 2
85 | 85 | 71 | 51.08 | 158400 | 110880 | 10.7 | 5000 | 1450.324 |  | 2
85 | 85 | 71 | 51.08 | 163100 | 114170 | 10.8 | 5625 | 1639.9497 |  | 2
95 | 80 | 59 | 27.74 | 130900 | 130900 | 11.83 | 3800 | 1062.7374 |  | 2
95 | 80 | 59 | 27.74 | 137300 | 137300 | 11.94 | 5000 | 1450.324 |  | 2
95 | 80 | 59 | 27.74 | 142000 | 142000 | 11.99 | 5625 | 1639.9497 |  | 2
95 | 85 | 59 | 19.34 | 133200 | 133200 | 11.85 | 3800 | 1062.7374 |  | 2
95 | 85 | 59 | 19.34 | 139600 | 139600 | 11.96 | 5000 | 1450.324 |  | 2
95 | 85 | 59 | 19.34 | 144300 | 144300 | 12.01 | 5625 | 1639.9497 |  | 2
95 | 80 | 63 | 39.17 | 132800 | 111552 | 11.82 | 3800 | 1062.7374 |  | 2
95 | 80 | 63 | 39.17 | 139300 | 139300 | 11.93 | 5000 | 1450.324 |  | 2
95 | 80 | 63 | 39.17 | 143900 | 143900 | 11.98 | 5625 | 1639.9497 |  | 2
95 | 85 | 63 | 29.06 | 135200 | 135200 | 11.84 | 3800 | 1081.4916 |  | 2
95 | 85 | 63 | 29.06 | 141600 | 141600 | 11.95 | 5000 | 1450.324 |  | 2
95 | 85 | 63 | 29.06 | 146300 | 146300 | 12 | 5625 | 1639.9497 |  | 2
95 | 80 | 67 | 51.57 | 137000 | 97270 | 11.81 | 3800 | 1081.4916 |  | 2
95 | 80 | 67 | 51.57 | 143400 | 107550 | 11.91 | 5000 | 1450.324 |  | 2
95 | 80 | 67 | 51.57 | 148100 | 106632 | 11.96 | 5625 | 1639.9497 |  | 2
95 | 85 | 67 | 39.6 | 139300 | 111440 | 11.83 | 3800 | 1081.4916 |  | 2
95 | 85 | 67 | 39.6 | 145800 | 122472 | 11.93 | 5000 | 1450.324 |  | 2
95 | 85 | 67 | 39.6 | 150400 | 121824 | 11.98 | 5625 | 1639.9497 |  | 2
95 | 80 | 71 | 65.06 | 143400 | 86040 | 11.9 | 3800 | 1081.4916 |  | 2
95 | 80 | 71 | 65.06 | 149800 | 89880 | 12 | 5000 | 1450.324 |  | 2
95 | 80 | 71 | 65.06 | 154400 | 92640 | 12 | 5625 | 1639.9497 |  | 2
95 | 85 | 71 | 51.08 | 145700 | 101990 | 11.9 | 3800 | 1081.4916 |  | 2
95 | 85 | 71 | 51.08 | 152100 | 106470 | 12 | 5000 | 1450.324 |  | 2
95 | 85 | 71 | 51.08 | 156800 | 109760 | 12.1 | 5625 | 1639.9497 |  | 2
105 | 80 | 59 | 27.74 | 123200 | 123200 | 13.26 | 3800 | 1062.7374 |  | 2
105 | 80 | 59 | 27.74 | 129600 | 129600 | 13.37 | 5000 | 1416.9832 |  | 2
105 | 80 | 59 | 27.74 | 134300 | 134300 | 13.42 | 5625 | 1604.5251 |  | 2
105 | 85 | 59 | 19.34 | 125600 | 125600 | 13.28 | 3800 | 1062.7374 |  | 2
105 | 85 | 59 | 19.34 | 132000 | 132000 | 13.39 | 5000 | 1416.9832 |  | 2
105 | 85 | 59 | 19.34 | 136600 | 136600 | 13.44 | 5625 | 1639.9497 |  | 2
105 | 80 | 63 | 39.17 | 125200 | 125200 | 13.25 | 3800 | 1062.7374 |  | 2
105 | 80 | 63 | 39.17 | 131600 | 131600 | 13.36 | 5000 | 1416.9832 |  | 2
105 | 80 | 63 | 39.17 | 136300 | 136300 | 13.41 | 5625 | 1639.9497 |  | 2
105 | 85 | 63 | 29.06 | 127500 | 127500 | 13.27 | 3800 | 1062.7374 |  | 2
105 | 85 | 63 | 29.06 | 134000 | 134000 | 13.38 | 5000 | 1416.9832 |  | 2
105 | 85 | 63 | 29.06 | 138600 | 138600 | 13.43 | 5625 | 1639.9497 |  | 2
105 | 80 | 67 | 51.57 | 129300 | 94389 | 13.24 | 3800 | 1062.7374 |  | 2
105 | 80 | 67 | 51.57 | 135800 | 104566 | 13.34 | 5000 | 1450.324 |  | 2
105 | 80 | 67 | 51.57 | 140400 | 103896 | 13.39 | 5625 | 1639.9497 |  | 2
105 | 85 | 67 | 39.6 | 131700 | 107994 | 13.26 | 3800 | 1062.7374 |  | 2
105 | 85 | 67 | 39.6 | 138100 | 118766 | 13.36 | 5000 | 1450.324 |  | 2
105 | 85 | 67 | 39.6 | 142800 | 142800 | 13.41 | 5625 | 1639.9497 |  | 2
105 | 80 | 71 | 65.06 | 135700 | 81420 | 13.3 | 3800 | 1081.4916 |  | 2
105 | 80 | 71 | 65.06 | 142100 | 85260 | 13.4 | 5000 | 1450.324 |  | 2
105 | 80 | 71 | 65.06 | 146800 | 88080 | 13.5 | 5625 | 1639.9497 |  | 2
105 | 85 | 71 | 51.08 | 138100 | 96670 | 13.3 | 3800 | 1081.4916 |  | 2
105 | 85 | 71 | 51.08 | 144500 | 101150 | 13.4 | 5000 | 1450.324 |  | 2
105 | 85 | 71 | 51.08 | 149100 | 104370 | 13.5 | 5625 | 1639.9497 |  | 2
115 | 80 | 59 | 27.74 | 116200 | 116200 | 14.94 | 3800 | 1062.7374 |  | 2
115 | 80 | 59 | 27.74 | 122700 | 122700 | 15.05 | 5000 | 1416.9832 |  | 2
115 | 80 | 59 | 27.74 | 127300 | 127300 | 15.09 | 5625 | 1604.5251 |  | 2
115 | 85 | 59 | 19.34 | 118600 | 118600 | 14.96 | 3800 | 1062.7374 |  | 2
115 | 85 | 59 | 19.34 | 125000 | 125000 | 15.07 | 5000 | 1416.9832 |  | 2
115 | 85 | 59 | 19.34 | 129700 | 129700 | 15.11 | 5625 | 1604.5251 |  | 2
115 | 80 | 63 | 39.17 | 118200 | 118200 | 14.93 | 3800 | 1062.7374 |  | 2
115 | 80 | 63 | 39.17 | 124600 | 124600 | 15.04 | 5000 | 1416.9832 |  | 2
115 | 80 | 63 | 39.17 | 129300 | 129300 | 15.09 | 5625 | 1604.5251 |  | 2
115 | 85 | 63 | 29.06 | 120500 | 120500 | 14.95 | 3800 | 1062.7374 |  | 2
115 | 85 | 63 | 29.06 | 127000 | 127000 | 15.06 | 5000 | 1416.9832 |  | 2
115 | 85 | 63 | 29.06 | 131600 | 131600 | 15.11 | 5625 | 1604.5251 |  | 2
115 | 80 | 67 | 51.57 | 122400 | 95472 | 14.91 | 3800 | 1043.9832 |  | 2
115 | 80 | 67 | 51.57 | 128800 | 105616 | 15.02 | 5000 | 1416.9832 |  | 2
115 | 80 | 67 | 51.57 | 133400 | 105386 | 15.07 | 5625 | 1604.5251 |  | 2
115 | 85 | 67 | 39.6 | 124700 | 108489 | 14.93 | 3800 | 1062.7374 |  | 2
115 | 85 | 67 | 39.6 | 131100 | 131100 | 15.04 | 5000 | 1416.9832 |  | 2
115 | 85 | 67 | 39.6 | 135800 | 135800 | 15.09 | 5625 | 1639.9497 |  | 2
115 | 80 | 71 | 65.06 | 128700 | 77220 | 15 | 3800 | 1062.7374 |  | 2
115 | 80 | 71 | 65.06 | 135200 | 94640 | 15.1 | 5000 | 1450.324 |  | 2
115 | 80 | 71 | 65.06 | 139800 | 97860 | 15.1 | 5625 | 1639.9497 |  | 2
115 | 85 | 71 | 51.08 | 131100 | 91770 | 15 | 3800 | 1062.7374 |  | 2
115 | 85 | 71 | 51.08 | 137500 | 110000 | 15.1 | 5000 | 1450.324 |  | 2
115 | 85 | 71 | 51.08 | 142200 | 113760 | 15.2 | 5625 | 1639.9497 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 6
Degradation Coefficient (C_d)
IEER or SEER | 14.2
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 70 | 59 | 52.7218 | 175388 | 103478.92 | 10.925 | 4500 | 433.1964 |  | 3
65 | 70 | 59 | 52.7218 | 177290 | 111692.7 | 10.984 | 5010 | 467.0085 |  | 3
65 | 70 | 59 | 52.7218 | 181904 | 121875.68 | 11.078 | 6000 | 867.8291 |  | 3
65 | 75 | 59 | 38.6294 | 175490 | 124597.9 | 10.916 | 4500 | 433.1964 |  | 3
65 | 75 | 59 | 38.6294 | 177392 | 133044 | 10.975 | 5010 | 467.0085 |  | 3
65 | 75 | 59 | 38.6294 | 182006 | 143784.74 | 11.069 | 6000 | 867.8291 |  | 3
65 | 70 | 63 | 68.6866 | 177859 | 92486.68 | 10.914 | 4500 | 433.1964 |  | 3
65 | 70 | 63 | 68.6866 | 179762 | 100666.72 | 10.973 | 5010 | 467.0085 |  | 3
65 | 70 | 63 | 68.6866 | 184376 | 110625.6 | 11.067 | 6000 | 867.8291 |  | 3
65 | 75 | 63 | 52.1129 | 177961 | 113895.04 | 10.905 | 4500 | 433.1964 |  | 3
65 | 75 | 63 | 52.1129 | 179864 | 122307.52 | 10.964 | 5010 | 467.0085 |  | 3
65 | 75 | 63 | 52.1129 | 184478 | 132824.16 | 11.058 | 6000 | 867.8291 |  | 3
65 | 70 | 67 | 86.0167 | 183087 | 71403.93 | 10.89 | 4500 | 433.1964 |  | 3
65 | 70 | 67 | 86.0167 | 184989 | 79545.27 | 10.949 | 5010 | 467.0085 |  | 3
65 | 70 | 67 | 86.0167 | 189603 | 89113.41 | 11.043 | 6000 | 867.8291 |  | 3
65 | 75 | 67 | 66.7494 | 183189 | 93426.39 | 10.881 | 4500 | 433.1964 |  | 3
65 | 75 | 67 | 66.7494 | 185091 | 101800.05 | 10.94 | 5010 | 467.0085 |  | 3
65 | 75 | 67 | 66.7494 | 189705 | 111925.95 | 11.034 | 6000 | 867.8291 |  | 3
65 | 75 | 71 | 82.6659 | 191174 | 70734.38 | 10.989 | 4500 | 433.1964 |  | 3
65 | 75 | 71 | 82.6659 | 193076 | 81091.92 | 11.048 | 5010 | 467.0085 |  | 3
65 | 75 | 71 | 82.6659 | 197690 | 90937.4 | 11.142 | 6000 | 867.8291 |  | 3
75 | 70 | 59 | 52.7218 | 173821 | 102554.39 | 12.346 | 4500 | 433.1964 |  | 3
75 | 70 | 59 | 52.7218 | 175724 | 112463.36 | 12.404 | 5010 | 467.0085 |  | 3
75 | 70 | 59 | 52.7218 | 180338 | 122629.84 | 12.499 | 6000 | 867.8291 |  | 3
75 | 75 | 59 | 38.6294 | 173923 | 125224.56 | 12.336 | 4500 | 433.1964 |  | 3
75 | 75 | 59 | 38.6294 | 175826 | 133627.76 | 12.395 | 5010 | 467.0085 |  | 3
75 | 75 | 59 | 38.6294 | 180440 | 144352 | 12.489 | 6000 | 867.8291 |  | 3
75 | 70 | 63 | 68.6866 | 176293 | 91672.36 | 12.334 | 4500 | 433.1964 |  | 3
75 | 70 | 63 | 68.6866 | 178195 | 101571.15 | 12.393 | 5010 | 467.0085 |  | 3
75 | 70 | 63 | 68.6866 | 182809 | 111513.49 | 12.487 | 6000 | 867.8291 |  | 3
75 | 75 | 63 | 52.1129 | 176395 | 112892.8 | 12.325 | 4500 | 433.1964 |  | 3
75 | 75 | 63 | 52.1129 | 178297 | 123024.93 | 12.384 | 5010 | 467.0085 |  | 3
75 | 75 | 63 | 52.1129 | 182911 | 133525.03 | 12.478 | 6000 | 867.8291 |  | 3
75 | 70 | 67 | 86.0167 | 181521 | 70793.19 | 12.31 | 4500 | 433.1964 |  | 3
75 | 70 | 67 | 86.0167 | 183423 | 80706.12 | 12.369 | 5010 | 467.0085 |  | 3
75 | 70 | 67 | 86.0167 | 188037 | 90257.76 | 12.463 | 6000 | 867.8291 |  | 3
75 | 75 | 67 | 66.7494 | 181623 | 92627.73 | 12.301 | 4500 | 433.1964 |  | 3
75 | 75 | 67 | 66.7494 | 183525 | 102774 | 12.36 | 5010 | 467.0085 |  | 3
75 | 75 | 67 | 66.7494 | 188139 | 112883.4 | 12.454 | 6000 | 867.8291 |  | 3
75 | 75 | 71 | 82.6659 | 189608 | 72051.04 | 12.41 | 4500 | 433.1964 |  | 3
75 | 75 | 71 | 82.6659 | 191510 | 80434.2 | 12.468 | 5010 | 467.0085 |  | 3
75 | 75 | 71 | 82.6659 | 196124 | 90217.04 | 12.563 | 6000 | 867.8291 |  | 3
85 | 70 | 59 | 52.7218 | 169252 | 104936.24 | 13.931 | 4500 | 433.1964 |  | 3
85 | 70 | 59 | 52.7218 | 171154 | 112961.64 | 13.99 | 5010 | 467.0085 |  | 3
85 | 70 | 59 | 52.7218 | 175768 | 123037.6 | 14.084 | 6000 | 867.8291 |  | 3
85 | 75 | 59 | 38.6294 | 169354 | 125321.96 | 13.922 | 4500 | 433.1964 |  | 3
85 | 75 | 59 | 38.6294 | 171256 | 133579.68 | 13.981 | 5010 | 467.0085 |  | 3
85 | 75 | 59 | 38.6294 | 175870 | 144213.4 | 14.075 | 6000 | 867.8291 |  | 3
85 | 70 | 63 | 68.6866 | 171724 | 92730.96 | 13.92 | 4500 | 433.1964 |  | 3
85 | 70 | 63 | 68.6866 | 173626 | 102439.34 | 13.979 | 5010 | 467.0085 |  | 3
85 | 70 | 63 | 68.6866 | 178240 | 112291.2 | 14.073 | 6000 | 867.8291 |  | 3
85 | 75 | 63 | 52.1129 | 171826 | 115123.42 | 13.911 | 4500 | 433.1964 |  | 3
85 | 75 | 63 | 52.1129 | 173728 | 123346.88 | 13.969 | 5010 | 467.0085 |  | 3
85 | 75 | 63 | 52.1129 | 178342 | 133756.5 | 14.063 | 6000 | 867.8291 |  | 3
85 | 70 | 67 | 86.0167 | 176951 | 74319.42 | 13.896 | 4500 | 433.1964 |  | 3
85 | 70 | 67 | 86.0167 | 178853 | 82272.38 | 13.954 | 5010 | 467.0085 |  | 3
85 | 70 | 67 | 86.0167 | 183467 | 91733.5 | 14.048 | 6000 | 867.8291 |  | 3
85 | 75 | 67 | 66.7494 | 177053 | 95608.62 | 13.886 | 4500 | 433.1964 |  | 3
85 | 75 | 67 | 66.7494 | 178955 | 103793.9 | 13.945 | 5010 | 467.0085 |  | 3
85 | 75 | 67 | 66.7494 | 183569 | 113812.78 | 14.039 | 6000 | 867.8291 |  | 3
85 | 75 | 71 | 82.6659 | 185038 | 74015.2 | 13.995 | 4500 | 433.1964 |  | 3
85 | 75 | 71 | 82.6659 | 186940 | 84123 | 14.054 | 5010 | 467.0085 |  | 3
85 | 75 | 71 | 82.6659 | 191554 | 93861.46 | 14.148 | 6000 | 867.8291 |  | 3
95 | 70 | 59 | 52.7218 | 161390 | 103289.6 | 15.647 | 4500 | 433.1964 |  | 3
95 | 70 | 59 | 52.7218 | 163292 | 111038.56 | 15.705 | 5010 | 467.0085 |  | 3
95 | 70 | 59 | 52.7218 | 167906 | 120892.32 | 15.799 | 6000 | 867.8291 |  | 3
95 | 75 | 59 | 38.6294 | 161492 | 122733.92 | 15.637 | 4500 | 433.1964 |  | 3
95 | 75 | 59 | 38.6294 | 163394 | 130715.2 | 15.696 | 5010 | 467.0085 |  | 3
95 | 75 | 59 | 38.6294 | 168008 | 168008 | 15.79 | 6000 | 867.8291 |  | 3
95 | 70 | 63 | 68.6866 | 163862 | 91762.72 | 15.635 | 4500 | 433.1964 |  | 3
95 | 70 | 63 | 68.6866 | 165764 | 101116.04 | 15.694 | 5010 | 467.0085 |  | 3
95 | 70 | 63 | 68.6866 | 170378 | 110745.7 | 15.788 | 6000 | 867.8291 |  | 3
95 | 75 | 63 | 52.1129 | 163964 | 113135.16 | 15.626 | 4500 | 433.1964 |  | 3
95 | 75 | 63 | 52.1129 | 165866 | 121082.18 | 15.685 | 5010 | 467.0085 |  | 3
95 | 75 | 63 | 52.1129 | 170480 | 131269.6 | 15.779 | 6000 | 867.8291 |  | 3
95 | 70 | 67 | 86.0167 | 169089 | 72708.27 | 15.611 | 4500 | 433.1964 |  | 3
95 | 70 | 67 | 86.0167 | 170991 | 82075.68 | 15.67 | 5010 | 467.0085 |  | 3
95 | 70 | 67 | 86.0167 | 175605 | 91314.6 | 15.764 | 6000 | 867.8291 |  | 3
95 | 75 | 67 | 66.7494 | 169191 | 94746.96 | 15.602 | 4500 | 433.1964 |  | 3
95 | 75 | 67 | 66.7494 | 171093 | 102655.8 | 15.661 | 5010 | 467.0085 |  | 3
95 | 75 | 67 | 66.7494 | 175707 | 112452.48 | 15.755 | 6000 | 867.8291 |  | 3
95 | 75 | 71 | 82.6659 | 177176 | 74413.92 | 15.711 | 4500 | 433.1964 |  | 3
95 | 75 | 71 | 82.6659 | 179078 | 84166.66 | 15.769 | 5010 | 467.0085 |  | 3
95 | 75 | 71 | 82.6659 | 183692 | 93682.92 | 15.863 | 6000 | 867.8291 |  | 3
105 | 70 | 59 | 52.7218 | 151782 | 100176.12 | 17.563 | 4500 | 433.1964 |  | 3
105 | 70 | 59 | 52.7218 | 153684 | 107578.8 | 17.622 | 5010 | 467.0085 |  | 3
105 | 70 | 59 | 52.7218 | 158298 | 117140.52 | 17.716 | 6000 | 867.8291 |  | 3
105 | 75 | 59 | 38.6294 | 151884 | 151884 | 17.554 | 4500 | 433.1964 |  | 3
105 | 75 | 59 | 38.6294 | 153786 | 153786 | 17.613 | 5010 | 467.0085 |  | 3
105 | 75 | 59 | 38.6294 | 158400 | 158400 | 17.707 | 6000 | 867.8291 |  | 3
105 | 70 | 63 | 68.6866 | 154254 | 89467.32 | 17.552 | 4500 | 433.1964 |  | 3
105 | 70 | 63 | 68.6866 | 156156 | 98378.28 | 17.611 | 5010 | 467.0085 |  | 3
105 | 70 | 63 | 68.6866 | 160770 | 107715.9 | 17.705 | 6000 | 867.8291 |  | 3
105 | 75 | 63 | 52.1129 | 154356 | 109592.76 | 17.543 | 4500 | 433.1964 |  | 3
105 | 75 | 63 | 52.1129 | 156258 | 117193.5 | 17.602 | 5010 | 467.0085 |  | 3
105 | 75 | 63 | 52.1129 | 160872 | 127088.88 | 17.696 | 6000 | 867.8291 |  | 3
105 | 70 | 67 | 86.0167 | 159481 | 73361.26 | 17.528 | 4500 | 433.1964 |  | 3
105 | 70 | 67 | 86.0167 | 161383 | 80691.5 | 17.587 | 5010 | 467.0085 |  | 3
105 | 70 | 67 | 86.0167 | 165997 | 89638.38 | 17.681 | 6000 | 867.8291 |  | 3
105 | 75 | 67 | 66.7494 | 159583 | 92558.14 | 17.519 | 4500 | 433.1964 |  | 3
105 | 75 | 67 | 66.7494 | 161485 | 100120.7 | 17.577 | 5010 | 467.0085 |  | 3
105 | 75 | 67 | 66.7494 | 166099 | 109625.34 | 17.672 | 6000 | 867.8291 |  | 3
105 | 75 | 71 | 82.6659 | 167568 | 73729.92 | 17.627 | 4500 | 433.1964 |  | 3
105 | 75 | 71 | 82.6659 | 169470 | 83040.3 | 17.686 | 5010 | 467.0085 |  | 3
105 | 75 | 71 | 82.6659 | 174084 | 92264.52 | 17.78 | 6000 | 867.8291 |  | 3
115 | 70 | 59 | 52.7218 | 143011 | 101537.81 | 19.812 | 4500 | 433.1964 |  | 3
115 | 70 | 59 | 52.7218 | 144913 | 108684.75 | 19.871 | 5010 | 467.0085 |  | 3
115 | 70 | 59 | 52.7218 | 149527 | 149527 | 19.965 | 6000 | 867.8291 |  | 3
115 | 75 | 59 | 38.6294 | 143113 | 143113 | 19.803 | 4500 | 433.1964 |  | 3
115 | 75 | 59 | 38.6294 | 145015 | 145015 | 19.862 | 5010 | 467.0085 |  | 3
115 | 75 | 59 | 38.6294 | 149629 | 149629 | 19.956 | 6000 | 867.8291 |  | 3
115 | 70 | 63 | 68.6866 | 145482 | 91653.66 | 19.801 | 4500 | 433.1964 |  | 3
115 | 70 | 63 | 68.6866 | 147385 | 100221.8 | 19.86 | 5010 | 467.0085 |  | 3
115 | 70 | 63 | 68.6866 | 151999 | 109439.28 | 19.954 | 6000 | 867.8291 |  | 3
115 | 75 | 63 | 52.1129 | 145584 | 110643.84 | 19.792 | 4500 | 433.1964 |  | 3
115 | 75 | 63 | 52.1129 | 147487 | 117989.6 | 19.851 | 5010 | 467.0085 |  | 3
115 | 75 | 63 | 52.1129 | 152100 | 127764 | 19.945 | 6000 | 867.8291 |  | 3
115 | 70 | 67 | 86.0167 | 150710 | 75355 | 19.777 | 4500 | 433.1964 |  | 3
115 | 70 | 67 | 86.0167 | 152612 | 83936.6 | 19.836 | 5010 | 467.0085 |  | 3
115 | 70 | 67 | 86.0167 | 157226 | 92763.34 | 19.93 | 6000 | 867.8291 |  | 3
115 | 75 | 67 | 66.7494 | 150812 | 95011.56 | 19.768 | 4500 | 433.1964 |  | 3
115 | 75 | 67 | 66.7494 | 152714 | 102318.38 | 19.826 | 5010 | 467.0085 |  | 3
115 | 75 | 67 | 66.7494 | 157328 | 111702.88 | 19.92 | 6000 | 867.8291 |  | 3
115 | 75 | 71 | 82.6659 | 158797 | 77810.53 | 19.876 | 4500 | 433.1964 |  | 3
115 | 75 | 71 | 82.6659 | 160699 | 86777.46 | 19.935 | 5010 | 467.0085 |  | 3
115 | 75 | 71 | 82.6659 | 165313 | 95881.54 | 20.029 | 6000 | 867.8291 |  | 3
65 | 80 | 59 | 27.7402 | 176396 | 146408.68 | 10.924 | 4500 | 433.1964 |  | 3
65 | 80 | 59 | 27.7402 | 178299 | 155120.13 | 10.983 | 5010 | 467.0085 |  | 3
65 | 80 | 59 | 27.7402 | 182913 | 166450.83 | 11.077 | 6000 | 867.8291 |  | 3
65 | 85 | 59 | 19.3387 | 179345 | 179345 | 10.951 | 4500 | 433.1964 |  | 3
65 | 85 | 59 | 19.3387 | 181247 | 181247 | 11.01 | 5010 | 467.0085 |  | 3
65 | 85 | 59 | 19.3387 | 185861 | 185861 | 11.104 | 6000 | 867.8291 |  | 3
65 | 80 | 63 | 39.1676 | 178868 | 135939.68 | 10.913 | 4500 | 433.1964 |  | 3
65 | 80 | 63 | 39.1676 | 180770 | 144616 | 10.971 | 5010 | 467.0085 |  | 3
65 | 80 | 63 | 39.1676 | 185384 | 155722.56 | 11.065 | 6000 | 867.8291 |  | 3
65 | 85 | 63 | 29.0563 | 181817 | 154544.45 | 10.94 | 4500 | 433.1964 |  | 3
65 | 85 | 63 | 29.0563 | 183719 | 165347.1 | 10.999 | 5010 | 467.0085 |  | 3
65 | 85 | 63 | 29.0563 | 188333 | 177033.02 | 11.093 | 6000 | 867.8291 |  | 3
65 | 80 | 67 | 51.5724 | 184096 | 115980.48 | 10.888 | 4500 | 433.1964 |  | 3
65 | 80 | 67 | 51.5724 | 185998 | 124618.66 | 10.947 | 5010 | 467.0085 |  | 3
65 | 80 | 67 | 51.5724 | 190612 | 135334.52 | 11.041 | 6000 | 867.8291 |  | 3
65 | 85 | 67 | 39.6049 | 187044 | 134671.68 | 10.915 | 4500 | 433.1964 |  | 3
65 | 85 | 67 | 39.6049 | 188946 | 145488.42 | 10.974 | 5010 | 467.0085 |  | 3
65 | 85 | 67 | 39.6049 | 193560 | 156783.6 | 11.068 | 6000 | 867.8291 |  | 3
65 | 80 | 71 | 65.0618 | 192080 | 94119.2 | 10.997 | 4500 | 433.1964 |  | 3
65 | 80 | 71 | 65.0618 | 193983 | 104750.82 | 11.056 | 5010 | 467.0085 |  | 3
65 | 80 | 71 | 65.0618 | 198597 | 115186.26 | 11.15 | 6000 | 867.8291 |  | 3
65 | 85 | 71 | 51.076 | 195029 | 115067.11 | 11.024 | 4500 | 433.1964 |  | 3
65 | 85 | 71 | 51.076 | 196931 | 124066.53 | 11.083 | 5010 | 467.0085 |  | 3
65 | 85 | 71 | 51.076 | 201545 | 135035.15 | 11.177 | 6000 | 867.8291 |  | 3
75 | 80 | 59 | 27.7402 | 174830 | 145108.9 | 12.344 | 4500 | 433.1964 |  | 3
75 | 80 | 59 | 27.7402 | 176732 | 155524.16 | 12.403 | 5010 | 467.0085 |  | 3
75 | 80 | 59 | 27.7402 | 181346 | 181346 | 12.497 | 6000 | 867.8291 |  | 3
75 | 85 | 59 | 19.3387 | 177779 | 177779 | 12.371 | 4500 | 433.1964 |  | 3
75 | 85 | 59 | 19.3387 | 179681 | 179681 | 12.43 | 5010 | 467.0085 |  | 3
75 | 85 | 59 | 19.3387 | 184295 | 184295 | 12.524 | 6000 | 867.8291 |  | 3
75 | 80 | 63 | 39.1676 | 177302 | 134749.52 | 12.333 | 4500 | 433.1964 |  | 3
75 | 80 | 63 | 39.1676 | 179204 | 145155.24 | 12.392 | 5010 | 467.0085 |  | 3
75 | 80 | 63 | 39.1676 | 183818 | 156245.3 | 12.486 | 6000 | 867.8291 |  | 3
75 | 85 | 63 | 29.0563 | 180250 | 155015 | 12.36 | 4500 | 433.1964 |  | 3
75 | 85 | 63 | 29.0563 | 182152 | 163936.8 | 12.419 | 5010 | 467.0085 |  | 3
75 | 85 | 63 | 29.0563 | 186766 | 175560.04 | 12.513 | 6000 | 867.8291 |  | 3
75 | 80 | 67 | 51.5724 | 182529 | 114993.27 | 12.308 | 4500 | 433.1964 |  | 3
75 | 80 | 67 | 51.5724 | 184431 | 125413.08 | 12.367 | 5010 | 467.0085 |  | 3
75 | 80 | 67 | 51.5724 | 189045 | 136112.4 | 12.461 | 6000 | 867.8291 |  | 3
75 | 85 | 67 | 39.6049 | 185478 | 135398.94 | 12.336 | 4500 | 433.1964 |  | 3
75 | 85 | 67 | 39.6049 | 187380 | 144282.6 | 12.394 | 5010 | 467.0085 |  | 3
75 | 85 | 67 | 39.6049 | 191994 | 155515.14 | 12.489 | 6000 | 867.8291 |  | 3
75 | 80 | 71 | 65.0618 | 190514 | 95257 | 12.417 | 4500 | 433.1964 |  | 3
75 | 80 | 71 | 65.0618 | 192416 | 103904.64 | 12.476 | 5010 | 467.0085 |  | 3
75 | 80 | 71 | 65.0618 | 197030 | 114277.4 | 12.57 | 6000 | 867.8291 |  | 3
75 | 85 | 71 | 51.076 | 193463 | 114143.17 | 12.444 | 4500 | 433.1964 |  | 3
75 | 85 | 71 | 51.076 | 195365 | 125033.6 | 12.503 | 5010 | 467.0085 |  | 3
75 | 85 | 71 | 51.076 | 199979 | 135985.72 | 12.597 | 6000 | 867.8291 |  | 3
85 | 80 | 59 | 27.7402 | 170261 | 170261 | 13.929 | 4500 | 433.1964 |  | 3
85 | 80 | 59 | 27.7402 | 172163 | 172163 | 13.988 | 5010 | 467.0085 |  | 3
85 | 80 | 59 | 27.7402 | 176777 | 176777 | 14.082 | 6000 | 867.8291 |  | 3
85 | 85 | 59 | 19.3387 | 173209 | 173209 | 13.956 | 4500 | 433.1964 |  | 3
85 | 85 | 59 | 19.3387 | 175111 | 175111 | 14.015 | 5010 | 467.0085 |  | 3
85 | 85 | 59 | 19.3387 | 179725 | 179725 | 14.109 | 6000 | 867.8291 |  | 3
85 | 80 | 63 | 39.1676 | 172732 | 136458.28 | 13.918 | 4500 | 433.1964 |  | 3
85 | 80 | 63 | 39.1676 | 174634 | 144946.22 | 13.977 | 5010 | 467.0085 |  | 3
85 | 80 | 63 | 39.1676 | 179248 | 155945.76 | 14.071 | 6000 | 867.8291 |  | 3
85 | 85 | 63 | 29.0563 | 175681 | 154599.28 | 13.945 | 4500 | 433.1964 |  | 3
85 | 85 | 63 | 29.0563 | 177583 | 165152.19 | 14.004 | 5010 | 467.0085 |  | 3
85 | 85 | 63 | 29.0563 | 182197 | 176731.09 | 14.098 | 6000 | 867.8291 |  | 3
85 | 80 | 67 | 51.5724 | 177960 | 117453.6 | 13.894 | 4500 | 433.1964 |  | 3
85 | 80 | 67 | 51.5724 | 179862 | 125903.4 | 13.953 | 5010 | 467.0085 |  | 3
85 | 80 | 67 | 51.5724 | 184476 | 136512.24 | 14.047 | 6000 | 867.8291 |  | 3
85 | 85 | 67 | 39.6049 | 180908 | 135681 | 13.921 | 4500 | 433.1964 |  | 3
85 | 85 | 67 | 39.6049 | 182810 | 146248 | 13.98 | 5010 | 467.0085 |  | 3
85 | 85 | 67 | 39.6049 | 187424 | 157436.16 | 14.074 | 6000 | 867.8291 |  | 3
85 | 80 | 71 | 65.0618 | 185945 | 96691.4 | 14.002 | 4500 | 433.1964 |  | 3
85 | 80 | 71 | 65.0618 | 187847 | 107072.79 | 14.061 | 5010 | 467.0085 |  | 3
85 | 80 | 71 | 65.0618 | 192461 | 117401.21 | 14.155 | 6000 | 867.8291 |  | 3
85 | 85 | 71 | 51.076 | 188893 | 117113.66 | 14.03 | 4500 | 433.1964 |  | 3
85 | 85 | 71 | 51.076 | 190795 | 125924.7 | 14.088 | 5010 | 467.0085 |  | 3
85 | 85 | 71 | 51.076 | 195409 | 136786.3 | 14.182 | 6000 | 867.8291 |  | 3
95 | 80 | 59 | 27.7402 | 162399 | 162399 | 15.645 | 4500 | 433.1964 |  | 3
95 | 80 | 59 | 27.7402 | 164301 | 164301 | 15.704 | 5010 | 467.0085 |  | 3
95 | 80 | 59 | 27.7402 | 168915 | 168915 | 15.798 | 6000 | 867.8291 |  | 3
95 | 85 | 59 | 19.3387 | 165347 | 165347 | 15.672 | 4500 | 433.1964 |  | 3
95 | 85 | 59 | 19.3387 | 167249 | 167249 | 15.731 | 5010 | 467.0085 |  | 3
95 | 85 | 59 | 19.3387 | 171863 | 171863 | 15.825 | 6000 | 867.8291 |  | 3
95 | 80 | 63 | 39.1676 | 164870 | 131896 | 15.634 | 4500 | 433.1964 |  | 3
95 | 80 | 63 | 39.1676 | 166773 | 141757.05 | 15.692 | 5010 | 467.0085 |  | 3
95 | 80 | 63 | 39.1676 | 171387 | 152534.43 | 15.787 | 6000 | 867.8291 |  | 3
95 | 85 | 63 | 29.0563 | 167819 | 151037.1 | 15.661 | 4500 | 433.1964 |  | 3
95 | 85 | 63 | 29.0563 | 169721 | 159537.74 | 15.72 | 5010 | 467.0085 |  | 3
95 | 85 | 63 | 29.0563 | 174335 | 174335 | 15.814 | 6000 | 867.8291 |  | 3
95 | 80 | 67 | 51.5724 | 170098 | 115666.64 | 15.609 | 4500 | 433.1964 |  | 3
95 | 80 | 67 | 51.5724 | 172000 | 123840 | 15.668 | 5010 | 467.0085 |  | 3
95 | 80 | 67 | 51.5724 | 176614 | 134226.64 | 15.762 | 6000 | 867.8291 |  | 3
95 | 85 | 67 | 39.6049 | 173046 | 133245.42 | 15.637 | 4500 | 433.1964 |  | 3
95 | 85 | 67 | 39.6049 | 174949 | 143458.18 | 15.695 | 5010 | 467.0085 |  | 3
95 | 85 | 67 | 39.6049 | 179563 | 154424.18 | 15.789 | 6000 | 867.8291 |  | 3
95 | 80 | 71 | 65.0618 | 178083 | 96164.82 | 15.718 | 4500 | 433.1964 |  | 3
95 | 80 | 71 | 65.0618 | 179985 | 104391.3 | 15.777 | 5010 | 467.0085 |  | 3
95 | 80 | 71 | 65.0618 | 184599 | 116297.37 | 15.871 | 6000 | 867.8291 |  | 3
95 | 85 | 71 | 51.076 | 181031 | 115859.84 | 15.745 | 4500 | 433.1964 |  | 3
95 | 85 | 71 | 51.076 | 182933 | 124394.44 | 15.804 | 5010 | 467.0085 |  | 3
95 | 85 | 71 | 51.076 | 187547 | 135033.84 | 15.898 | 6000 | 867.8291 |  | 3
105 | 80 | 59 | 27.7402 | 152791 | 152791 | 17.562 | 4500 | 433.1964 |  | 3
105 | 80 | 59 | 27.7402 | 154693 | 154693 | 17.62 | 5010 | 467.0085 |  | 3
105 | 80 | 59 | 27.7402 | 159307 | 159307 | 17.715 | 6000 | 867.8291 |  | 3
105 | 85 | 59 | 19.3387 | 155739 | 155739 | 17.589 | 4500 | 433.1964 |  | 3
105 | 85 | 59 | 19.3387 | 157641 | 157641 | 17.648 | 5010 | 467.0085 |  | 3
105 | 85 | 59 | 19.3387 | 162255 | 162255 | 17.742 | 6000 | 867.8291 |  | 3
105 | 80 | 63 | 39.1676 | 155262 | 128867.46 | 17.55 | 4500 | 433.1964 |  | 3
105 | 80 | 63 | 39.1676 | 157164 | 136732.68 | 17.609 | 5010 | 467.0085 |  | 3
105 | 80 | 63 | 39.1676 | 161778 | 147217.98 | 17.703 | 6000 | 867.8291 |  | 3
105 | 85 | 63 | 29.0563 | 158211 | 158211 | 17.578 | 4500 | 433.1964 |  | 3
105 | 85 | 63 | 29.0563 | 160113 | 160113 | 17.636 | 5010 | 467.0085 |  | 3
105 | 85 | 63 | 29.0563 | 164727 | 164727 | 17.73 | 6000 | 867.8291 |  | 3
105 | 80 | 67 | 51.5724 | 160490 | 112343 | 17.526 | 4500 | 433.1964 |  | 3
105 | 80 | 67 | 51.5724 | 162392 | 120170.08 | 17.585 | 5010 | 467.0085 |  | 3
105 | 80 | 67 | 51.5724 | 167006 | 130264.68 | 17.679 | 6000 | 867.8291 |  | 3
105 | 85 | 67 | 39.6049 | 163438 | 129116.02 | 17.553 | 4500 | 433.1964 |  | 3
105 | 85 | 67 | 39.6049 | 165340 | 138885.6 | 17.612 | 5010 | 467.0085 |  | 3
105 | 85 | 67 | 39.6049 | 169954 | 149559.52 | 17.706 | 6000 | 867.8291 |  | 3
105 | 80 | 71 | 65.0618 | 168475 | 94346 | 17.635 | 4500 | 433.1964 |  | 3
105 | 80 | 71 | 65.0618 | 170377 | 103929.97 | 17.694 | 5010 | 467.0085 |  | 3
105 | 80 | 71 | 65.0618 | 174991 | 113744.15 | 17.788 | 6000 | 867.8291 |  | 3
105 | 85 | 71 | 51.076 | 171423 | 113139.18 | 17.662 | 4500 | 433.1964 |  | 3
105 | 85 | 71 | 51.076 | 173325 | 121327.5 | 17.721 | 5010 | 467.0085 |  | 3
105 | 85 | 71 | 51.076 | 177939 | 131674.86 | 17.815 | 6000 | 867.8291 |  | 3
115 | 80 | 59 | 27.7402 | 144019 | 144019 | 19.81 | 4500 | 433.1964 |  | 3
115 | 80 | 59 | 27.7402 | 145921 | 145921 | 19.869 | 5010 | 467.0085 |  | 3
115 | 80 | 59 | 27.7402 | 150535 | 150535 | 19.963 | 6000 | 867.8291 |  | 3
115 | 85 | 59 | 19.3387 | 146968 | 146968 | 19.838 | 4500 | 433.1964 |  | 3
115 | 85 | 59 | 19.3387 | 148870 | 148870 | 19.896 | 5010 | 467.0085 |  | 3
115 | 85 | 59 | 19.3387 | 153484 | 153484 | 19.99 | 6000 | 867.8291 |  | 3
115 | 80 | 63 | 39.1676 | 146491 | 127447.17 | 19.799 | 4500 | 433.1964 |  | 3
115 | 80 | 63 | 39.1676 | 148393 | 136521.56 | 19.858 | 5010 | 467.0085 |  | 3
115 | 80 | 63 | 39.1676 | 153007 | 153007 | 19.952 | 6000 | 867.8291 |  | 3
115 | 85 | 63 | 29.0563 | 149439 | 149439 | 19.826 | 4500 | 433.1964 |  | 3
115 | 85 | 63 | 29.0563 | 151342 | 151342 | 19.885 | 5010 | 467.0085 |  | 3
115 | 85 | 63 | 29.0563 | 155956 | 155956 | 19.979 | 6000 | 867.8291 |  | 3
115 | 80 | 67 | 51.5724 | 151718 | 113788.5 | 19.775 | 4500 | 433.1964 |  | 3
115 | 80 | 67 | 51.5724 | 153621 | 121360.59 | 19.834 | 5010 | 467.0085 |  | 3
115 | 80 | 67 | 51.5724 | 158235 | 131335.05 | 19.928 | 6000 | 867.8291 |  | 3
115 | 85 | 67 | 39.6049 | 154667 | 129920.28 | 19.802 | 4500 | 433.1964 |  | 3
115 | 85 | 67 | 39.6049 | 156569 | 138720.13 | 19.861 | 5010 | 467.0085 |  | 3
115 | 85 | 67 | 39.6049 | 161183 | 149900.19 | 19.955 | 6000 | 867.8291 |  | 3
115 | 80 | 71 | 65.0618 | 159703 | 97418.83 | 19.884 | 4500 | 433.1964 |  | 3
115 | 80 | 71 | 65.0618 | 161606 | 105043.9 | 19.942 | 5010 | 467.0085 |  | 3
115 | 80 | 71 | 65.0618 | 166219 | 116353.3 | 20.037 | 6000 | 867.8291 |  | 3
115 | 85 | 71 | 51.076 | 162652 | 115482.92 | 19.911 | 4500 | 433.1964 |  | 3
115 | 85 | 71 | 51.076 | 164554 | 123415.5 | 19.97 | 5010 | 467.0085 |  | 3
115 | 85 | 71 | 51.076 | 169168 | 133642.72 | 20.064 | 6000 | 867.8291 |  | 3
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 7
Degradation Coefficient (C_d)
IEER or SEER | 14.2
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 70 | 59 | 52.7218 | 235203 | 141121.8 | 15.161 | 6000 | 717.685 |  | 4
65 | 70 | 59 | 52.7218 | 237074 | 149356.62 | 15.212 | 6475 | 848.7154 |  | 4
65 | 70 | 59 | 52.7218 | 244645 | 163912.15 | 15.347 | 8000 | 1400.3128 |  | 4
65 | 75 | 59 | 38.6294 | 235340 | 169444.8 | 15.15 | 6000 | 717.685 |  | 4
65 | 75 | 59 | 38.6294 | 237210 | 177907.5 | 15.2 | 6475 | 848.7154 |  | 4
65 | 75 | 59 | 38.6294 | 244781 | 195824.8 | 15.336 | 8000 | 1400.3128 |  | 4
65 | 70 | 63 | 68.6866 | 238509 | 126409.77 | 15.147 | 6000 | 717.685 |  | 4
65 | 70 | 63 | 68.6866 | 240379 | 134612.24 | 15.198 | 6475 | 848.7154 |  | 4
65 | 70 | 63 | 68.6866 | 247950 | 148770 | 15.333 | 8000 | 1400.3128 |  | 4
65 | 75 | 63 | 52.1129 | 238645 | 155119.25 | 15.136 | 6000 | 717.685 |  | 4
65 | 75 | 63 | 52.1129 | 240515 | 163550.2 | 15.187 | 6475 | 848.7154 |  | 4
65 | 75 | 63 | 52.1129 | 248086 | 178621.92 | 15.322 | 8000 | 1400.3128 |  | 4
65 | 70 | 67 | 86.0167 | 245499 | 98199.6 | 15.117 | 6000 | 717.685 |  | 4
65 | 70 | 67 | 86.0167 | 247369 | 106368.67 | 15.168 | 6475 | 848.7154 |  | 4
65 | 70 | 67 | 86.0167 | 254940 | 119821.8 | 15.303 | 8000 | 1400.3128 |  | 4
65 | 75 | 67 | 66.7494 | 245635 | 127730.2 | 15.106 | 6000 | 717.685 |  | 4
65 | 75 | 67 | 66.7494 | 247505 | 136127.75 | 15.157 | 6475 | 848.7154 |  | 4
65 | 75 | 67 | 66.7494 | 255076 | 153045.6 | 15.292 | 8000 | 1400.3128 |  | 4
65 | 75 | 71 | 82.6659 | 256313 | 99962.07 | 15.239 | 6000 | 717.685 |  | 4
65 | 75 | 71 | 82.6659 | 258183 | 108436.86 | 15.29 | 6475 | 848.7154 |  | 4
65 | 75 | 71 | 82.6659 | 265754 | 122246.84 | 15.425 | 8000 | 1400.3128 |  | 4
75 | 70 | 59 | 52.7218 | 233109 | 142196.49 | 16.903 | 6000 | 717.685 |  | 4
75 | 70 | 59 | 52.7218 | 234979 | 150386.56 | 16.954 | 6475 | 848.7154 |  | 4
75 | 70 | 59 | 52.7218 | 242550 | 164934 | 17.089 | 8000 | 1400.3128 |  | 4
75 | 75 | 59 | 38.6294 | 233245 | 170268.85 | 16.892 | 6000 | 717.685 |  | 4
75 | 75 | 59 | 38.6294 | 235115 | 178687.4 | 16.942 | 6475 | 848.7154 |  | 4
75 | 75 | 59 | 38.6294 | 242686 | 194148.8 | 17.078 | 8000 | 1400.3128 |  | 4
75 | 70 | 63 | 68.6866 | 236414 | 127663.56 | 16.889 | 6000 | 717.685 |  | 4
75 | 70 | 63 | 68.6866 | 238284 | 135821.88 | 16.94 | 6475 | 848.7154 |  | 4
75 | 70 | 63 | 68.6866 | 245855 | 149971.55 | 17.075 | 8000 | 1400.3128 |  | 4
75 | 75 | 63 | 52.1129 | 236550 | 156123 | 16.878 | 6000 | 717.685 |  | 4
75 | 75 | 63 | 52.1129 | 238420 | 164509.8 | 16.929 | 6475 | 848.7154 |  | 4
75 | 75 | 63 | 52.1129 | 245991 | 179573.43 | 17.064 | 8000 | 1400.3128 |  | 4
75 | 70 | 67 | 86.0167 | 243404 | 99795.64 | 16.859 | 6000 | 717.685 |  | 4
75 | 70 | 67 | 86.0167 | 245274 | 107920.56 | 16.91 | 6475 | 848.7154 |  | 4
75 | 70 | 67 | 86.0167 | 252845 | 121365.6 | 17.045 | 8000 | 1400.3128 |  | 4
75 | 75 | 67 | 66.7494 | 243541 | 129076.73 | 16.848 | 6000 | 717.685 |  | 4
75 | 75 | 67 | 66.7494 | 245411 | 137430.16 | 16.899 | 6475 | 848.7154 |  | 4
75 | 75 | 67 | 66.7494 | 252982 | 151789.2 | 17.034 | 8000 | 1400.3128 |  | 4
75 | 75 | 71 | 82.6659 | 254218 | 99145.02 | 16.981 | 6000 | 717.685 |  | 4
75 | 75 | 71 | 82.6659 | 256088 | 107556.96 | 17.032 | 6475 | 848.7154 |  | 4
75 | 75 | 71 | 82.6659 | 263659 | 123919.73 | 17.167 | 8000 | 1400.3128 |  | 4
85 | 70 | 59 | 52.7218 | 226999 | 143009.37 | 18.848 | 6000 | 717.685 |  | 4
85 | 70 | 59 | 52.7218 | 228869 | 151053.54 | 18.898 | 6475 | 848.7154 |  | 4
85 | 70 | 59 | 52.7218 | 236440 | 165508 | 19.034 | 8000 | 1400.3128 |  | 4
85 | 75 | 59 | 38.6294 | 227135 | 227135 | 18.836 | 6000 | 717.685 |  | 4
85 | 75 | 59 | 38.6294 | 229005 | 229005 | 18.887 | 6475 | 848.7154 |  | 4
85 | 75 | 59 | 38.6294 | 236576 | 236576 | 19.022 | 8000 | 1400.3128 |  | 4
85 | 70 | 63 | 68.6866 | 230304 | 128970.24 | 18.834 | 6000 | 717.685 |  | 4
85 | 70 | 63 | 68.6866 | 232174 | 136982.66 | 18.885 | 6475 | 848.7154 |  | 4
85 | 70 | 63 | 68.6866 | 239745 | 151039.35 | 19.02 | 8000 | 1400.3128 |  | 4
85 | 75 | 63 | 52.1129 | 230440 | 156699.2 | 18.823 | 6000 | 717.685 |  | 4
85 | 75 | 63 | 52.1129 | 232310 | 164940.1 | 18.873 | 6475 | 848.7154 |  | 4
85 | 75 | 63 | 52.1129 | 239881 | 179910.75 | 19.009 | 8000 | 1400.3128 |  | 4
85 | 70 | 67 | 86.0167 | 237294 | 102036.42 | 18.804 | 6000 | 717.685 |  | 4
85 | 70 | 67 | 86.0167 | 239164 | 110015.44 | 18.855 | 6475 | 848.7154 |  | 4
85 | 70 | 67 | 86.0167 | 246735 | 123367.5 | 18.99 | 8000 | 1400.3128 |  | 4
85 | 75 | 67 | 66.7494 | 237430 | 130586.5 | 18.793 | 6000 | 717.685 |  | 4
85 | 75 | 67 | 66.7494 | 239300 | 138794 | 18.844 | 6475 | 848.7154 |  | 4
85 | 75 | 67 | 66.7494 | 246871 | 155528.73 | 18.979 | 8000 | 1400.3128 |  | 4
85 | 75 | 71 | 82.6659 | 248108 | 104205.36 | 18.926 | 6000 | 717.685 |  | 4
85 | 75 | 71 | 82.6659 | 249978 | 112490.1 | 18.977 | 6475 | 848.7154 |  | 4
85 | 75 | 71 | 82.6659 | 257549 | 126199.01 | 19.112 | 8000 | 1400.3128 |  | 4
95 | 70 | 59 | 52.7218 | 216486 | 140715.9 | 20.952 | 6000 | 717.685 |  | 4
95 | 70 | 59 | 52.7218 | 218356 | 148482.08 | 21.003 | 6475 | 848.7154 |  | 4
95 | 70 | 59 | 52.7218 | 225927 | 225927 | 21.138 | 8000 | 1400.3128 |  | 4
95 | 75 | 59 | 38.6294 | 216622 | 216622 | 20.941 | 6000 | 717.685 |  | 4
95 | 75 | 59 | 38.6294 | 218492 | 218492 | 20.992 | 6475 | 848.7154 |  | 4
95 | 75 | 59 | 38.6294 | 226063 | 226063 | 21.127 | 8000 | 1400.3128 |  | 4
95 | 70 | 63 | 68.6866 | 219791 | 127478.78 | 20.938 | 6000 | 717.685 |  | 4
95 | 70 | 63 | 68.6866 | 221661 | 135213.21 | 20.989 | 6475 | 848.7154 |  | 4
95 | 70 | 63 | 68.6866 | 229232 | 149000.8 | 21.124 | 8000 | 1400.3128 |  | 4
95 | 75 | 63 | 52.1129 | 219927 | 153948.9 | 20.927 | 6000 | 717.685 |  | 4
95 | 75 | 63 | 52.1129 | 221797 | 161911.81 | 20.978 | 6475 | 848.7154 |  | 4
95 | 75 | 63 | 52.1129 | 229368 | 176613.36 | 21.113 | 8000 | 1400.3128 |  | 4
95 | 70 | 67 | 86.0167 | 226781 | 102051.45 | 20.909 | 6000 | 717.685 |  | 4
95 | 70 | 67 | 86.0167 | 228651 | 109752.48 | 20.959 | 6475 | 848.7154 |  | 4
95 | 70 | 67 | 86.0167 | 236222 | 122835.44 | 21.095 | 8000 | 1400.3128 |  | 4
95 | 75 | 67 | 66.7494 | 226917 | 129342.69 | 20.897 | 6000 | 717.685 |  | 4
95 | 75 | 67 | 66.7494 | 228787 | 137272.2 | 20.948 | 6475 | 848.7154 |  | 4
95 | 75 | 67 | 66.7494 | 236359 | 151269.76 | 21.083 | 8000 | 1400.3128 |  | 4
95 | 75 | 71 | 82.6659 | 237595 | 104541.8 | 21.031 | 6000 | 717.685 |  | 4
95 | 75 | 71 | 82.6659 | 239465 | 112548.55 | 21.081 | 6475 | 848.7154 |  | 4
95 | 75 | 71 | 82.6659 | 247036 | 125988.36 | 21.217 | 8000 | 1400.3128 |  | 4
105 | 70 | 59 | 52.7218 | 203638 | 203638 | 23.303 | 6000 | 588.334 |  | 4
105 | 70 | 59 | 52.7218 | 205508 | 205508 | 23.354 | 6475 | 773.3623 |  | 4
105 | 70 | 59 | 52.7218 | 213079 | 213079 | 23.489 | 8000 | 1400.3128 |  | 4
105 | 75 | 59 | 38.6294 | 203774 | 203774 | 23.292 | 6000 | 588.334 |  | 4
105 | 75 | 59 | 38.6294 | 205644 | 205644 | 23.343 | 6475 | 773.3623 |  | 4
105 | 75 | 59 | 38.6294 | 213215 | 213215 | 23.478 | 8000 | 1400.3128 |  | 4
105 | 70 | 63 | 68.6866 | 206943 | 124165.8 | 23.29 | 6000 | 588.334 |  | 4
105 | 70 | 63 | 68.6866 | 208813 | 131552.19 | 23.34 | 6475 | 773.3623 |  | 4
105 | 70 | 63 | 68.6866 | 216384 | 144977.28 | 23.476 | 8000 | 1400.3128 |  | 4
105 | 75 | 63 | 52.1129 | 207079 | 149096.88 | 23.278 | 6000 | 588.334 |  | 4
105 | 75 | 63 | 52.1129 | 208949 | 156711.75 | 23.329 | 6475 | 773.3623 |  | 4
105 | 75 | 63 | 52.1129 | 216520 | 171050.8 | 23.464 | 8000 | 1400.3128 |  | 4
105 | 70 | 67 | 86.0167 | 213933 | 100548.51 | 23.26 | 6000 | 717.685 |  | 4
105 | 70 | 67 | 86.0167 | 215803 | 107901.5 | 23.311 | 6475 | 848.7154 |  | 4
105 | 70 | 67 | 86.0167 | 223374 | 120621.96 | 23.446 | 8000 | 1400.3128 |  | 4
105 | 75 | 67 | 66.7494 | 214069 | 126300.71 | 23.249 | 6000 | 717.685 |  | 4
105 | 75 | 67 | 66.7494 | 215939 | 133882.18 | 23.299 | 6475 | 848.7154 |  | 4
105 | 75 | 67 | 66.7494 | 223511 | 147517.26 | 23.435 | 8000 | 1400.3128 |  | 4
105 | 75 | 71 | 82.6659 | 224747 | 103383.62 | 23.382 | 6000 | 717.685 |  | 4
105 | 75 | 71 | 82.6659 | 226617 | 111042.33 | 23.433 | 6475 | 848.7154 |  | 4
105 | 75 | 71 | 82.6659 | 234188 | 124119.64 | 23.568 | 8000 | 1400.3128 |  | 4
115 | 70 | 59 | 52.7218 | 191909 | 191909 | 26.062 | 6000 | 588.334 |  | 4
115 | 70 | 59 | 52.7218 | 193779 | 193779 | 26.113 | 6475 | 773.3623 |  | 4
115 | 70 | 59 | 52.7218 | 201350 | 201350 | 26.248 | 8000 | 1381.5587 |  | 4
115 | 75 | 59 | 38.6294 | 192045 | 192045 | 26.051 | 6000 | 588.334 |  | 4
115 | 75 | 59 | 38.6294 | 193915 | 193915 | 26.101 | 6475 | 773.3623 |  | 4
115 | 75 | 59 | 38.6294 | 201486 | 201486 | 26.237 | 8000 | 1381.5587 |  | 4
115 | 70 | 63 | 68.6866 | 195214 | 126889.1 | 26.048 | 6000 | 588.334 |  | 4
115 | 70 | 63 | 68.6866 | 197084 | 134017.12 | 26.099 | 6475 | 773.3623 |  | 4
115 | 70 | 63 | 68.6866 | 204655 | 147351.6 | 26.234 | 8000 | 1381.5587 |  | 4
115 | 75 | 63 | 52.1129 | 195350 | 150419.5 | 26.037 | 6000 | 588.334 |  | 4
115 | 75 | 63 | 52.1129 | 197220 | 157776 | 26.088 | 6475 | 773.3623 |  | 4
115 | 75 | 63 | 52.1129 | 204791 | 204791 | 26.223 | 8000 | 1381.5587 |  | 4
115 | 70 | 67 | 86.0167 | 202204 | 105146.08 | 26.018 | 6000 | 588.334 |  | 4
115 | 70 | 67 | 86.0167 | 204074 | 112240.7 | 26.069 | 6475 | 773.3623 |  | 4
115 | 70 | 67 | 86.0167 | 211645 | 124870.55 | 26.204 | 8000 | 1400.3128 |  | 4
115 | 75 | 67 | 66.7494 | 202340 | 129497.6 | 26.007 | 6000 | 588.334 |  | 4
115 | 75 | 67 | 66.7494 | 204210 | 136820.7 | 26.058 | 6475 | 773.3623 |  | 4
115 | 75 | 67 | 66.7494 | 211781 | 150364.51 | 26.193 | 8000 | 1400.3128 |  | 4
115 | 75 | 71 | 82.6659 | 213018 | 108639.18 | 26.14 | 6000 | 717.685 |  | 4
115 | 75 | 71 | 82.6659 | 214888 | 116039.52 | 26.191 | 6475 | 848.7154 |  | 4
115 | 75 | 71 | 82.6659 | 222459 | 129026.22 | 26.326 | 8000 | 1400.3128 |  | 4
65 | 80 | 59 | 27.7402 | 236552 | 198703.68 | 15.159 | 6000 | 717.685 |  | 4
65 | 80 | 59 | 27.7402 | 238422 | 207427.14 | 15.209 | 6475 | 848.7154 |  | 4
65 | 80 | 59 | 27.7402 | 245993 | 245993 | 15.345 | 8000 | 1400.3128 |  | 4
65 | 85 | 59 | 19.3387 | 240495 | 240495 | 15.192 | 6000 | 717.685 |  | 4
65 | 85 | 59 | 19.3387 | 242365 | 242365 | 15.243 | 6475 | 848.7154 |  | 4
65 | 85 | 59 | 19.3387 | 249936 | 249936 | 15.378 | 8000 | 1400.3128 |  | 4
65 | 80 | 63 | 39.1676 | 239857 | 184689.89 | 15.145 | 6000 | 717.685 |  | 4
65 | 80 | 63 | 39.1676 | 241727 | 193381.6 | 15.196 | 6475 | 848.7154 |  | 4
65 | 80 | 63 | 39.1676 | 249298 | 209410.32 | 15.331 | 8000 | 1400.3128 |  | 4
65 | 85 | 63 | 29.0563 | 243800 | 212106 | 15.178 | 6000 | 717.685 |  | 4
65 | 85 | 63 | 29.0563 | 245670 | 221103 | 15.229 | 6475 | 848.7154 |  | 4
65 | 85 | 63 | 29.0563 | 253241 | 238046.54 | 15.364 | 8000 | 1400.3128 |  | 4
65 | 80 | 67 | 51.5724 | 246847 | 157982.08 | 15.115 | 6000 | 717.685 |  | 4
65 | 80 | 67 | 51.5724 | 248717 | 166640.39 | 15.166 | 6475 | 848.7154 |  | 4
65 | 80 | 67 | 51.5724 | 256289 | 181965.19 | 15.301 | 8000 | 1400.3128 |  | 4
65 | 85 | 67 | 39.6049 | 250790 | 185584.6 | 15.149 | 6000 | 717.685 |  | 4
65 | 85 | 67 | 39.6049 | 252660 | 194548.2 | 15.199 | 6475 | 848.7154 |  | 4
65 | 85 | 67 | 39.6049 | 260231 | 210787.11 | 15.335 | 8000 | 1400.3128 |  | 4
65 | 80 | 71 | 65.0618 | 257525 | 131337.75 | 15.248 | 6000 | 717.685 |  | 4
65 | 80 | 71 | 65.0618 | 259395 | 140073.3 | 15.299 | 6475 | 848.7154 |  | 4
65 | 80 | 71 | 65.0618 | 266966 | 154840.28 | 15.434 | 8000 | 1400.3128 |  | 4
65 | 85 | 71 | 51.076 | 261468 | 156880.8 | 15.282 | 6000 | 717.685 |  | 4
65 | 85 | 71 | 51.076 | 263338 | 165902.94 | 15.333 | 6475 | 848.7154 |  | 4
65 | 85 | 71 | 51.076 | 270909 | 184218.12 | 15.468 | 8000 | 1400.3128 |  | 4
75 | 80 | 59 | 27.7402 | 234457 | 234457 | 16.901 | 6000 | 717.685 |  | 4
75 | 80 | 59 | 27.7402 | 236328 | 236328 | 16.952 | 6475 | 848.7154 |  | 4
75 | 80 | 59 | 27.7402 | 243899 | 243899 | 17.087 | 8000 | 1400.3128 |  | 4
75 | 85 | 59 | 19.3387 | 238400 | 238400 | 16.934 | 6000 | 717.685 |  | 4
75 | 85 | 59 | 19.3387 | 240270 | 240270 | 16.985 | 6475 | 848.7154 |  | 4
75 | 85 | 59 | 19.3387 | 247841 | 247841 | 17.12 | 8000 | 1400.3128 |  | 4
75 | 80 | 63 | 39.1676 | 237763 | 185455.14 | 16.887 | 6000 | 717.685 |  | 4
75 | 80 | 63 | 39.1676 | 239633 | 194102.73 | 16.938 | 6475 | 848.7154 |  | 4
75 | 80 | 63 | 39.1676 | 247204 | 210123.4 | 17.073 | 8000 | 1400.3128 |  | 4
75 | 85 | 63 | 29.0563 | 241705 | 210283.35 | 16.92 | 6000 | 717.685 |  | 4
75 | 85 | 63 | 29.0563 | 243575 | 219217.5 | 16.971 | 6475 | 848.7154 |  | 4
75 | 85 | 63 | 29.0563 | 251147 | 251147 | 17.106 | 8000 | 1400.3128 |  | 4
75 | 80 | 67 | 51.5724 | 244753 | 159089.45 | 16.857 | 6000 | 717.685 |  | 4
75 | 80 | 67 | 51.5724 | 246623 | 167703.64 | 16.908 | 6475 | 848.7154 |  | 4
75 | 80 | 67 | 51.5724 | 254194 | 183019.68 | 17.043 | 8000 | 1400.3128 |  | 4
75 | 85 | 67 | 39.6049 | 248696 | 184035.04 | 16.891 | 6000 | 717.685 |  | 4
75 | 85 | 67 | 39.6049 | 250566 | 192935.82 | 16.941 | 6475 | 848.7154 |  | 4
75 | 85 | 67 | 39.6049 | 258137 | 211672.34 | 17.077 | 8000 | 1400.3128 |  | 4
75 | 80 | 71 | 65.0618 | 255430 | 130269.3 | 16.991 | 6000 | 717.685 |  | 4
75 | 80 | 71 | 65.0618 | 257300 | 138942 | 17.041 | 6475 | 848.7154 |  | 4
75 | 80 | 71 | 65.0618 | 264871 | 156273.89 | 17.177 | 8000 | 1400.3128 |  | 4
75 | 85 | 71 | 51.076 | 259373 | 158217.53 | 17.024 | 6000 | 717.685 |  | 4
75 | 85 | 71 | 51.076 | 261243 | 167195.52 | 17.075 | 6475 | 848.7154 |  | 4
75 | 85 | 71 | 51.076 | 268814 | 182793.52 | 17.21 | 8000 | 1400.3128 |  | 4
85 | 80 | 59 | 27.7402 | 228347 | 228347 | 18.845 | 6000 | 717.685 |  | 4
85 | 80 | 59 | 27.7402 | 230217 | 230217 | 18.896 | 6475 | 848.7154 |  | 4
85 | 80 | 59 | 27.7402 | 237788 | 237788 | 19.031 | 8000 | 1400.3128 |  | 4
85 | 85 | 59 | 19.3387 | 232290 | 232290 | 18.879 | 6000 | 717.685 |  | 4
85 | 85 | 59 | 19.3387 | 234160 | 234160 | 18.93 | 6475 | 848.7154 |  | 4
85 | 85 | 59 | 19.3387 | 241731 | 241731 | 19.065 | 8000 | 1400.3128 |  | 4
85 | 80 | 63 | 39.1676 | 231652 | 185321.6 | 18.832 | 6000 | 717.685 |  | 4
85 | 80 | 63 | 39.1676 | 233522 | 193823.26 | 18.883 | 6475 | 848.7154 |  | 4
85 | 80 | 63 | 39.1676 | 241093 | 209750.91 | 19.018 | 8000 | 1400.3128 |  | 4
85 | 85 | 63 | 29.0563 | 235595 | 235595 | 18.865 | 6000 | 717.685 |  | 4
85 | 85 | 63 | 29.0563 | 237465 | 237465 | 18.916 | 6475 | 848.7154 |  | 4
85 | 85 | 63 | 29.0563 | 245036 | 245036 | 19.051 | 8000 | 1400.3128 |  | 4
85 | 80 | 67 | 51.5724 | 238642 | 159890.14 | 18.802 | 6000 | 717.685 |  | 4
85 | 80 | 67 | 51.5724 | 240512 | 168358.4 | 18.853 | 6475 | 848.7154 |  | 4
85 | 80 | 67 | 51.5724 | 248084 | 183582.16 | 18.988 | 8000 | 1400.3128 |  | 4
85 | 85 | 67 | 39.6049 | 242585 | 186790.45 | 18.835 | 6000 | 717.685 |  | 4
85 | 85 | 67 | 39.6049 | 244455 | 195564 | 18.886 | 6475 | 848.7154 |  | 4
85 | 85 | 67 | 39.6049 | 252026 | 211701.84 | 19.021 | 8000 | 1400.3128 |  | 4
85 | 80 | 71 | 65.0618 | 249320 | 134632.8 | 18.935 | 6000 | 717.685 |  | 4
85 | 80 | 71 | 65.0618 | 251190 | 143178.3 | 18.986 | 6475 | 848.7154 |  | 4
85 | 80 | 71 | 65.0618 | 258761 | 157844.21 | 19.121 | 8000 | 1400.3128 |  | 4
85 | 85 | 71 | 51.076 | 253263 | 159555.69 | 18.969 | 6000 | 717.685 |  | 4
85 | 85 | 71 | 51.076 | 255133 | 168387.78 | 19.019 | 6475 | 848.7154 |  | 4
85 | 85 | 71 | 51.076 | 262704 | 183892.8 | 19.155 | 8000 | 1400.3128 |  | 4
95 | 80 | 59 | 27.7402 | 217834 | 217834 | 20.95 | 6000 | 717.685 |  | 4
95 | 80 | 59 | 27.7402 | 219704 | 219704 | 21.001 | 6475 | 848.7154 |  | 4
95 | 80 | 59 | 27.7402 | 227276 | 227276 | 21.136 | 8000 | 1400.3128 |  | 4
95 | 85 | 59 | 19.3387 | 221777 | 221777 | 20.983 | 6000 | 717.685 |  | 4
95 | 85 | 59 | 19.3387 | 223647 | 223647 | 21.034 | 6475 | 848.7154 |  | 4
95 | 85 | 59 | 19.3387 | 231218 | 231218 | 21.169 | 8000 | 1400.3128 |  | 4
95 | 80 | 63 | 39.1676 | 221139 | 181333.98 | 20.936 | 6000 | 717.685 |  | 4
95 | 80 | 63 | 39.1676 | 223009 | 189557.65 | 20.987 | 6475 | 848.7154 |  | 4
95 | 80 | 63 | 39.1676 | 230581 | 230581 | 21.122 | 8000 | 1400.3128 |  | 4
95 | 85 | 63 | 29.0563 | 225082 | 225082 | 20.97 | 6000 | 717.685 |  | 4
95 | 85 | 63 | 29.0563 | 226952 | 226952 | 21.02 | 6475 | 848.7154 |  | 4
95 | 85 | 63 | 29.0563 | 234523 | 234523 | 21.156 | 8000 | 1400.3128 |  | 4
95 | 80 | 67 | 51.5724 | 228130 | 157409.7 | 20.906 | 6000 | 717.685 |  | 4
95 | 80 | 67 | 51.5724 | 230000 | 165600 | 20.957 | 6475 | 848.7154 |  | 4
95 | 80 | 67 | 51.5724 | 237571 | 180553.96 | 21.092 | 8000 | 1400.3128 |  | 4
95 | 85 | 67 | 39.6049 | 232072 | 183336.88 | 20.94 | 6000 | 717.685 |  | 4
95 | 85 | 67 | 39.6049 | 233942 | 191832.44 | 20.991 | 6475 | 848.7154 |  | 4
95 | 85 | 67 | 39.6049 | 241514 | 207702.04 | 21.126 | 8000 | 1400.3128 |  | 4
95 | 80 | 71 | 65.0618 | 238807 | 131343.85 | 21.04 | 6000 | 717.685 |  | 4
95 | 80 | 71 | 65.0618 | 240677 | 139592.66 | 21.09 | 6475 | 848.7154 |  | 4
95 | 80 | 71 | 65.0618 | 248248 | 156396.24 | 21.226 | 8000 | 1400.3128 |  | 4
95 | 85 | 71 | 51.076 | 242750 | 157787.5 | 21.073 | 6000 | 717.685 |  | 4
95 | 85 | 71 | 51.076 | 244620 | 166341.6 | 21.124 | 6475 | 848.7154 |  | 4
95 | 85 | 71 | 51.076 | 252191 | 181577.52 | 21.259 | 8000 | 1400.3128 |  | 4
105 | 80 | 59 | 27.7402 | 204986 | 204986 | 23.301 | 6000 | 588.334 |  | 4
105 | 80 | 59 | 27.7402 | 206856 | 206856 | 23.352 | 6475 | 773.3623 |  | 4
105 | 80 | 59 | 27.7402 | 214428 | 214428 | 23.487 | 8000 | 1400.3128 |  | 4
105 | 85 | 59 | 19.3387 | 208929 | 208929 | 23.335 | 6000 | 588.334 |  | 4
105 | 85 | 59 | 19.3387 | 210799 | 210799 | 23.385 | 6475 | 773.3623 |  | 4
105 | 85 | 59 | 19.3387 | 218370 | 218370 | 23.521 | 8000 | 1400.3128 |  | 4
105 | 80 | 63 | 39.1676 | 208291 | 208291 | 23.287 | 6000 | 588.334 |  | 4
105 | 80 | 63 | 39.1676 | 210161 | 210161 | 23.338 | 6475 | 773.3623 |  | 4
105 | 80 | 63 | 39.1676 | 217733 | 217733 | 23.473 | 8000 | 1400.3128 |  | 4
105 | 85 | 63 | 29.0563 | 212234 | 212234 | 23.321 | 6000 | 717.685 |  | 4
105 | 85 | 63 | 29.0563 | 214104 | 214104 | 23.372 | 6475 | 848.7154 |  | 4
105 | 85 | 63 | 29.0563 | 221675 | 221675 | 23.507 | 8000 | 1400.3128 |  | 4
105 | 80 | 67 | 51.5724 | 215282 | 152850.22 | 23.258 | 6000 | 717.685 |  | 4
105 | 80 | 67 | 51.5724 | 217152 | 160692.48 | 23.308 | 6475 | 848.7154 |  | 4
105 | 80 | 67 | 51.5724 | 224723 | 175283.94 | 23.444 | 8000 | 1400.3128 |  | 4
105 | 85 | 67 | 39.6049 | 219224 | 177571.44 | 23.291 | 6000 | 717.685 |  | 4
105 | 85 | 67 | 39.6049 | 221094 | 185718.96 | 23.342 | 6475 | 848.7154 |  | 4
105 | 85 | 67 | 39.6049 | 228666 | 201226.08 | 23.477 | 8000 | 1400.3128 |  | 4
105 | 80 | 71 | 65.0618 | 225959 | 131056.22 | 23.391 | 6000 | 717.685 |  | 4
105 | 80 | 71 | 65.0618 | 227829 | 138975.69 | 23.442 | 6475 | 848.7154 |  | 4
105 | 80 | 71 | 65.0618 | 235400 | 153010 | 23.577 | 8000 | 1400.3128 |  | 4
105 | 85 | 71 | 51.076 | 229902 | 154034.34 | 23.424 | 6000 | 717.685 |  | 4
105 | 85 | 71 | 51.076 | 231772 | 162240.4 | 23.475 | 6475 | 848.7154 |  | 4
105 | 85 | 71 | 51.076 | 239343 | 177113.82 | 23.61 | 8000 | 1400.3128 |  | 4
115 | 80 | 59 | 27.7402 | 193257 | 193257 | 26.06 | 6000 | 588.334 |  | 4
115 | 80 | 59 | 27.7402 | 195127 | 195127 | 26.111 | 6475 | 773.3623 |  | 4
115 | 80 | 59 | 27.7402 | 202698 | 202698 | 26.246 | 8000 | 1381.5587 |  | 4
115 | 85 | 59 | 19.3387 | 197200 | 197200 | 26.093 | 6000 | 588.334 |  | 4
115 | 85 | 59 | 19.3387 | 199070 | 199070 | 26.144 | 6475 | 773.3623 |  | 4
115 | 85 | 59 | 19.3387 | 206641 | 206641 | 26.279 | 8000 | 1381.5587 |  | 4
115 | 80 | 63 | 39.1676 | 196562 | 196562 | 26.046 | 6000 | 588.334 |  | 4
115 | 80 | 63 | 39.1676 | 198432 | 198432 | 26.097 | 6475 | 773.3623 |  | 4
115 | 80 | 63 | 39.1676 | 206003 | 206003 | 26.232 | 8000 | 1381.5587 |  | 4
115 | 85 | 63 | 29.0563 | 200505 | 200505 | 26.079 | 6000 | 588.334 |  | 4
115 | 85 | 63 | 29.0563 | 202375 | 202375 | 26.13 | 6475 | 773.3623 |  | 4
115 | 85 | 63 | 29.0563 | 209946 | 209946 | 26.265 | 8000 | 1381.5587 |  | 4
115 | 80 | 67 | 51.5724 | 203552 | 154699.52 | 26.016 | 6000 | 588.334 |  | 4
115 | 80 | 67 | 51.5724 | 205423 | 162284.17 | 26.067 | 6475 | 773.3623 |  | 4
115 | 80 | 67 | 51.5724 | 212994 | 176785.02 | 26.202 | 8000 | 1400.3128 |  | 4
115 | 85 | 67 | 39.6049 | 207495 | 178445.7 | 26.05 | 6000 | 588.334 |  | 4
115 | 85 | 67 | 39.6049 | 209365 | 209365 | 26.1 | 6475 | 773.3623 |  | 4
115 | 85 | 67 | 39.6049 | 216936 | 216936 | 26.236 | 8000 | 1400.3128 |  | 4
115 | 80 | 71 | 65.0618 | 214230 | 132822.6 | 26.15 | 6000 | 717.685 |  | 4
115 | 80 | 71 | 65.0618 | 216100 | 140465 | 26.2 | 6475 | 848.7154 |  | 4
115 | 80 | 71 | 65.0618 | 223671 | 156569.7 | 26.336 | 8000 | 1400.3128 |  | 4
115 | 85 | 71 | 51.076 | 218173 | 157084.56 | 26.183 | 6000 | 717.685 |  | 4
115 | 85 | 71 | 51.076 | 220043 | 165032.25 | 26.234 | 6475 | 848.7154 |  | 4
115 | 85 | 71 | 51.076 | 227614 | 179815.06 | 26.369 | 8000 | 1400.3128 |  | 4
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 8
Degradation Coefficient (C_d)
IEER or SEER | 13
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 70 | 59 | 52.7218 | 296034 | 171699.72 | 21.453 | 7500 | 1034.8004 |  | 5
65 | 70 | 59 | 52.7218 | 298920 | 182341.2 | 21.538 | 8250 | 1380.5097 |  | 5
65 | 70 | 59 | 52.7218 | 307364 | 199786.6 | 21.702 | 10000 | 2507.4079 |  | 5
65 | 75 | 59 | 38.6294 | 296206 | 207344.2 | 21.438 | 7500 | 1034.8004 |  | 5
65 | 75 | 59 | 38.6294 | 299092 | 218337.16 | 21.523 | 8250 | 1380.5097 |  | 5
65 | 75 | 59 | 38.6294 | 307536 | 236802.72 | 21.687 | 10000 | 2507.4079 |  | 5
65 | 70 | 63 | 68.6866 | 300201 | 153102.51 | 21.434 | 7500 | 1034.8004 |  | 5
65 | 70 | 63 | 68.6866 | 303087 | 163666.98 | 21.52 | 8250 | 1380.5097 |  | 5
65 | 70 | 63 | 68.6866 | 311531 | 180687.98 | 21.684 | 10000 | 2507.4079 |  | 5
65 | 75 | 63 | 52.1129 | 300373 | 189234.99 | 21.419 | 7500 | 1034.8004 |  | 5
65 | 75 | 63 | 52.1129 | 303259 | 200150.94 | 21.505 | 8250 | 1380.5097 |  | 5
65 | 75 | 63 | 52.1129 | 311703 | 218192.1 | 21.669 | 10000 | 2507.4079 |  | 5
65 | 70 | 67 | 86.0167 | 309015 | 117425.7 | 21.395 | 7500 | 1034.8004 |  | 5
65 | 70 | 67 | 86.0167 | 311901 | 130998.42 | 21.48 | 8250 | 1380.5097 |  | 5
65 | 70 | 67 | 86.0167 | 320345 | 147358.7 | 21.644 | 10000 | 2507.4079 |  | 5
65 | 75 | 67 | 66.7494 | 309187 | 154593.5 | 21.38 | 7500 | 1034.8004 |  | 5
65 | 75 | 67 | 66.7494 | 312073 | 168519.42 | 21.465 | 8250 | 1380.5097 |  | 5
65 | 75 | 67 | 66.7494 | 320517 | 185899.86 | 21.629 | 10000 | 2507.4079 |  | 5
65 | 75 | 71 | 82.6659 | 322650 | 119380.5 | 21.557 | 7500 | 1034.8004 |  | 5
65 | 75 | 71 | 82.6659 | 325536 | 133469.76 | 21.643 | 8250 | 1380.5097 |  | 5
65 | 75 | 71 | 82.6659 | 333980 | 150291 | 21.807 | 10000 | 2507.4079 |  | 5
75 | 70 | 59 | 52.7218 | 293393 | 170167.94 | 23.779 | 7500 | 1034.8004 |  | 5
75 | 70 | 59 | 52.7218 | 296279 | 183692.98 | 23.864 | 8250 | 1380.5097 |  | 5
75 | 70 | 59 | 52.7218 | 304723 | 201117.18 | 24.028 | 10000 | 2507.4079 |  | 5
75 | 75 | 59 | 38.6294 | 293564 | 205494.8 | 23.764 | 7500 | 1034.8004 |  | 5
75 | 75 | 59 | 38.6294 | 296450 | 219373 | 23.849 | 8250 | 1380.5097 |  | 5
75 | 75 | 59 | 38.6294 | 304895 | 237818.1 | 24.013 | 10000 | 2507.4079 |  | 5
75 | 70 | 63 | 68.6866 | 297560 | 151755.6 | 23.761 | 7500 | 1034.8004 |  | 5
75 | 70 | 63 | 68.6866 | 300446 | 165245.3 | 23.846 | 8250 | 1380.5097 |  | 5
75 | 70 | 63 | 68.6866 | 308890 | 182245.1 | 24.01 | 10000 | 2507.4079 |  | 5
75 | 75 | 63 | 52.1129 | 297732 | 187571.16 | 23.746 | 7500 | 1034.8004 |  | 5
75 | 75 | 63 | 52.1129 | 300618 | 201414.06 | 23.831 | 8250 | 1380.5097 |  | 5
75 | 75 | 63 | 52.1129 | 309062 | 219434.02 | 23.995 | 10000 | 2507.4079 |  | 5
75 | 70 | 67 | 86.0167 | 306374 | 119485.86 | 23.721 | 7500 | 1034.8004 |  | 5
75 | 70 | 67 | 86.0167 | 309260 | 129889.2 | 23.806 | 8250 | 1380.5097 |  | 5
75 | 70 | 67 | 86.0167 | 317704 | 149320.88 | 23.97 | 10000 | 2507.4079 |  | 5
75 | 75 | 67 | 66.7494 | 306546 | 156338.46 | 23.706 | 7500 | 1034.8004 |  | 5
75 | 75 | 67 | 66.7494 | 309431 | 167092.74 | 23.791 | 8250 | 1380.5097 |  | 5
75 | 75 | 67 | 66.7494 | 317876 | 184368.08 | 23.955 | 10000 | 2507.4079 |  | 5
75 | 75 | 71 | 82.6659 | 320009 | 118403.33 | 23.884 | 7500 | 1034.8004 |  | 5
75 | 75 | 71 | 82.6659 | 322895 | 132386.95 | 23.969 | 8250 | 1380.5097 |  | 5
75 | 75 | 71 | 82.6659 | 331339 | 149102.55 | 24.133 | 10000 | 2507.4079 |  | 5
85 | 70 | 59 | 52.7218 | 285688 | 174269.68 | 26.376 | 7500 | 1034.8004 |  | 5
85 | 70 | 59 | 52.7218 | 288574 | 184687.36 | 26.461 | 8250 | 1380.5097 |  | 5
85 | 70 | 59 | 52.7218 | 297019 | 201972.92 | 26.625 | 10000 | 2507.4079 |  | 5
85 | 75 | 59 | 38.6294 | 285860 | 205819.2 | 26.36 | 7500 | 1034.8004 |  | 5
85 | 75 | 59 | 38.6294 | 288746 | 219446.96 | 26.446 | 8250 | 1380.5097 |  | 5
85 | 75 | 59 | 38.6294 | 297191 | 297191 | 26.61 | 10000 | 2507.4079 |  | 5
85 | 70 | 63 | 68.6866 | 289855 | 156521.7 | 26.357 | 7500 | 1034.8004 |  | 5
85 | 70 | 63 | 68.6866 | 292741 | 166862.37 | 26.443 | 8250 | 1380.5097 |  | 5
85 | 70 | 63 | 68.6866 | 301186 | 183723.46 | 26.607 | 10000 | 2507.4079 |  | 5
85 | 75 | 63 | 52.1129 | 290027 | 188517.55 | 26.342 | 7500 | 1034.8004 |  | 5
85 | 75 | 63 | 52.1129 | 292913 | 202109.97 | 26.427 | 8250 | 1380.5097 |  | 5
85 | 75 | 63 | 52.1129 | 301358 | 219991.34 | 26.592 | 10000 | 2507.4079 |  | 5
85 | 70 | 67 | 86.0167 | 298669 | 122454.29 | 26.318 | 7500 | 1034.8004 |  | 5
85 | 70 | 67 | 86.0167 | 301555 | 135699.75 | 26.403 | 8250 | 1380.5097 |  | 5
85 | 70 | 67 | 86.0167 | 310000 | 151900 | 26.567 | 10000 | 2507.4079 |  | 5
85 | 75 | 67 | 66.7494 | 298841 | 158385.73 | 26.302 | 7500 | 1034.8004 |  | 5
85 | 75 | 67 | 66.7494 | 301727 | 171984.39 | 26.388 | 8250 | 1380.5097 |  | 5
85 | 75 | 67 | 66.7494 | 310172 | 189204.92 | 26.552 | 10000 | 2507.4079 |  | 5
85 | 75 | 71 | 82.6659 | 312304 | 124921.6 | 26.48 | 7500 | 1034.8004 |  | 5
85 | 75 | 71 | 82.6659 | 315190 | 135531.7 | 26.566 | 8250 | 1380.5097 |  | 5
85 | 75 | 71 | 82.6659 | 323635 | 155344.8 | 26.73 | 10000 | 2507.4079 |  | 5
95 | 70 | 59 | 52.7218 | 272433 | 168908.46 | 29.186 | 7500 | 1020.5467 |  | 5
95 | 70 | 59 | 52.7218 | 275319 | 181710.54 | 29.271 | 8250 | 1354.1248 |  | 5
95 | 70 | 59 | 52.7218 | 283763 | 198634.1 | 29.435 | 10000 | 2507.4079 |  | 5
95 | 75 | 59 | 38.6294 | 272605 | 272605 | 29.171 | 7500 | 1020.5467 |  | 5
95 | 75 | 59 | 38.6294 | 275491 | 275491 | 29.256 | 8250 | 1354.1248 |  | 5
95 | 75 | 59 | 38.6294 | 283935 | 283935 | 29.42 | 10000 | 2507.4079 |  | 5
95 | 70 | 63 | 68.6866 | 276600 | 152130 | 29.167 | 7500 | 1020.5467 |  | 5
95 | 70 | 63 | 68.6866 | 279486 | 164896.74 | 29.253 | 8250 | 1354.1248 |  | 5
95 | 70 | 63 | 68.6866 | 287931 | 181396.53 | 29.417 | 10000 | 2507.4079 |  | 5
95 | 75 | 63 | 52.1129 | 276772 | 185437.24 | 29.152 | 7500 | 1020.5467 |  | 5
95 | 75 | 63 | 52.1129 | 279658 | 198557.18 | 29.237 | 8250 | 1354.1248 |  | 5
95 | 75 | 63 | 52.1129 | 288103 | 216077.25 | 29.402 | 10000 | 2507.4079 |  | 5
95 | 70 | 67 | 86.0167 | 285414 | 122728.02 | 29.128 | 7500 | 1034.8004 |  | 5
95 | 70 | 67 | 86.0167 | 288300 | 135501 | 29.213 | 8250 | 1380.5097 |  | 5
95 | 70 | 67 | 86.0167 | 296744 | 151339.44 | 29.377 | 10000 | 2507.4079 |  | 5
95 | 75 | 67 | 66.7494 | 285586 | 157072.3 | 29.112 | 7500 | 1034.8004 |  | 5
95 | 75 | 67 | 66.7494 | 288472 | 167313.76 | 29.198 | 8250 | 1380.5097 |  | 5
95 | 75 | 67 | 66.7494 | 296916 | 187057.08 | 29.362 | 10000 | 2507.4079 |  | 5
95 | 75 | 71 | 82.6659 | 299049 | 125600.58 | 29.29 | 7500 | 1034.8004 |  | 5
95 | 75 | 71 | 82.6659 | 301935 | 135870.75 | 29.376 | 8250 | 1380.5097 |  | 5
95 | 75 | 71 | 82.6659 | 310379 | 152085.71 | 29.54 | 10000 | 2507.4079 |  | 5
105 | 70 | 59 | 52.7218 | 256233 | 163989.12 | 32.325 | 7500 | 1020.5467 |  | 5
105 | 70 | 59 | 52.7218 | 259119 | 176200.92 | 32.41 | 8250 | 1354.1248 |  | 5
105 | 70 | 59 | 52.7218 | 267564 | 267564 | 32.575 | 10000 | 2483.4847 |  | 5
105 | 75 | 59 | 38.6294 | 256405 | 256405 | 32.31 | 7500 | 1020.5467 |  | 5
105 | 75 | 59 | 38.6294 | 259291 | 259291 | 32.395 | 8250 | 1354.1248 |  | 5
105 | 75 | 59 | 38.6294 | 267736 | 267736 | 32.56 | 10000 | 2483.4847 |  | 5
105 | 70 | 63 | 68.6866 | 260400 | 148428 | 32.307 | 7500 | 1020.5467 |  | 5
105 | 70 | 63 | 68.6866 | 263286 | 160604.46 | 32.392 | 8250 | 1354.1248 |  | 5
105 | 70 | 63 | 68.6866 | 271731 | 176625.15 | 32.556 | 10000 | 2483.4847 |  | 5
105 | 75 | 63 | 52.1129 | 260572 | 179794.68 | 32.292 | 7500 | 1020.5467 |  | 5
105 | 75 | 63 | 52.1129 | 263458 | 192324.34 | 32.377 | 8250 | 1354.1248 |  | 5
105 | 75 | 63 | 52.1129 | 271903 | 209365.31 | 32.541 | 10000 | 2483.4847 |  | 5
105 | 70 | 67 | 86.0167 | 269214 | 121146.3 | 32.267 | 7500 | 1020.5467 |  | 5
105 | 70 | 67 | 86.0167 | 272100 | 133329 | 32.352 | 8250 | 1354.1248 |  | 5
105 | 70 | 67 | 86.0167 | 280545 | 148688.85 | 32.517 | 10000 | 2507.4079 |  | 5
105 | 75 | 67 | 66.7494 | 269386 | 153550.02 | 32.252 | 7500 | 1020.5467 |  | 5
105 | 75 | 67 | 66.7494 | 272272 | 163363.2 | 32.337 | 8250 | 1354.1248 |  | 5
105 | 75 | 67 | 66.7494 | 280717 | 182466.05 | 32.502 | 10000 | 2507.4079 |  | 5
105 | 75 | 71 | 82.6659 | 282849 | 124453.56 | 32.43 | 7500 | 1034.8004 |  | 5
105 | 75 | 71 | 82.6659 | 285735 | 134295.45 | 32.515 | 8250 | 1380.5097 |  | 5
105 | 75 | 71 | 82.6659 | 294180 | 150031.8 | 32.68 | 10000 | 2507.4079 |  | 5
115 | 70 | 59 | 52.7218 | 241444 | 241444 | 36.009 | 7500 | 1020.5467 |  | 5
115 | 70 | 59 | 52.7218 | 244330 | 244330 | 36.094 | 8250 | 1354.1248 |  | 5
115 | 70 | 59 | 52.7218 | 252775 | 252775 | 36.258 | 10000 | 2483.4847 |  | 5
115 | 75 | 59 | 38.6294 | 241616 | 241616 | 35.994 | 7500 | 1020.5467 |  | 5
115 | 75 | 59 | 38.6294 | 244502 | 244502 | 36.079 | 8250 | 1354.1248 |  | 5
115 | 75 | 59 | 38.6294 | 252947 | 252947 | 36.243 | 10000 | 2483.4847 |  | 5
115 | 70 | 63 | 68.6866 | 245611 | 152278.82 | 35.99 | 7500 | 1020.5467 |  | 5
115 | 70 | 63 | 68.6866 | 248497 | 164008.02 | 36.076 | 8250 | 1354.1248 |  | 5
115 | 70 | 63 | 68.6866 | 256942 | 179859.4 | 36.24 | 10000 | 2483.4847 |  | 5
115 | 75 | 63 | 52.1129 | 245783 | 181879.42 | 35.975 | 7500 | 1020.5467 |  | 5
115 | 75 | 63 | 52.1129 | 248669 | 193961.82 | 36.06 | 8250 | 1354.1248 |  | 5
115 | 75 | 63 | 52.1129 | 257114 | 210833.48 | 36.225 | 10000 | 2483.4847 |  | 5
115 | 70 | 67 | 86.0167 | 254425 | 127212.5 | 35.951 | 7500 | 1020.5467 |  | 5
115 | 70 | 67 | 86.0167 | 257311 | 136374.83 | 36.036 | 8250 | 1354.1248 |  | 5
115 | 70 | 67 | 86.0167 | 265756 | 151480.92 | 36.2 | 10000 | 2483.4847 |  | 5
115 | 75 | 67 | 66.7494 | 254597 | 155304.17 | 35.935 | 7500 | 1020.5467 |  | 5
115 | 75 | 67 | 66.7494 | 257483 | 167363.95 | 36.021 | 8250 | 1354.1248 |  | 5
115 | 75 | 67 | 66.7494 | 265928 | 183490.32 | 36.185 | 10000 | 2483.4847 |  | 5
115 | 75 | 71 | 82.6659 | 268060 | 128668.8 | 36.113 | 7500 | 1020.5467 |  | 5
115 | 75 | 71 | 82.6659 | 270946 | 140891.92 | 36.199 | 8250 | 1354.1248 |  | 5
115 | 75 | 71 | 82.6659 | 279391 | 156458.96 | 36.363 | 10000 | 2483.4847 |  | 5
65 | 80 | 59 | 27.7402 | 297734 | 241164.54 | 21.45 | 7500 | 1034.8004 |  | 5
65 | 80 | 59 | 27.7402 | 300620 | 255527 | 21.535 | 8250 | 1380.5097 |  | 5
65 | 80 | 59 | 27.7402 | 309065 | 275067.85 | 21.699 | 10000 | 2507.4079 |  | 5
65 | 85 | 59 | 19.3387 | 302705 | 302705 | 21.494 | 7500 | 1034.8004 |  | 5
65 | 85 | 59 | 19.3387 | 305591 | 305591 | 21.58 | 8250 | 1380.5097 |  | 5
65 | 85 | 59 | 19.3387 | 314036 | 314036 | 21.744 | 10000 | 2507.4079 |  | 5
65 | 80 | 63 | 39.1676 | 301901 | 223406.74 | 21.432 | 7500 | 1034.8004 |  | 5
65 | 80 | 63 | 39.1676 | 304787 | 237733.86 | 21.517 | 8250 | 1380.5097 |  | 5
65 | 80 | 63 | 39.1676 | 313232 | 256850.24 | 21.681 | 10000 | 2507.4079 |  | 5
65 | 85 | 63 | 29.0563 | 306873 | 254704.59 | 21.476 | 7500 | 1034.8004 |  | 5
65 | 85 | 63 | 29.0563 | 309759 | 269490.33 | 21.561 | 8250 | 1380.5097 |  | 5
65 | 85 | 63 | 29.0563 | 318203 | 289564.73 | 21.726 | 10000 | 2507.4079 |  | 5
65 | 80 | 67 | 51.5724 | 310715 | 192643.3 | 21.392 | 7500 | 1034.8004 |  | 5
65 | 80 | 67 | 51.5724 | 313601 | 203840.65 | 21.477 | 8250 | 1380.5097 |  | 5
65 | 80 | 67 | 51.5724 | 322046 | 222211.74 | 21.641 | 10000 | 2507.4079 |  | 5
65 | 85 | 67 | 39.6049 | 315686 | 224137.06 | 21.436 | 7500 | 1034.8004 |  | 5
65 | 85 | 67 | 39.6049 | 318572 | 238929 | 21.522 | 8250 | 1380.5097 |  | 5
65 | 85 | 67 | 39.6049 | 327017 | 258343.43 | 21.686 | 10000 | 2507.4079 |  | 5
65 | 80 | 71 | 65.0618 | 324178 | 155605.44 | 21.57 | 7500 | 1034.8004 |  | 5
65 | 80 | 71 | 65.0618 | 327064 | 170073.28 | 21.655 | 8250 | 1380.5097 |  | 5
65 | 80 | 71 | 65.0618 | 335509 | 187885.04 | 21.819 | 10000 | 2507.4079 |  | 5
65 | 85 | 71 | 51.076 | 329149 | 190906.42 | 21.614 | 7500 | 1034.8004 |  | 5
65 | 85 | 71 | 51.076 | 332035 | 205861.7 | 21.699 | 8250 | 1380.5097 |  | 5
65 | 85 | 71 | 51.076 | 340480 | 224716.8 | 21.864 | 10000 | 2507.4079 |  | 5
75 | 80 | 59 | 27.7402 | 295093 | 295093 | 23.776 | 7500 | 1034.8004 |  | 5
75 | 80 | 59 | 27.7402 | 297979 | 297979 | 23.861 | 8250 | 1380.5097 |  | 5
75 | 80 | 59 | 27.7402 | 306423 | 306423 | 24.026 | 10000 | 2507.4079 |  | 5
75 | 85 | 59 | 19.3387 | 300064 | 300064 | 23.821 | 7500 | 1034.8004 |  | 5
75 | 85 | 59 | 19.3387 | 302950 | 302950 | 23.906 | 8250 | 1380.5097 |  | 5
75 | 85 | 59 | 19.3387 | 311395 | 311395 | 24.07 | 10000 | 2507.4079 |  | 5
75 | 80 | 63 | 39.1676 | 299260 | 224445 | 23.758 | 7500 | 1034.8004 |  | 5
75 | 80 | 63 | 39.1676 | 302146 | 235673.88 | 23.843 | 8250 | 1380.5097 |  | 5
75 | 80 | 63 | 39.1676 | 310591 | 254684.62 | 24.007 | 10000 | 2507.4079 |  | 5
75 | 85 | 63 | 29.0563 | 304232 | 255554.88 | 23.802 | 7500 | 1034.8004 |  | 5
75 | 85 | 63 | 29.0563 | 307118 | 270263.84 | 23.887 | 8250 | 1380.5097 |  | 5
75 | 85 | 63 | 29.0563 | 315562 | 290317.04 | 24.052 | 10000 | 2507.4079 |  | 5
75 | 80 | 67 | 51.5724 | 308074 | 191005.88 | 23.718 | 7500 | 1034.8004 |  | 5
75 | 80 | 67 | 51.5724 | 310960 | 205233.6 | 23.803 | 8250 | 1380.5097 |  | 5
75 | 80 | 67 | 51.5724 | 319404 | 223582.8 | 23.968 | 10000 | 2507.4079 |  | 5
75 | 85 | 67 | 39.6049 | 313045 | 225392.4 | 23.762 | 7500 | 1034.8004 |  | 5
75 | 85 | 67 | 39.6049 | 315931 | 236948.25 | 23.848 | 8250 | 1380.5097 |  | 5
75 | 85 | 67 | 39.6049 | 324376 | 256257.04 | 24.012 | 10000 | 2507.4079 |  | 5
75 | 80 | 71 | 65.0618 | 321537 | 157553.13 | 23.896 | 7500 | 1034.8004 |  | 5
75 | 80 | 71 | 65.0618 | 324423 | 171944.19 | 23.981 | 8250 | 1380.5097 |  | 5
75 | 80 | 71 | 65.0618 | 332868 | 189734.76 | 24.145 | 10000 | 2507.4079 |  | 5
75 | 85 | 71 | 51.076 | 326508 | 189374.64 | 23.94 | 7500 | 1034.8004 |  | 5
75 | 85 | 71 | 51.076 | 329394 | 204224.28 | 24.026 | 8250 | 1380.5097 |  | 5
75 | 85 | 71 | 51.076 | 337839 | 222973.74 | 24.19 | 10000 | 2507.4079 |  | 5
85 | 80 | 59 | 27.7402 | 287389 | 287389 | 26.373 | 7500 | 1034.8004 |  | 5
85 | 80 | 59 | 27.7402 | 290275 | 290275 | 26.458 | 8250 | 1380.5097 |  | 5
85 | 80 | 59 | 27.7402 | 298719 | 298719 | 26.622 | 10000 | 2507.4079 |  | 5
85 | 85 | 59 | 19.3387 | 292360 | 292360 | 26.417 | 7500 | 1034.8004 |  | 5
85 | 85 | 59 | 19.3387 | 295246 | 295246 | 26.502 | 8250 | 1380.5097 |  | 5
85 | 85 | 59 | 19.3387 | 303690 | 303690 | 26.667 | 10000 | 2507.4079 |  | 5
85 | 80 | 63 | 39.1676 | 291556 | 224498.12 | 26.354 | 7500 | 1034.8004 |  | 5
85 | 80 | 63 | 39.1676 | 294442 | 238498.02 | 26.44 | 8250 | 1380.5097 |  | 5
85 | 80 | 63 | 39.1676 | 302886 | 257453.1 | 26.604 | 10000 | 2507.4079 |  | 5
85 | 85 | 63 | 29.0563 | 296527 | 255013.22 | 26.399 | 7500 | 1034.8004 |  | 5
85 | 85 | 63 | 29.0563 | 299413 | 269471.7 | 26.484 | 8250 | 1380.5097 |  | 5
85 | 85 | 63 | 29.0563 | 307858 | 307858 | 26.648 | 10000 | 2507.4079 |  | 5
85 | 80 | 67 | 51.5724 | 300370 | 192236.8 | 26.315 | 7500 | 1034.8004 |  | 5
85 | 80 | 67 | 51.5724 | 303256 | 206214.08 | 26.4 | 8250 | 1380.5097 |  | 5
85 | 80 | 67 | 51.5724 | 311700 | 224424 | 26.564 | 10000 | 2507.4079 |  | 5
85 | 85 | 67 | 39.6049 | 305341 | 225952.34 | 26.359 | 7500 | 1034.8004 |  | 5
85 | 85 | 67 | 39.6049 | 308227 | 240417.06 | 26.444 | 8250 | 1380.5097 |  | 5
85 | 85 | 67 | 39.6049 | 316671 | 259670.22 | 26.609 | 10000 | 2507.4079 |  | 5
85 | 80 | 71 | 65.0618 | 313833 | 160054.83 | 26.493 | 7500 | 1034.8004 |  | 5
85 | 80 | 71 | 65.0618 | 316719 | 174195.45 | 26.578 | 8250 | 1380.5097 |  | 5
85 | 80 | 71 | 65.0618 | 325163 | 191846.17 | 26.742 | 10000 | 2507.4079 |  | 5
85 | 85 | 71 | 51.076 | 318804 | 194470.44 | 26.537 | 7500 | 1034.8004 |  | 5
85 | 85 | 71 | 51.076 | 321690 | 205881.6 | 26.622 | 8250 | 1380.5097 |  | 5
85 | 85 | 71 | 51.076 | 330134 | 224491.12 | 26.787 | 10000 | 2507.4079 |  | 5
95 | 80 | 59 | 27.7402 | 274133 | 274133 | 29.183 | 7500 | 1020.5467 |  | 5
95 | 80 | 59 | 27.7402 | 277019 | 277019 | 29.268 | 8250 | 1354.1248 |  | 5
95 | 80 | 59 | 27.7402 | 285464 | 285464 | 29.432 | 10000 | 2507.4079 |  | 5
95 | 85 | 59 | 19.3387 | 279105 | 279105 | 29.227 | 7500 | 1020.5467 |  | 5
95 | 85 | 59 | 19.3387 | 281991 | 281991 | 29.312 | 8250 | 1380.5097 |  | 5
95 | 85 | 59 | 19.3387 | 290435 | 290435 | 29.477 | 10000 | 2507.4079 |  | 5
95 | 80 | 63 | 39.1676 | 278301 | 219857.79 | 29.164 | 7500 | 1020.5467 |  | 5
95 | 80 | 63 | 39.1676 | 281187 | 233385.21 | 29.25 | 8250 | 1380.5097 |  | 5
95 | 80 | 63 | 39.1676 | 289631 | 251978.97 | 29.414 | 10000 | 2507.4079 |  | 5
95 | 85 | 63 | 29.0563 | 283272 | 283272 | 29.209 | 7500 | 1034.8004 |  | 5
95 | 85 | 63 | 29.0563 | 286158 | 286158 | 29.294 | 8250 | 1380.5097 |  | 5
95 | 85 | 63 | 29.0563 | 294602 | 294602 | 29.458 | 10000 | 2507.4079 |  | 5
95 | 80 | 67 | 51.5724 | 287114 | 189495.24 | 29.125 | 7500 | 1034.8004 |  | 5
95 | 80 | 67 | 51.5724 | 290000 | 203000 | 29.21 | 8250 | 1380.5097 |  | 5
95 | 80 | 67 | 51.5724 | 298445 | 220849.3 | 29.374 | 10000 | 2507.4079 |  | 5
95 | 85 | 67 | 39.6049 | 292086 | 221985.36 | 29.169 | 7500 | 1034.8004 |  | 5
95 | 85 | 67 | 39.6049 | 294972 | 233027.88 | 29.254 | 8250 | 1380.5097 |  | 5
95 | 85 | 67 | 39.6049 | 303416 | 251835.28 | 29.419 | 10000 | 2507.4079 |  | 5
95 | 80 | 71 | 65.0618 | 300577 | 159305.81 | 29.303 | 7500 | 1034.8004 |  | 5
95 | 80 | 71 | 65.0618 | 303463 | 172973.91 | 29.388 | 8250 | 1380.5097 |  | 5
95 | 80 | 71 | 65.0618 | 311908 | 190263.88 | 29.552 | 10000 | 2507.4079 |  | 5
95 | 85 | 71 | 51.076 | 305549 | 189440.38 | 29.347 | 7500 | 1034.8004 |  | 5
95 | 85 | 71 | 51.076 | 308435 | 203567.1 | 29.432 | 8250 | 1380.5097 |  | 5
95 | 85 | 71 | 51.076 | 316879 | 221815.3 | 29.597 | 10000 | 2507.4079 |  | 5
105 | 80 | 59 | 27.7402 | 257934 | 257934 | 32.322 | 7500 | 1020.5467 |  | 5
105 | 80 | 59 | 27.7402 | 260820 | 260820 | 32.408 | 8250 | 1354.1248 |  | 5
105 | 80 | 59 | 27.7402 | 269264 | 269264 | 32.572 | 10000 | 2483.4847 |  | 5
105 | 85 | 59 | 19.3387 | 262905 | 262905 | 32.367 | 7500 | 1020.5467 |  | 5
105 | 85 | 59 | 19.3387 | 265791 | 265791 | 32.452 | 8250 | 1354.1248 |  | 5
105 | 85 | 59 | 19.3387 | 274236 | 274236 | 32.616 | 10000 | 2483.4847 |  | 5
105 | 80 | 63 | 39.1676 | 262101 | 212301.81 | 32.304 | 7500 | 1020.5467 |  | 5
105 | 80 | 63 | 39.1676 | 264987 | 225238.95 | 32.389 | 8250 | 1354.1248 |  | 5
105 | 80 | 63 | 39.1676 | 273431 | 273431 | 32.554 | 10000 | 2483.4847 |  | 5
105 | 85 | 63 | 29.0563 | 267072 | 267072 | 32.349 | 7500 | 1020.5467 |  | 5
105 | 85 | 63 | 29.0563 | 269958 | 269958 | 32.434 | 8250 | 1354.1248 |  | 5
105 | 85 | 63 | 29.0563 | 278403 | 278403 | 32.598 | 10000 | 2483.4847 |  | 5
105 | 80 | 67 | 51.5724 | 270915 | 184222.2 | 32.264 | 7500 | 1020.5467 |  | 5
105 | 80 | 67 | 51.5724 | 273801 | 197136.72 | 32.35 | 8250 | 1354.1248 |  | 5
105 | 80 | 67 | 51.5724 | 282245 | 214506.2 | 32.514 | 10000 | 2507.4079 |  | 5
105 | 85 | 67 | 39.6049 | 275886 | 215191.08 | 32.309 | 7500 | 1020.5467 |  | 5
105 | 85 | 67 | 39.6049 | 278772 | 225805.32 | 32.394 | 8250 | 1354.1248 |  | 5
105 | 85 | 67 | 39.6049 | 287217 | 244134.45 | 32.558 | 10000 | 2507.4079 |  | 5
105 | 80 | 71 | 65.0618 | 284378 | 156407.9 | 32.442 | 7500 | 1034.8004 |  | 5
105 | 80 | 71 | 65.0618 | 287264 | 169485.76 | 32.527 | 8250 | 1380.5097 |  | 5
105 | 80 | 71 | 65.0618 | 295708 | 186296.04 | 32.692 | 10000 | 2507.4079 |  | 5
105 | 85 | 71 | 51.076 | 289349 | 185183.36 | 32.487 | 7500 | 1034.8004 |  | 5
105 | 85 | 71 | 51.076 | 292235 | 198719.8 | 32.572 | 8250 | 1380.5097 |  | 5
105 | 85 | 71 | 51.076 | 300680 | 216489.6 | 32.736 | 10000 | 2507.4079 |  | 5
115 | 80 | 59 | 27.7402 | 243145 | 243145 | 36.006 | 7500 | 1020.5467 |  | 5
115 | 80 | 59 | 27.7402 | 246031 | 246031 | 36.091 | 8250 | 1354.1248 |  | 5
115 | 80 | 59 | 27.7402 | 254475 | 254475 | 36.255 | 10000 | 2483.4847 |  | 5
115 | 85 | 59 | 19.3387 | 248116 | 248116 | 36.05 | 7500 | 1020.5467 |  | 5
115 | 85 | 59 | 19.3387 | 251002 | 251002 | 36.136 | 8250 | 1354.1248 |  | 5
115 | 85 | 59 | 19.3387 | 259447 | 259447 | 36.3 | 10000 | 2483.4847 |  | 5
115 | 80 | 63 | 39.1676 | 247312 | 247312 | 35.988 | 7500 | 1020.5467 |  | 5
115 | 80 | 63 | 39.1676 | 250198 | 250198 | 36.073 | 8250 | 1354.1248 |  | 5
115 | 80 | 63 | 39.1676 | 258642 | 258642 | 36.237 | 10000 | 2483.4847 |  | 5
115 | 85 | 63 | 29.0563 | 252283 | 252283 | 36.032 | 7500 | 1020.5467 |  | 5
115 | 85 | 63 | 29.0563 | 255169 | 255169 | 36.117 | 8250 | 1354.1248 |  | 5
115 | 85 | 63 | 29.0563 | 263614 | 263614 | 36.282 | 10000 | 2483.4847 |  | 5
115 | 80 | 67 | 51.5724 | 256126 | 186971.98 | 35.948 | 7500 | 1020.5467 |  | 5
115 | 80 | 67 | 51.5724 | 259012 | 199439.24 | 36.033 | 8250 | 1354.1248 |  | 5
115 | 80 | 67 | 51.5724 | 267456 | 216639.36 | 36.197 | 10000 | 2483.4847 |  | 5
115 | 85 | 67 | 39.6049 | 261097 | 214099.54 | 35.992 | 7500 | 1020.5467 |  | 5
115 | 85 | 67 | 39.6049 | 263983 | 227289.36 | 36.077 | 8250 | 1354.1248 |  | 5
115 | 85 | 67 | 39.6049 | 272428 | 245185.2 | 36.242 | 10000 | 2483.4847 |  | 5
115 | 80 | 71 | 65.0618 | 269589 | 161753.4 | 36.126 | 7500 | 1020.5467 |  | 5
115 | 80 | 71 | 65.0618 | 272475 | 174384 | 36.211 | 8250 | 1354.1248 |  | 5
115 | 80 | 71 | 65.0618 | 280919 | 191024.92 | 36.375 | 10000 | 2507.4079 |  | 5
115 | 85 | 71 | 51.076 | 274560 | 189446.4 | 36.17 | 7500 | 1020.5467 |  | 5
115 | 85 | 71 | 51.076 | 277446 | 202535.58 | 36.255 | 8250 | 1354.1248 |  | 5
115 | 85 | 71 | 51.076 | 285891 | 220136.07 | 36.42 | 10000 | 2507.4079 |  | 5
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions