## Table 1
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 75 | 75 | 100 | 378000 | 134300 | 22.5 | 6000 | 983.5531 |  | 1
75 | 75 | 72 | 86.8609 | 362000 | 146300 | 22.1 | 6000 | 983.5531 |  | 1
75 | 75 | 67 | 66.7494 | 334000 | 178500 | 21.3 | 6000 | 833.5196 |  | 1
75 | 75 | 62 | 48.6386 | 308000 | 208520 | 20.8 | 6000 | 833.5196 |  | 1
75 | 75 | 57 | 32.2833 | 282000 | 236860 | 20.5 | 6000 | 833.5196 |  | 1
75 | 75 | 75 | 100 | 399000 | 133125 | 23 | 7500 | 1316.9609 |  | 1
75 | 75 | 72 | 86.8609 | 379000 | 157125 | 22.5 | 7500 | 1316.9609 |  | 1
75 | 75 | 67 | 66.7494 | 351000 | 190887.5 | 21.7 | 7500 | 1316.9609 |  | 1
75 | 75 | 62 | 48.6386 | 325000 | 227650 | 21.2 | 7500 | 1150.257 |  | 1
75 | 75 | 57 | 32.2833 | 297000 | 258887.5 | 20.7 | 7500 | 1150.257 |  | 1
75 | 75 | 75 | 100 | 412000 | 134950 | 23.4 | 9000 | 1948.352 |  | 1
75 | 75 | 72 | 86.8609 | 392000 | 159225 | 22.8 | 9000 | 1762.8939 |  | 1
75 | 75 | 67 | 66.7494 | 363000 | 201760 | 22.1 | 9000 | 1762.8939 |  | 1
75 | 75 | 62 | 48.6386 | 336000 | 244770 | 21.4 | 9000 | 1587.8547 |  | 1
75 | 75 | 57 | 32.2833 | 312000 | 275730 | 21 | 9000 | 1587.8547 |  | 1
75 | 75 | 75 | 100 | 421000 | 138775 | 23.6 | 10500 | 2558.905 |  | 1
75 | 75 | 72 | 86.8609 | 401000 | 163107.5 | 23.1 | 10500 | 2558.905 |  | 1
75 | 75 | 67 | 66.7494 | 372000 | 210797.5 | 22.3 | 10500 | 2369.2793 |  | 1
75 | 75 | 62 | 48.6386 | 345000 | 260642.5 | 21.6 | 10500 | 2190.0726 |  | 1
75 | 75 | 57 | 32.2833 | 327000 | 288727.5 | 21.3 | 10500 | 2190.0726 |  | 1
85 | 85 | 75 | 63.5688 | 367000 | 170700 | 24.7 | 6000 | 983.5531 |  | 1
85 | 85 | 72 | 54.0993 | 353000 | 185700 | 24.4 | 6000 | 983.5531 |  | 1
85 | 85 | 67 | 39.6049 | 326000 | 226830 | 23.7 | 6000 | 833.5196 |  | 1
85 | 85 | 62 | 26.5524 | 300000 | 258810 | 23.4 | 6000 | 833.5196 |  | 1
85 | 85 | 57 | 14.765 | 273000 | 287140 | 23.2 | 6000 | 758.5028 |  | 1
85 | 85 | 75 | 63.5688 | 384000 | 180875 | 25.2 | 7500 | 1316.9609 |  | 1
85 | 85 | 72 | 54.0993 | 369000 | 214350 | 24.8 | 7500 | 1316.9609 |  | 1
85 | 85 | 67 | 39.6049 | 342000 | 253525 | 24.1 | 7500 | 1150.257 |  | 1
85 | 85 | 62 | 26.5524 | 316000 | 291350 | 23.7 | 7500 | 1150.257 |  | 1
85 | 85 | 57 | 14.765 | 290000 | 312462.5 | 23.1 | 7500 | 1150.257 |  | 1
85 | 85 | 75 | 63.5688 | 396000 | 193050 | 25.6 | 9000 | 1762.8939 |  | 1
85 | 85 | 72 | 54.0993 | 380000 | 227765 | 25.1 | 9000 | 1762.8939 |  | 1
85 | 85 | 67 | 39.6049 | 353000 | 275240 | 24.4 | 9000 | 1762.8939 |  | 1
85 | 85 | 62 | 26.5524 | 327000 | 321230 | 23.9 | 9000 | 1587.8547 |  | 1
85 | 85 | 57 | 14.765 | 305000 | 340775 | 23.6 | 9000 | 1587.8547 |  | 1
85 | 85 | 75 | 63.5688 | 404000 | 206540 | 25.8 | 10500 | 2558.905 |  | 1
85 | 85 | 72 | 54.0993 | 389000 | 245470 | 25.3 | 10500 | 2369.2793 |  | 1
85 | 85 | 67 | 39.6049 | 361000 | 297202.5 | 24.7 | 10500 | 2369.2793 |  | 1
85 | 85 | 62 | 26.5524 | 335000 | 349357.5 | 24.1 | 10500 | 2190.0726 |  | 1
85 | 85 | 57 | 14.765 | 319000 | 356117.5 | 23.8 | 10500 | 2190.0726 |  | 1
95 | 95 | 75 | 40.2091 | 357000 | 245000 | 27.4 | 6000 | 983.5531 |  | 1
95 | 95 | 72 | 33.2947 | 343000 | 261000 | 27.1 | 6000 | 833.5196 |  | 1
95 | 95 | 67 | 22.7111 | 316000 | 276190 | 26.6 | 6000 | 833.5196 |  | 1
95 | 95 | 62 | 13.1803 | 289000 | 310150 | 26.4 | 6000 | 833.5196 |  | 1
95 | 95 | 57 | 4.5734 | 264000 | 338140 | 26.1 | 6000 | 758.5028 |  | 1
95 | 95 | 75 | 40.2091 | 373000 | 273750 | 27.9 | 7500 | 1316.9609 |  | 1
95 | 95 | 72 | 33.2947 | 357000 | 265100 | 27.5 | 7500 | 1316.9609 |  | 1
95 | 95 | 67 | 22.7111 | 331000 | 316475 | 27 | 7500 | 1150.257 |  | 1
95 | 95 | 62 | 13.1803 | 304000 | 355950 | 26.6 | 7500 | 1150.257 |  | 1
95 | 95 | 57 | 4.5734 | 281000 | 363575 | 26.1 | 7500 | 1150.257 |  | 1
95 | 95 | 75 | 40.2091 | 383000 | 307500 | 28.2 | 9000 | 1762.8939 |  | 1
95 | 95 | 72 | 33.2947 | 368000 | 299860 | 27.8 | 9000 | 1762.8939 |  | 1
95 | 95 | 67 | 22.7111 | 341000 | 352285 | 27.3 | 9000 | 1587.8547 |  | 1
95 | 95 | 62 | 13.1803 | 315000 | 398255 | 26.9 | 9000 | 1587.8547 |  | 1
95 | 95 | 57 | 4.5734 | 295000 | 398950 | 26.6 | 9000 | 1587.8547 |  | 1
95 | 95 | 75 | 40.2091 | 391000 | 285542.5 | 28.4 | 10500 | 2369.2793 |  | 1
95 | 95 | 72 | 33.2947 | 376000 | 331402.5 | 28 | 10500 | 2369.2793 |  | 1
95 | 95 | 67 | 22.7111 | 349000 | 384867.5 | 27.5 | 10500 | 2190.0726 |  | 1
95 | 95 | 62 | 13.1803 | 322000 | 434600 | 27.1 | 10500 | 2190.0726 |  | 1
95 | 95 | 57 | 4.5734 | 309000 | 418147.5 | 26.8 | 10500 | 2190.0726 |  | 1
105 | 105 | 75 | 25.1345 | 344000 | 306000 | 30.5 | 6000 | 833.5196 |  | 1
105 | 105 | 72 | 20.0232 | 330000 | 323000 | 30.3 | 6000 | 833.5196 |  | 1
105 | 105 | 67 | 12.1996 | 304000 | 327950 | 30 | 6000 | 833.5196 |  | 1
105 | 105 | 62 | 5.1542 | 277000 | 361900 | 29.8 | 6000 | 758.5028 |  | 1
105 | 105 | 57 | -1.2082 | 251000 | 382600 | 30.2 | 6000 | 758.5028 |  | 1
105 | 105 | 75 | 25.1345 | 360000 | 351250 | 31 | 7500 | 1316.9609 |  | 1
105 | 105 | 72 | 20.0232 | 344000 | 325687.5 | 30.7 | 7500 | 1150.257 |  | 1
105 | 105 | 67 | 12.1996 | 318000 | 381187.5 | 30.3 | 7500 | 1150.257 |  | 1
105 | 105 | 62 | 5.1542 | 291000 | 421312.5 | 30 | 7500 | 1150.257 |  | 1
105 | 105 | 57 | -1.2082 | 268000 | 426812.5 | 29.9 | 7500 | 1066.905 |  | 1
105 | 105 | 75 | 25.1345 | 369000 | 356950 | 31.2 | 9000 | 1762.8939 |  | 1
105 | 105 | 72 | 20.0232 | 354000 | 375050 | 31 | 9000 | 1762.8939 |  | 1
105 | 105 | 67 | 12.1996 | 327000 | 426475 | 30.6 | 9000 | 1587.8547 |  | 1
105 | 105 | 62 | 5.1542 | 301000 | 474425 | 30.2 | 9000 | 1587.8547 |  | 1
105 | 105 | 57 | -1.2082 | 284000 | 452300 | 30.1 | 9000 | 1587.8547 |  | 1
105 | 105 | 75 | 25.1345 | 377000 | 369900 | 31.5 | 10500 | 2369.2793 |  | 1
105 | 105 | 72 | 20.0232 | 361000 | 418225 | 31.2 | 10500 | 2369.2793 |  | 1
105 | 105 | 67 | 12.1996 | 334000 | 473000 | 30.7 | 10500 | 2190.0726 |  | 1
105 | 105 | 62 | 5.1542 | 308000 | 519000 | 30.5 | 10500 | 2190.0726 |  | 1
105 | 105 | 57 | -1.2082 | 297000 | 473137.5 | 30.2 | 10500 | 2190.0726 |  | 1
115 | 115 | 75 | 15.3648 | 330000 | 366000 | 34 | 6000 | 833.5196 |  | 1
115 | 115 | 72 | 11.5424 | 315000 | 384000 | 33.9 | 6000 | 833.5196 |  | 1
115 | 115 | 67 | 5.6915 | 289000 | 379040 | 33.9 | 6000 | 833.5196 |  | 1
115 | 115 | 62 | 0.42275 | 263000 | 412660 | 34.2 | 6000 | 758.5028 |  | 1
115 | 115 | 57 | -4.3353 | 237000 | 423420 | 34.6 | 6000 | 758.5028 |  | 1
115 | 115 | 75 | 15.3648 | 344000 | 429750 | 34.4 | 7500 | 1150.257 |  | 1
115 | 115 | 72 | 11.5424 | 328000 | 391225 | 34.3 | 7500 | 1150.257 |  | 1
115 | 115 | 67 | 5.6915 | 302000 | 442662.5 | 34.1 | 7500 | 1150.257 |  | 1
115 | 115 | 62 | 0.42275 | 276000 | 484437.5 | 34.3 | 7500 | 1066.905 |  | 1
115 | 115 | 57 | -4.3353 | 256000 | 466787.5 | 34.6 | 7500 | 1066.905 |  | 1
115 | 115 | 75 | 15.3648 | 352000 | 395015 | 34.7 | 9000 | 1762.8939 |  | 1
115 | 115 | 72 | 11.5424 | 337000 | 450735 | 34.6 | 9000 | 1587.8547 |  | 1
115 | 115 | 67 | 5.6915 | 310000 | 503130 | 34.3 | 9000 | 1587.8547 |  | 1
115 | 115 | 62 | 0.42275 | 285000 | 548595 | 34.4 | 9000 | 1587.8547 |  | 1
115 | 115 | 57 | -4.3353 | 272000 | 497225 | 34.5 | 9000 | 1500.3352 |  | 1
115 | 115 | 75 | 15.3648 | 360000 | 455145 | 35.1 | 10500 | 2369.2793 |  | 1
115 | 115 | 72 | 11.5424 | 344000 | 506357.5 | 34.8 | 10500 | 2190.0726 |  | 1
115 | 115 | 67 | 5.6915 | 317000 | 558400 | 34.4 | 10500 | 2190.0726 |  | 1
115 | 115 | 62 | 0.42275 | 291000 | 598357.5 | 34.5 | 10500 | 2190.0726 |  | 1
115 | 115 | 57 | -4.3353 | 285000 | 519465 | 34.4 | 10500 | 2190.0726 |  | 1
75 | 75 | 75 | 100 | 428000 | 138260 | 23.8 | 12000 | 3346.581 |  | 1
75 | 75 | 72 | 86.8609 | 408000 | 166980 | 23.3 | 12000 | 3346.581 |  | 1
75 | 75 | 67 | 66.7494 | 378000 | 221000 | 22.5 | 12000 | 3148.6201 |  | 1
75 | 75 | 62 | 48.6386 | 352000 | 275000 | 21.8 | 12000 | 3148.6201 |  | 1
75 | 75 | 57 | 32.2833 | 339000 | 299220 | 21.5 | 12000 | 2961.0782 |  | 1
75 | 75 | 75 | 100 | 434000 | 138307.5 | 24 | 13500 | 4332.2179 |  | 1
75 | 75 | 72 | 86.8609 | 414000 | 170852.5 | 23.4 | 13500 | 4332.2179 |  | 1
75 | 75 | 67 | 66.7494 | 383000 | 230110 | 22.6 | 13500 | 4132.1732 |  | 1
75 | 75 | 62 | 48.6386 | 357000 | 285852.5 | 21.9 | 13500 | 4132.1732 |  | 1
75 | 75 | 57 | 32.2833 | 349000 | 308702.5 | 21.8 | 13500 | 3944.6313 |  | 1
75 | 75 | 75 | 100 | 439000 | 137850 | 24.1 | 15000 | 5542.905 |  | 1
75 | 75 | 72 | 86.8609 | 418000 | 174550 | 23.6 | 15000 | 5542.905 |  | 1
75 | 75 | 67 | 66.7494 | 388000 | 238725 | 22.7 | 15000 | 5338.6927 |  | 1
75 | 75 | 62 | 48.6386 | 360000 | 295200 | 22 | 15000 | 5338.6927 |  | 1
75 | 75 | 57 | 32.2833 | 357000 | 315525 | 22 | 15000 | 5338.6927 |  | 1
85 | 85 | 75 | 63.5688 | 411000 | 222720 | 26 | 12000 | 3346.581 |  | 1
85 | 85 | 72 | 54.0993 | 395000 | 261680 | 25.5 | 12000 | 3148.6201 |  | 1
85 | 85 | 67 | 39.6049 | 368000 | 319000 | 24.8 | 12000 | 3148.6201 |  | 1
85 | 85 | 62 | 26.5524 | 341000 | 372000 | 24.3 | 12000 | 2961.0782 |  | 1
85 | 85 | 57 | 14.765 | 330000 | 368460 | 24 | 12000 | 2961.0782 |  | 1
85 | 85 | 75 | 63.5688 | 417000 | 235177.5 | 26.2 | 13500 | 4332.2179 |  | 1
85 | 85 | 72 | 54.0993 | 400000 | 276147.5 | 25.7 | 13500 | 4132.1732 |  | 1
85 | 85 | 67 | 39.6049 | 373000 | 338632.5 | 25 | 13500 | 4132.1732 |  | 1
85 | 85 | 62 | 26.5524 | 346000 | 388405 | 24.4 | 13500 | 3944.6313 |  | 1
85 | 85 | 57 | 14.765 | 340000 | 379555 | 24.2 | 13500 | 3944.6313 |  | 1
85 | 85 | 75 | 63.5688 | 422000 | 247975 | 26.3 | 15000 | 5542.905 |  | 1
85 | 85 | 72 | 54.0993 | 404000 | 291275 | 25.8 | 15000 | 5542.905 |  | 1
85 | 85 | 67 | 39.6049 | 376000 | 357275 | 25.1 | 15000 | 5338.6927 |  | 1
85 | 85 | 62 | 26.5524 | 349000 | 405975 | 24.4 | 15000 | 5146.9832 |  | 1
85 | 85 | 57 | 14.765 | 348000 | 388650 | 24.4 | 15000 | 5146.9832 |  | 1
95 | 95 | 75 | 40.2091 | 398000 | 313580 | 28.6 | 12000 | 3148.6201 |  | 1
95 | 95 | 72 | 33.2947 | 382000 | 359460 | 28.2 | 12000 | 3148.6201 |  | 1
95 | 95 | 67 | 22.7111 | 355000 | 417440 | 27.6 | 12000 | 3148.6201 |  | 1
95 | 95 | 62 | 13.1803 | 328000 | 465460 | 27.2 | 12000 | 2961.0782 |  | 1
95 | 95 | 57 | 4.5734 | 320000 | 432860 | 27 | 12000 | 2961.0782 |  | 1
95 | 95 | 75 | 40.2091 | 404000 | 339380 | 28.8 | 13500 | 4332.2179 |  | 1
95 | 95 | 72 | 33.2947 | 387000 | 386290 | 28.3 | 13500 | 4132.1732 |  | 1
95 | 95 | 67 | 22.7111 | 359000 | 448517.5 | 27.7 | 13500 | 4132.1732 |  | 1
95 | 95 | 62 | 13.1803 | 332000 | 491835 | 27.3 | 13500 | 3944.6313 |  | 1
95 | 95 | 57 | 4.5734 | 330000 | 445830 | 27.2 | 13500 | 3944.6313 |  | 1
95 | 95 | 75 | 40.2091 | 408000 | 363200 | 28.9 | 15000 | 5542.905 |  | 1
95 | 95 | 72 | 33.2947 | 391000 | 411625 | 28.5 | 15000 | 5338.6927 |  | 1
95 | 95 | 67 | 22.7111 | 363000 | 479100 | 27.8 | 15000 | 5338.6927 |  | 1
95 | 95 | 62 | 13.1803 | 339000 | 502300 | 27.3 | 15000 | 5146.9832 |  | 1
95 | 95 | 57 | 4.5734 | 338000 | 456800 | 27.3 | 15000 | 5146.9832 |  | 1
105 | 105 | 75 | 25.1345 | 383000 | 408900 | 31.7 | 12000 | 3148.6201 |  | 1
105 | 105 | 72 | 20.0232 | 367000 | 456100 | 31.4 | 12000 | 3148.6201 |  | 1
105 | 105 | 67 | 12.1996 | 340000 | 514400 | 30.9 | 12000 | 2961.0782 |  | 1
105 | 105 | 62 | 5.1542 | 313000 | 553800 | 30.5 | 12000 | 2961.0782 |  | 1
105 | 105 | 57 | -1.2082 | 308000 | 489500 | 30.4 | 12000 | 2961.0782 |  | 1
105 | 105 | 75 | 25.1345 | 388000 | 449725 | 31.9 | 13500 | 4132.1732 |  | 1
105 | 105 | 72 | 20.0232 | 371000 | 494150 | 31.5 | 13500 | 4132.1732 |  | 1
105 | 105 | 67 | 12.1996 | 344000 | 556862.5 | 31 | 13500 | 3944.6313 |  | 1
105 | 105 | 62 | 5.1542 | 320000 | 561450 | 30.4 | 13500 | 3944.6313 |  | 1
105 | 105 | 57 | -1.2082 | 317000 | 502625 | 30.6 | 13500 | 3944.6313 |  | 1
105 | 105 | 75 | 25.1345 | 392000 | 481125 | 32 | 15000 | 5338.6927 |  | 1
105 | 105 | 72 | 20.0232 | 375000 | 530375 | 31.6 | 15000 | 5338.6927 |  | 1
105 | 105 | 67 | 12.1996 | 347000 | 598500 | 31 | 15000 | 5146.9832 |  | 1
105 | 105 | 62 | 5.1542 | 326000 | 589125 | 30.7 | 15000 | 5146.9832 |  | 1
105 | 105 | 57 | -1.2082 | 325000 | 514750 | 30.7 | 15000 | 5146.9832 |  | 1
115 | 115 | 75 | 15.3648 | 365000 | 509500 | 35.3 | 12000 | 3148.6201 |  | 1
115 | 115 | 72 | 11.5424 | 349000 | 556360 | 35 | 12000 | 2961.0782 |  | 1
115 | 115 | 67 | 5.6915 | 322000 | 614980 | 34.5 | 12000 | 2961.0782 |  | 1
115 | 115 | 62 | 0.42275 | 296000 | 633880 | 34.4 | 12000 | 2961.0782 |  | 1
115 | 115 | 57 | -4.3353 | 295000 | 539860 | 34.5 | 12000 | 2961.0782 |  | 1
115 | 115 | 75 | 15.3648 | 369000 | 558812.5 | 35.4 | 13500 | 4132.1732 |  | 1
115 | 115 | 72 | 11.5424 | 353000 | 606207.5 | 35.1 | 13500 | 4132.1732 |  | 1
115 | 115 | 67 | 5.6915 | 326000 | 664207.5 | 34.6 | 13500 | 3944.6313 |  | 1
115 | 115 | 62 | 0.42275 | 303000 | 661627.5 | 34.5 | 13500 | 3944.6313 |  | 1
115 | 115 | 57 | -4.3353 | 303000 | 552480 | 34.5 | 13500 | 3944.6313 |  | 1
115 | 115 | 75 | 15.3648 | 372000 | 602350 | 35.5 | 15000 | 5338.6927 |  | 1
115 | 115 | 72 | 11.5424 | 356000 | 647125 | 35.2 | 15000 | 5338.6927 |  | 1
115 | 115 | 67 | 5.6915 | 329000 | 716900 | 34.6 | 15000 | 5146.9832 |  | 1
115 | 115 | 62 | 0.42275 | 311000 | 679600 | 34.5 | 15000 | 5146.9832 |  | 1
115 | 115 | 57 | -4.3353 | 310000 | 564100 | 34.5 | 15000 | 5146.9832 |  | 1
75 | 75 | 75 | 100 | 384000 | 137300 | 22.8 | 6000 | 983.5531 |  | 2
75 | 75 | 72 | 86.8609 | 367000 | 156300 | 22.3 | 6000 | 983.5531 |  | 2
75 | 75 | 67 | 66.7494 | 338000 | 181540 | 21.5 | 6000 | 833.5196 |  | 2
75 | 75 | 62 | 48.6386 | 312000 | 218168 | 20.8 | 6000 | 833.5196 |  | 2
75 | 75 | 57 | 32.2833 | 289000 | 250168 | 20.3 | 6000 | 833.5196 |  | 2
75 | 75 | 75 | 100 | 405000 | 138125 | 23.3 | 7500 | 1489.9162 |  | 2
75 | 75 | 72 | 86.8609 | 386000 | 157650 | 22.8 | 7500 | 1316.9609 |  | 2
75 | 75 | 67 | 66.7494 | 356000 | 197270 | 21.9 | 7500 | 1316.9609 |  | 2
75 | 75 | 62 | 48.6386 | 329000 | 239365 | 21.2 | 7500 | 1150.257 |  | 2
75 | 75 | 57 | 32.2833 | 307000 | 266062.5 | 20.6 | 7500 | 1150.257 |  | 2
75 | 75 | 75 | 100 | 418000 | 132295 | 23.7 | 9000 | 1948.352 |  | 2
75 | 75 | 72 | 86.8609 | 400000 | 162790 | 23.1 | 9000 | 1762.8939 |  | 2
75 | 75 | 67 | 66.7494 | 369000 | 209305 | 22.3 | 9000 | 1762.8939 |  | 2
75 | 75 | 62 | 48.6386 | 341000 | 257124 | 21.5 | 9000 | 1587.8547 |  | 2
75 | 75 | 57 | 32.2833 | 323000 | 285245 | 21.1 | 9000 | 1587.8547 |  | 2
75 | 75 | 75 | 100 | 429000 | 137220 | 23.9 | 10500 | 2558.905 |  | 2
75 | 75 | 72 | 86.8609 | 410000 | 167755 | 23.4 | 10500 | 2558.905 |  | 2
75 | 75 | 67 | 66.7494 | 378000 | 220600 | 22.5 | 10500 | 2369.2793 |  | 2
75 | 75 | 62 | 48.6386 | 351000 | 274022.5 | 21.8 | 10500 | 2369.2793 |  | 2
75 | 75 | 57 | 32.2833 | 338000 | 298572.5 | 21.5 | 10500 | 2190.0726 |  | 2
85 | 85 | 75 | 63.5688 | 373000 | 173700 | 25 | 6000 | 983.5531 |  | 2
85 | 85 | 72 | 54.0993 | 356000 | 192700 | 24.5 | 6000 | 983.5531 |  | 2
85 | 85 | 67 | 39.6049 | 330000 | 236584 | 23.7 | 6000 | 833.5196 |  | 2
85 | 85 | 62 | 26.5524 | 305000 | 267832 | 23.2 | 6000 | 833.5196 |  | 2
85 | 85 | 57 | 14.765 | 282000 | 298832 | 22.9 | 6000 | 833.5196 |  | 2
85 | 85 | 75 | 63.5688 | 392000 | 186875 | 25.5 | 7500 | 1316.9609 |  | 2
85 | 85 | 72 | 54.0993 | 373000 | 222175 | 25 | 7500 | 1316.9609 |  | 2
85 | 85 | 67 | 39.6049 | 346000 | 264730 | 24.2 | 7500 | 1150.257 |  | 2
85 | 85 | 62 | 26.5524 | 322000 | 304635 | 23.6 | 7500 | 1150.257 |  | 2
85 | 85 | 57 | 14.765 | 299000 | 333762.5 | 23.1 | 7500 | 1150.257 |  | 2
85 | 85 | 75 | 63.5688 | 404000 | 208250 | 25.9 | 9000 | 1948.352 |  | 2
85 | 85 | 72 | 54.0993 | 386000 | 242705 | 25.3 | 9000 | 1762.8939 |  | 2
85 | 85 | 67 | 39.6049 | 358000 | 292190 | 24.5 | 9000 | 1762.8939 |  | 2
85 | 85 | 62 | 26.5524 | 333000 | 338876 | 23.9 | 9000 | 1587.8547 |  | 2
85 | 85 | 57 | 14.765 | 317000 | 354260 | 23.5 | 9000 | 1587.8547 |  | 2
85 | 85 | 75 | 63.5688 | 414000 | 225935 | 26.1 | 10500 | 2558.905 |  | 2
85 | 85 | 72 | 54.0993 | 395000 | 261822.5 | 25.6 | 10500 | 2369.2793 |  | 2
85 | 85 | 67 | 39.6049 | 367000 | 317977.5 | 24.8 | 10500 | 2369.2793 |  | 2
85 | 85 | 62 | 26.5524 | 342000 | 371977.5 | 24.1 | 10500 | 2190.0726 |  | 2
85 | 85 | 57 | 14.765 | 331000 | 369850 | 23.9 | 10500 | 2190.0726 |  | 2
95 | 95 | 75 | 40.2091 | 360000 | 247000 | 27.5 | 6000 | 983.5531 |  | 2
95 | 95 | 72 | 33.2947 | 346000 | 258100 | 27.1 | 6000 | 833.5196 |  | 2
95 | 95 | 67 | 22.7111 | 322000 | 294090 | 26.5 | 6000 | 833.5196 |  | 2
95 | 95 | 62 | 13.1803 | 297000 | 329070 | 26.1 | 6000 | 833.5196 |  | 2
95 | 95 | 57 | 4.5734 | 272000 | 358070 | 26 | 6000 | 758.5028 |  | 2
95 | 95 | 75 | 40.2091 | 377000 | 279750 | 28 | 7500 | 1316.9609 |  | 2
95 | 95 | 72 | 33.2947 | 362000 | 290662.5 | 27.6 | 7500 | 1316.9609 |  | 2
95 | 95 | 67 | 22.7111 | 337000 | 337612.5 | 26.9 | 7500 | 1150.257 |  | 2
95 | 95 | 62 | 13.1803 | 312000 | 379850 | 26.5 | 7500 | 1150.257 |  | 2
95 | 95 | 57 | 4.5734 | 291000 | 393712.5 | 26.2 | 7500 | 1150.257 |  | 2
95 | 95 | 75 | 40.2091 | 389000 | 285285 | 28.4 | 9000 | 1762.8939 |  | 2
95 | 95 | 72 | 33.2947 | 374000 | 326680 | 27.9 | 9000 | 1762.8939 |  | 2
95 | 95 | 67 | 22.7111 | 348000 | 377650 | 27.2 | 9000 | 1587.8547 |  | 2
95 | 95 | 62 | 13.1803 | 323000 | 427135 | 26.7 | 9000 | 1587.8547 |  | 2
95 | 95 | 57 | 4.5734 | 309000 | 418890 | 26.5 | 9000 | 1587.8547 |  | 2
95 | 95 | 75 | 40.2091 | 399000 | 319530 | 28.7 | 10500 | 2369.2793 |  | 2
95 | 95 | 72 | 33.2947 | 383000 | 358727.5 | 28.2 | 10500 | 2369.2793 |  | 2
95 | 95 | 67 | 22.7111 | 356000 | 417192.5 | 27.5 | 10500 | 2369.2793 |  | 2
95 | 95 | 62 | 13.1803 | 331000 | 467460 | 27 | 10500 | 2190.0726 |  | 2
95 | 95 | 57 | 4.5734 | 323000 | 437345 | 26.8 | 10500 | 2190.0726 |  | 2
105 | 105 | 75 | 25.1345 | 350000 | 309000 | 30.5 | 6000 | 833.5196 |  | 2
105 | 105 | 72 | 20.0232 | 336000 | 301950 | 30.2 | 6000 | 833.5196 |  | 2
105 | 105 | 67 | 12.1996 | 311000 | 350800 | 29.8 | 6000 | 833.5196 |  | 2
105 | 105 | 62 | 5.1542 | 285000 | 386100 | 29.6 | 6000 | 833.5196 |  | 2
105 | 105 | 57 | -1.2082 | 260000 | 407150 | 29.9 | 6000 | 758.5028 |  | 2
105 | 105 | 75 | 25.1345 | 365000 | 331437.5 | 31 | 7500 | 1316.9609 |  | 2
105 | 105 | 72 | 20.0232 | 351000 | 360500 | 30.7 | 7500 | 1316.9609 |  | 2
105 | 105 | 67 | 12.1996 | 326000 | 407687.5 | 30.2 | 7500 | 1150.257 |  | 2
105 | 105 | 62 | 5.1542 | 300000 | 451812.5 | 29.9 | 7500 | 1150.257 |  | 2
105 | 105 | 57 | -1.2082 | 281000 | 446000 | 29.8 | 7500 | 1150.257 |  | 2
105 | 105 | 75 | 25.1345 | 377000 | 366425 | 31.4 | 9000 | 1762.8939 |  | 2
105 | 105 | 72 | 20.0232 | 362000 | 408800 | 31 | 9000 | 1762.8939 |  | 2
105 | 105 | 67 | 12.1996 | 336000 | 461750 | 30.5 | 9000 | 1587.8547 |  | 2
105 | 105 | 62 | 5.1542 | 310000 | 510225 | 30.3 | 9000 | 1587.8547 |  | 2
105 | 105 | 57 | -1.2082 | 298000 | 473725 | 30 | 9000 | 1587.8547 |  | 2
105 | 105 | 75 | 25.1345 | 386000 | 415437.5 | 31.7 | 10500 | 2369.2793 |  | 2
105 | 105 | 72 | 20.0232 | 370000 | 457100 | 31.3 | 10500 | 2369.2793 |  | 2
105 | 105 | 67 | 12.1996 | 343000 | 513987.5 | 30.7 | 10500 | 2190.0726 |  | 2
105 | 105 | 62 | 5.1542 | 317000 | 561100 | 30.5 | 10500 | 2190.0726 |  | 2
105 | 105 | 57 | -1.2082 | 312000 | 496800 | 30.3 | 10500 | 2190.0726 |  | 2
115 | 115 | 75 | 15.3648 | 338000 | 369000 | 34.1 | 6000 | 833.5196 |  | 2
115 | 115 | 72 | 11.5424 | 323000 | 358660 | 33.9 | 6000 | 833.5196 |  | 2
115 | 115 | 67 | 5.6915 | 297000 | 407830 | 33.7 | 6000 | 833.5196 |  | 2
115 | 115 | 62 | 0.42275 | 272000 | 442140 | 33.9 | 6000 | 758.5028 |  | 2
115 | 115 | 57 | -4.3353 | 247000 | 449280 | 34.8 | 6000 | 758.5028 |  | 2
115 | 115 | 75 | 15.3648 | 351000 | 379000 | 34.5 | 7500 | 1316.9609 |  | 2
115 | 115 | 72 | 11.5424 | 337000 | 429987.5 | 34.4 | 7500 | 1150.257 |  | 2
115 | 115 | 67 | 5.6915 | 310000 | 479650 | 34.1 | 7500 | 1150.257 |  | 2
115 | 115 | 62 | 0.42275 | 285000 | 521537.5 | 34.1 | 7500 | 1150.257 |  | 2
115 | 115 | 57 | -4.3353 | 269000 | 491337.5 | 34.5 | 7500 | 1066.905 |  | 2
115 | 115 | 75 | 15.3648 | 362000 | 450525 | 35 | 9000 | 1762.8939 |  | 2
115 | 115 | 72 | 11.5424 | 346000 | 494385 | 34.7 | 9000 | 1587.8547 |  | 2
115 | 115 | 67 | 5.6915 | 320000 | 544850 | 34.3 | 9000 | 1587.8547 |  | 2
115 | 115 | 62 | 0.42275 | 294000 | 589850 | 34.5 | 9000 | 1587.8547 |  | 2
115 | 115 | 57 | -4.3353 | 285000 | 520620 | 34.4 | 9000 | 1587.8547 |  | 2
115 | 115 | 75 | 15.3648 | 370000 | 511655 | 35.3 | 10500 | 2369.2793 |  | 2
115 | 115 | 72 | 11.5424 | 353000 | 552740 | 35 | 10500 | 2369.2793 |  | 2
115 | 115 | 67 | 5.6915 | 326000 | 610782.5 | 34.5 | 10500 | 2190.0726 |  | 2
115 | 115 | 62 | 0.42275 | 302000 | 638612.5 | 34.5 | 10500 | 2190.0726 |  | 2
115 | 115 | 57 | -4.3353 | 299000 | 545592.5 | 34.5 | 10500 | 2190.0726 |  | 2
75 | 75 | 75 | 100 | 437000 | 137360 | 24.2 | 12000 | 3346.581 |  | 2
75 | 75 | 72 | 86.8609 | 417000 | 172720 | 23.6 | 12000 | 3346.581 |  | 2
75 | 75 | 67 | 66.7494 | 385000 | 232060 | 22.7 | 12000 | 3148.6201 |  | 2
75 | 75 | 62 | 48.6386 | 356000 | 286720 | 21.9 | 12000 | 3148.6201 |  | 2
75 | 75 | 57 | 32.2833 | 350000 | 308900 | 21.8 | 12000 | 2961.0782 |  | 2
75 | 75 | 75 | 100 | 444000 | 138655 | 24.3 | 13500 | 4332.2179 |  | 2
75 | 75 | 72 | 86.8609 | 423000 | 177427.5 | 23.8 | 13500 | 4332.2179 |  | 2
75 | 75 | 67 | 66.7494 | 391000 | 242685 | 22.9 | 13500 | 4132.1732 |  | 2
75 | 75 | 62 | 48.6386 | 361000 | 298397.5 | 22.1 | 13500 | 4132.1732 |  | 2
75 | 75 | 57 | 32.2833 | 360000 | 318217.5 | 22.1 | 13500 | 4132.1732 |  | 2
75 | 75 | 75 | 100 | 449000 | 138950 | 24.5 | 15000 | 5542.905 |  | 2
75 | 75 | 72 | 86.8609 | 428000 | 180475 | 23.9 | 15000 | 5542.905 |  | 2
75 | 75 | 67 | 66.7494 | 396000 | 253475 | 23 | 15000 | 5338.6927 |  | 2
75 | 75 | 62 | 48.6386 | 370000 | 307900 | 22.3 | 15000 | 5338.6927 |  | 2
75 | 75 | 57 | 32.2833 | 369000 | 325875 | 22.3 | 15000 | 5338.6927 |  | 2
85 | 85 | 75 | 63.5688 | 421000 | 240300 | 26.4 | 12000 | 3346.581 |  | 2
85 | 85 | 72 | 54.0993 | 402000 | 279280 | 25.8 | 12000 | 3346.581 |  | 2
85 | 85 | 67 | 39.6049 | 373000 | 341600 | 25 | 12000 | 3148.6201 |  | 2
85 | 85 | 62 | 26.5524 | 348000 | 393620 | 24.3 | 12000 | 2961.0782 |  | 2
85 | 85 | 57 | 14.765 | 343000 | 382780 | 24.2 | 12000 | 2961.0782 |  | 2
85 | 85 | 75 | 63.5688 | 427000 | 254087.5 | 26.5 | 13500 | 4332.2179 |  | 2
85 | 85 | 72 | 54.0993 | 407000 | 297315 | 26 | 13500 | 4332.2179 |  | 2
85 | 85 | 67 | 39.6049 | 378000 | 364315 | 25.1 | 13500 | 4132.1732 |  | 2
85 | 85 | 62 | 26.5524 | 353000 | 409860 | 24.4 | 13500 | 4132.1732 |  | 2
85 | 85 | 57 | 14.765 | 353000 | 394040 | 24.4 | 13500 | 4132.1732 |  | 2
85 | 85 | 75 | 63.5688 | 432000 | 267875 | 26.6 | 15000 | 5542.905 |  | 2
85 | 85 | 72 | 54.0993 | 412000 | 314525 | 26.1 | 15000 | 5542.905 |  | 2
85 | 85 | 67 | 39.6049 | 382000 | 387525 | 25.2 | 15000 | 5338.6927 |  | 2
85 | 85 | 62 | 26.5524 | 362000 | 422450 | 24.7 | 15000 | 5338.6927 |  | 2
85 | 85 | 57 | 14.765 | 361000 | 403300 | 24.7 | 15000 | 5338.6927 |  | 2
95 | 95 | 75 | 40.2091 | 406000 | 347320 | 28.9 | 12000 | 3346.581 |  | 2
95 | 95 | 72 | 33.2947 | 389000 | 391260 | 28.4 | 12000 | 3148.6201 |  | 2
95 | 95 | 67 | 22.7111 | 362000 | 454240 | 27.7 | 12000 | 3148.6201 |  | 2
95 | 95 | 62 | 13.1803 | 337000 | 497320 | 27.1 | 12000 | 2961.0782 |  | 2
95 | 95 | 57 | 4.5734 | 334000 | 452800 | 27 | 12000 | 2961.0782 |  | 2
95 | 95 | 75 | 40.2091 | 411000 | 375110 | 29 | 13500 | 4332.2179 |  | 2
95 | 95 | 72 | 33.2947 | 395000 | 421565 | 28.6 | 13500 | 4132.1732 |  | 2
95 | 95 | 67 | 22.7111 | 367000 | 490792.5 | 27.8 | 13500 | 4132.1732 |  | 2
95 | 95 | 62 | 13.1803 | 344000 | 517745 | 27.3 | 13500 | 3944.6313 |  | 2
95 | 95 | 57 | 4.5734 | 344000 | 466512.5 | 27.3 | 13500 | 3944.6313 |  | 2
95 | 95 | 75 | 40.2091 | 416000 | 400425 | 29.2 | 15000 | 5542.905 |  | 2
95 | 95 | 72 | 33.2947 | 399000 | 447900 | 28.7 | 15000 | 5338.6927 |  | 2
95 | 95 | 67 | 22.7111 | 370000 | 525850 | 27.9 | 15000 | 5338.6927 |  | 2
95 | 95 | 62 | 13.1803 | 352000 | 530200 | 27.5 | 15000 | 5338.6927 |  | 2
95 | 95 | 57 | 4.5734 | 352000 | 475750 | 27.5 | 15000 | 5338.6927 |  | 2
105 | 105 | 75 | 25.1345 | 392000 | 457500 | 31.9 | 12000 | 3148.6201 |  | 2
105 | 105 | 72 | 20.0232 | 376000 | 501100 | 31.5 | 12000 | 3148.6201 |  | 2
105 | 105 | 67 | 12.1996 | 348000 | 565400 | 30.9 | 12000 | 2961.0782 |  | 2
105 | 105 | 62 | 5.1542 | 324000 | 591600 | 30.4 | 12000 | 2961.0782 |  | 2
105 | 105 | 57 | -1.2082 | 323000 | 514400 | 30.5 | 12000 | 2961.0782 |  | 2
105 | 105 | 75 | 25.1345 | 397000 | 495850 | 32.1 | 13500 | 4132.1732 |  | 2
105 | 105 | 72 | 20.0232 | 380000 | 544275 | 31.7 | 13500 | 4132.1732 |  | 2
105 | 105 | 67 | 12.1996 | 353000 | 614987.5 | 31 | 13500 | 4132.1732 |  | 2
105 | 105 | 62 | 5.1542 | 333000 | 603725 | 30.6 | 13500 | 3944.6313 |  | 2
105 | 105 | 57 | -1.2082 | 332000 | 528762.5 | 30.7 | 13500 | 3944.6313 |  | 2
105 | 105 | 75 | 25.1345 | 402000 | 537500 | 32.3 | 15000 | 5542.905 |  | 2
105 | 105 | 72 | 20.0232 | 384000 | 581500 | 31.8 | 15000 | 5338.6927 |  | 2
105 | 105 | 67 | 12.1996 | 356000 | 658625 | 31.2 | 15000 | 5338.6927 |  | 2
105 | 105 | 62 | 5.1542 | 340000 | 628750 | 30.9 | 15000 | 5146.9832 |  | 2
105 | 105 | 57 | -1.2082 | 340000 | 542125 | 30.9 | 15000 | 5146.9832 |  | 2
115 | 115 | 75 | 15.3648 | 375000 | 564700 | 35.5 | 12000 | 3148.6201 |  | 2
115 | 115 | 72 | 11.5424 | 359000 | 610940 | 35.2 | 12000 | 3148.6201 |  | 2
115 | 115 | 67 | 5.6915 | 331000 | 674560 | 34.6 | 12000 | 2961.0782 |  | 2
115 | 115 | 62 | 0.42275 | 311000 | 659740 | 34.3 | 12000 | 2961.0782 |  | 2
115 | 115 | 57 | -4.3353 | 309000 | 563100 | 34.5 | 12000 | 2961.0782 |  | 2
115 | 115 | 75 | 15.3648 | 380000 | 620787.5 | 35.7 | 13500 | 4132.1732 |  | 2
115 | 115 | 72 | 11.5424 | 363000 | 665985 | 35.3 | 13500 | 4132.1732 |  | 2
115 | 115 | 67 | 5.6915 | 335000 | 737182.5 | 34.8 | 13500 | 3944.6313 |  | 2
115 | 115 | 62 | 0.42275 | 318000 | 697417.5 | 34.7 | 13500 | 3944.6313 |  | 2
115 | 115 | 57 | -4.3353 | 318000 | 583072.5 | 34.6 | 13500 | 3944.6313 |  | 2
115 | 115 | 75 | 15.3648 | 384000 | 670100 | 35.9 | 15000 | 5338.6927 |  | 2
115 | 115 | 72 | 11.5424 | 366000 | 719875 | 35.5 | 15000 | 5338.6927 |  | 2
115 | 115 | 67 | 5.6915 | 338000 | 791875 | 34.9 | 15000 | 5146.9832 |  | 2
115 | 115 | 62 | 0.42275 | 325000 | 711925 | 34.8 | 15000 | 5146.9832 |  | 2
115 | 115 | 57 | -4.3353 | 325000 | 596425 | 34.7 | 15000 | 5146.9832 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 2
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Net
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 75 | 75 | 100 | 437000 | 152850 | 27 | 7000 | 83922.9162 |  | 1
75 | 75 | 72 | 86.8609 | 419000 | 175850 | 26.3 | 7000 | 83922.9162 |  | 1
75 | 75 | 67 | 66.7494 | 387000 | 208015 | 25.3 | 7000 | 63710.067 |  | 1
75 | 75 | 62 | 48.6386 | 358000 | 248674 | 24.4 | 7000 | 63710.067 |  | 1
75 | 75 | 57 | 32.2833 | 332000 | 285674 | 23.8 | 7000 | 188496.2793 |  | 1
75 | 75 | 75 | 100 | 459000 | 152812.5 | 27.7 | 8750 | 87650.8324 |  | 1
75 | 75 | 72 | 86.8609 | 439000 | 176887.5 | 27 | 8750 | 87650.8324 |  | 1
75 | 75 | 67 | 66.7494 | 407000 | 223518.75 | 25.9 | 8750 | 87650.8324 |  | 1
75 | 75 | 62 | 48.6386 | 377000 | 270037.5 | 24.9 | 8750 | 69780.1732 |  | 1
75 | 75 | 57 | 32.2833 | 352000 | 303887.5 | 24.2 | 8750 | 69780.1732 |  | 1
75 | 75 | 75 | 100 | 466000 | 156793.75 | 27.9 | 9625 | 89801.3128 |  | 1
75 | 75 | 72 | 86.8609 | 446000 | 179917.5 | 27.2 | 9625 | 89801.3128 |  | 1
75 | 75 | 67 | 66.7494 | 414000 | 230800 | 26.1 | 9625 | 89801.3128 |  | 1
75 | 75 | 62 | 48.6386 | 384000 | 280741.25 | 25.1 | 9625 | 73210.1061 |  | 1
75 | 75 | 57 | 32.2833 | 361000 | 319035 | 24.5 | 9625 | 73210.1061 |  | 1
75 | 75 | 75 | 100 | 472000 | 145755 | 28.1 | 10500 | 92485.2458 |  | 1
75 | 75 | 72 | 86.8609 | 453000 | 182910 | 27.4 | 10500 | 92485.2458 |  | 1
75 | 75 | 67 | 66.7494 | 420000 | 237600 | 26.3 | 10500 | 92485.2458 |  | 1
75 | 75 | 62 | 48.6386 | 389000 | 292022.5 | 25.3 | 10500 | 76960.9441 |  | 1
75 | 75 | 57 | 32.2833 | 370000 | 326530 | 24.7 | 10500 | 76960.9441 |  | 1
85 | 85 | 75 | 63.5688 | 424000 | 196150 | 29.5 | 7000 | 83922.9162 |  | 1
85 | 85 | 72 | 54.0993 | 406000 | 220150 | 28.8 | 7000 | 83922.9162 |  | 1
85 | 85 | 67 | 39.6049 | 377000 | 271370 | 27.8 | 7000 | 63710.067 |  | 1
85 | 85 | 62 | 26.5524 | 350000 | 309326 | 27 | 7000 | 188496.2793 |  | 1
85 | 85 | 57 | 14.765 | 323000 | 345326 | 26.6 | 7000 | 188496.2793 |  | 1
85 | 85 | 75 | 63.5688 | 444000 | 210187.5 | 30.1 | 8750 | 87650.8324 |  | 1
85 | 85 | 72 | 54.0993 | 424000 | 251075 | 29.4 | 8750 | 87650.8324 |  | 1
85 | 85 | 67 | 39.6049 | 395000 | 303481.25 | 28.4 | 8750 | 69780.1732 |  | 1
85 | 85 | 62 | 26.5524 | 368000 | 350685 | 27.5 | 8750 | 69780.1732 |  | 1
85 | 85 | 57 | 14.765 | 344000 | 378112.5 | 26.9 | 8750 | 205589.6816 |  | 1
85 | 85 | 75 | 63.5688 | 450000 | 218206.25 | 30.4 | 9625 | 89801.3128 |  | 1
85 | 85 | 72 | 54.0993 | 432000 | 262611.875 | 29.7 | 9625 | 89801.3128 |  | 1
85 | 85 | 67 | 39.6049 | 402000 | 318200 | 28.6 | 9625 | 89801.3128 |  | 1
85 | 85 | 62 | 26.5524 | 375000 | 372258.75 | 27.7 | 9625 | 73210.1061 |  | 1
85 | 85 | 57 | 14.765 | 353000 | 394435.625 | 27.2 | 9625 | 73210.1061 |  | 1
85 | 85 | 75 | 63.5688 | 456000 | 232892.5 | 30.6 | 10500 | 92485.2458 |  | 1
85 | 85 | 72 | 54.0993 | 438000 | 273667.5 | 29.9 | 10500 | 92485.2458 |  | 1
85 | 85 | 67 | 39.6049 | 408000 | 333400 | 28.8 | 10500 | 92485.2458 |  | 1
85 | 85 | 62 | 26.5524 | 380000 | 389977.5 | 27.9 | 10500 | 76960.9441 |  | 1
85 | 85 | 57 | 14.765 | 363000 | 405315 | 27.4 | 10500 | 76960.9441 |  | 1
95 | 95 | 75 | 40.2091 | 409000 | 281500 | 32.3 | 7000 | 83922.9162 |  | 1
95 | 95 | 72 | 33.2947 | 394000 | 294950 | 31.7 | 7000 | 63710.067 |  | 1
95 | 95 | 67 | 22.7111 | 368000 | 336950 | 30.9 | 7000 | 63710.067 |  | 1
95 | 95 | 62 | 13.1803 | 340000 | 378260 | 30.3 | 7000 | 188496.2793 |  | 1
95 | 95 | 57 | 4.5734 | 311000 | 409105 | 30 | 7000 | 188496.2793 |  | 1
95 | 95 | 75 | 40.2091 | 427000 | 319375 | 32.9 | 8750 | 87650.8324 |  | 1
95 | 95 | 72 | 33.2947 | 411000 | 328718.75 | 32.3 | 8750 | 87650.8324 |  | 1
95 | 95 | 67 | 22.7111 | 384000 | 385937.5 | 31.4 | 8750 | 69780.1732 |  | 1
95 | 95 | 62 | 13.1803 | 357000 | 435381.25 | 30.7 | 8750 | 69780.1732 |  | 1
95 | 95 | 57 | 4.5734 | 333000 | 451387.5 | 30.4 | 8750 | 205589.6816 |  | 1
95 | 95 | 75 | 40.2091 | 433000 | 294933.125 | 33.2 | 9625 | 89801.3128 |  | 1
95 | 95 | 72 | 33.2947 | 418000 | 350578.75 | 32.5 | 9625 | 89801.3128 |  | 1
95 | 95 | 67 | 22.7111 | 391000 | 408343.125 | 31.6 | 9625 | 73210.1061 |  | 1
95 | 95 | 62 | 13.1803 | 363000 | 461931.25 | 30.9 | 9625 | 73210.1061 |  | 1
95 | 95 | 57 | 4.5734 | 344000 | 466285.625 | 30.6 | 9625 | 215246.0056 |  | 1
95 | 95 | 75 | 40.2091 | 438000 | 320867.5 | 33.4 | 10500 | 92485.2458 |  | 1
95 | 95 | 72 | 33.2947 | 423000 | 368995 | 32.7 | 10500 | 92485.2458 |  | 1
95 | 95 | 67 | 22.7111 | 397000 | 430460 | 31.8 | 10500 | 76960.9441 |  | 1
95 | 95 | 62 | 13.1803 | 369000 | 488192.5 | 31.1 | 10500 | 76960.9441 |  | 1
95 | 95 | 57 | 4.5734 | 353000 | 477740 | 30.8 | 10500 | 76960.9441 |  | 1
105 | 105 | 75 | 25.1345 | 398000 | 353500 | 35.7 | 7000 | 63710.067 |  | 1
105 | 105 | 72 | 20.0232 | 382000 | 344850 | 35.2 | 7000 | 63710.067 |  | 1
105 | 105 | 67 | 12.1996 | 355000 | 403175 | 34.6 | 7000 | 63710.067 |  | 1
105 | 105 | 62 | 5.1542 | 327000 | 442100 | 34.2 | 7000 | 188496.2793 |  | 1
105 | 105 | 57 | -1.2082 | 298000 | 466325 | 34.4 | 7000 | 188496.2793 |  | 1
105 | 105 | 75 | 25.1345 | 413000 | 376937.5 | 36.3 | 8750 | 87650.8324 |  | 1
105 | 105 | 72 | 20.0232 | 399000 | 408937.5 | 35.8 | 8750 | 69780.1732 |  | 1
105 | 105 | 67 | 12.1996 | 371000 | 467562.5 | 35.1 | 8750 | 69780.1732 |  | 1
105 | 105 | 62 | 5.1542 | 343000 | 515968.75 | 34.6 | 8750 | 205589.6816 |  | 1
105 | 105 | 57 | -1.2082 | 321000 | 511093.75 | 34.4 | 8750 | 205589.6816 |  | 1
105 | 105 | 75 | 25.1345 | 419000 | 384103.125 | 36.5 | 9625 | 89801.3128 |  | 1
105 | 105 | 72 | 20.0232 | 405000 | 439278.125 | 36 | 9625 | 89801.3128 |  | 1
105 | 105 | 67 | 12.1996 | 377000 | 497571.875 | 35.3 | 9625 | 73210.1061 |  | 1
105 | 105 | 62 | 5.1542 | 349000 | 551218.75 | 34.8 | 9625 | 215246.0056 |  | 1
105 | 105 | 57 | -1.2082 | 332000 | 527868.75 | 34.6 | 9625 | 215246.0056 |  | 1
105 | 105 | 75 | 25.1345 | 425000 | 413887.5 | 36.7 | 10500 | 92485.2458 |  | 1
105 | 105 | 72 | 20.0232 | 410000 | 467212.5 | 36.2 | 10500 | 92485.2458 |  | 1
105 | 105 | 67 | 12.1996 | 382000 | 526100 | 35.4 | 10500 | 76960.9441 |  | 1
105 | 105 | 62 | 5.1542 | 354000 | 582987.5 | 35.1 | 10500 | 76960.9441 |  | 1
105 | 105 | 57 | -1.2082 | 341000 | 543125 | 34.8 | 10500 | 225698.3408 |  | 1
115 | 115 | 75 | 15.3648 | 383000 | 423500 | 39.6 | 7000 | 63710.067 |  | 1
115 | 115 | 72 | 11.5424 | 367000 | 410075 | 39.3 | 7000 | 63710.067 |  | 1
115 | 115 | 67 | 5.6915 | 339000 | 466245 | 38.9 | 7000 | 188496.2793 |  | 1
115 | 115 | 62 | 0.42275 | 311000 | 508635 | 39.1 | 7000 | 188496.2793 |  | 1
115 | 115 | 57 | -4.3353 | 284000 | 514770 | 39.9 | 7000 | 188496.2793 |  | 1
115 | 115 | 75 | 15.3648 | 397000 | 427762.5 | 40.2 | 8750 | 69780.1732 |  | 1
115 | 115 | 72 | 11.5424 | 382000 | 489081.25 | 39.9 | 8750 | 69780.1732 |  | 1
115 | 115 | 67 | 5.6915 | 354000 | 546187.5 | 39.4 | 8750 | 69780.1732 |  | 1
115 | 115 | 62 | 0.42275 | 326000 | 596556.25 | 39.3 | 8750 | 205589.6816 |  | 1
115 | 115 | 57 | -4.3353 | 308000 | 564025 | 39.7 | 8750 | 205589.6816 |  | 1
115 | 115 | 75 | 15.3648 | 403000 | 473861.25 | 40.5 | 9625 | 89801.3128 |  | 1
115 | 115 | 72 | 11.5424 | 388000 | 525389.375 | 40.1 | 9625 | 73210.1061 |  | 1
115 | 115 | 67 | 5.6915 | 359000 | 583800.625 | 39.6 | 9625 | 73210.1061 |  | 1
115 | 115 | 62 | 0.42275 | 332000 | 637506.25 | 39.5 | 9625 | 215246.0056 |  | 1
115 | 115 | 57 | -4.3353 | 318000 | 581099.375 | 39.6 | 9625 | 215246.0056 |  | 1
115 | 115 | 75 | 15.3648 | 408000 | 510527.5 | 40.7 | 10500 | 92485.2458 |  | 1
115 | 115 | 72 | 11.5424 | 393000 | 561697.5 | 40.3 | 10500 | 76960.9441 |  | 1
115 | 115 | 67 | 5.6915 | 364000 | 624782.5 | 39.7 | 10500 | 76960.9441 |  | 1
115 | 115 | 62 | 0.42275 | 336000 | 677782.5 | 39.8 | 10500 | 225698.3408 |  | 1
115 | 115 | 57 | -4.3353 | 327000 | 597847.5 | 39.7 | 10500 | 225698.3408 |  | 1
75 | 75 | 75 | 100 | 482000 | 152043.75 | 28.5 | 12225 | 98707.4693 |  | 1
75 | 75 | 72 | 86.8609 | 463000 | 188009.5 | 27.8 | 12225 | 98707.4693 |  | 1
75 | 75 | 67 | 66.7494 | 430000 | 250992.375 | 26.6 | 12225 | 98707.4693 |  | 1
75 | 75 | 62 | 48.6386 | 400000 | 312992.375 | 25.6 | 12225 | 84979.4022 |  | 1
75 | 75 | 57 | 32.2833 | 386000 | 340767.5 | 25.2 | 12225 | 84979.4022 |  | 1
75 | 75 | 75 | 100 | 491000 | 151960 | 28.8 | 14000 | 106123.7095 |  | 1
75 | 75 | 72 | 86.8609 | 471000 | 192880 | 28 | 14000 | 106123.7095 |  | 1
75 | 75 | 67 | 66.7494 | 438000 | 263340 | 26.9 | 14000 | 106123.7095 |  | 1
75 | 75 | 62 | 48.6386 | 406000 | 326880 | 25.8 | 14000 | 106123.7095 |  | 1
75 | 75 | 57 | 32.2833 | 400000 | 353590 | 25.6 | 14000 | 94246.0559 |  | 1
75 | 75 | 75 | 100 | 496000 | 152600 | 28.9 | 15000 | 110733.0726 |  | 1
75 | 75 | 72 | 86.8609 | 475000 | 195300 | 28.2 | 15000 | 110733.0726 |  | 1
75 | 75 | 67 | 66.7494 | 442000 | 270475 | 27 | 15000 | 110733.0726 |  | 1
75 | 75 | 62 | 48.6386 | 411000 | 333775 | 26 | 15000 | 110733.0726 |  | 1
75 | 75 | 57 | 32.2833 | 406000 | 358750 | 25.8 | 15000 | 110733.0726 |  | 1
85 | 85 | 75 | 63.5688 | 466000 | 252301 | 30.9 | 12225 | 98707.4693 |  | 1
85 | 85 | 72 | 54.0993 | 447000 | 295662.875 | 30.2 | 12225 | 98707.4693 |  | 1
85 | 85 | 67 | 39.6049 | 417000 | 361007.625 | 29.1 | 12225 | 98707.4693 |  | 1
85 | 85 | 62 | 26.5524 | 390000 | 424007.625 | 28.2 | 12225 | 84979.4022 |  | 1
85 | 85 | 57 | 14.765 | 379000 | 422887.75 | 27.9 | 12225 | 84979.4022 |  | 1
85 | 85 | 75 | 63.5688 | 475000 | 269810 | 31.2 | 14000 | 106123.7095 |  | 1
85 | 85 | 72 | 54.0993 | 455000 | 316120 | 30.5 | 14000 | 106123.7095 |  | 1
85 | 85 | 67 | 39.6049 | 424000 | 388660 | 29.3 | 14000 | 106123.7095 |  | 1
85 | 85 | 62 | 26.5524 | 397000 | 449350 | 28.4 | 14000 | 94246.0559 |  | 1
85 | 85 | 57 | 14.765 | 392000 | 437640 | 28.3 | 14000 | 94246.0559 |  | 1
85 | 85 | 75 | 63.5688 | 478000 | 278225 | 31.4 | 15000 | 110733.0726 |  | 1
85 | 85 | 72 | 54.0993 | 458000 | 327700 | 30.6 | 15000 | 110733.0726 |  | 1
85 | 85 | 67 | 39.6049 | 427000 | 403525 | 29.4 | 15000 | 110733.0726 |  | 1
85 | 85 | 62 | 26.5524 | 400000 | 460400 | 28.5 | 15000 | 99688.9385 |  | 1
85 | 85 | 57 | 14.765 | 398000 | 444425 | 28.5 | 15000 | 99688.9385 |  | 1
95 | 95 | 75 | 40.2091 | 449000 | 358404.25 | 33.7 | 12225 | 98707.4693 |  | 1
95 | 95 | 72 | 33.2947 | 433000 | 407472.75 | 33.1 | 12225 | 98707.4693 |  | 1
95 | 95 | 67 | 22.7111 | 405000 | 474489.875 | 32.1 | 12225 | 98707.4693 |  | 1
95 | 95 | 62 | 13.1803 | 378000 | 535489.875 | 31.4 | 12225 | 84979.4022 |  | 1
95 | 95 | 57 | 4.5734 | 369000 | 500113.125 | 31.1 | 12225 | 84979.4022 |  | 1
95 | 95 | 75 | 40.2091 | 456000 | 391420 | 34 | 14000 | 106123.7095 |  | 1
95 | 95 | 72 | 33.2947 | 439000 | 442350 | 33.3 | 14000 | 106123.7095 |  | 1
95 | 95 | 67 | 22.7111 | 412000 | 517660 | 32.3 | 14000 | 106123.7095 |  | 1
95 | 95 | 62 | 13.1803 | 385000 | 568730 | 31.6 | 14000 | 94246.0559 |  | 1
95 | 95 | 57 | 4.5734 | 382000 | 515980 | 31.5 | 14000 | 94246.0559 |  | 1
95 | 95 | 75 | 40.2091 | 460000 | 408950 | 34.1 | 15000 | 110733.0726 |  | 1
95 | 95 | 72 | 33.2947 | 442000 | 460900 | 33.4 | 15000 | 110733.0726 |  | 1
95 | 95 | 67 | 22.7111 | 415000 | 540375 | 32.4 | 15000 | 110733.0726 |  | 1
95 | 95 | 62 | 13.1803 | 389000 | 571575 | 31.6 | 15000 | 99688.9385 |  | 1
95 | 95 | 57 | 4.5734 | 388000 | 524125 | 31.6 | 15000 | 99688.9385 |  | 1
105 | 105 | 75 | 25.1345 | 435000 | 468035.625 | 37.1 | 12225 | 98707.4693 |  | 1
105 | 105 | 72 | 20.0232 | 418000 | 518121.25 | 36.5 | 12225 | 98707.4693 |  | 1
105 | 105 | 67 | 12.1996 | 390000 | 585483.125 | 35.7 | 12225 | 84979.4022 |  | 1
105 | 105 | 62 | 5.1542 | 362000 | 633759.375 | 35.2 | 12225 | 84979.4022 |  | 1
105 | 105 | 57 | -1.2082 | 356000 | 564436.25 | 35.1 | 12225 | 84979.4022 |  | 1
105 | 105 | 75 | 25.1345 | 441000 | 516550 | 37.4 | 14000 | 106123.7095 |  | 1
105 | 105 | 72 | 20.0232 | 425000 | 568250 | 36.8 | 14000 | 106123.7095 |  | 1
105 | 105 | 67 | 12.1996 | 396000 | 644100 | 35.9 | 14000 | 94246.0559 |  | 1
105 | 105 | 62 | 5.1542 | 370000 | 667150 | 35.3 | 14000 | 94246.0559 |  | 1
105 | 105 | 57 | -1.2082 | 369000 | 584600 | 35.3 | 14000 | 94246.0559 |  | 1
105 | 105 | 75 | 25.1345 | 444000 | 544375 | 37.5 | 15000 | 110733.0726 |  | 1
105 | 105 | 72 | 20.0232 | 428000 | 599625 | 36.9 | 15000 | 110733.0726 |  | 1
105 | 105 | 67 | 12.1996 | 399000 | 674625 | 36 | 15000 | 99688.9385 |  | 1
105 | 105 | 62 | 5.1542 | 376000 | 673250 | 35.4 | 15000 | 99688.9385 |  | 1
105 | 105 | 57 | -1.2082 | 375000 | 597750 | 35.5 | 15000 | 99688.9385 |  | 1
115 | 115 | 75 | 15.3648 | 417000 | 578356.5 | 41.1 | 12225 | 98707.4693 |  | 1
115 | 115 | 72 | 11.5424 | 400000 | 627769.75 | 40.6 | 12225 | 84979.4022 |  | 1
115 | 115 | 67 | 5.6915 | 371000 | 695476.375 | 39.9 | 12225 | 84979.4022 |  | 1
115 | 115 | 62 | 0.42275 | 345000 | 727649.875 | 39.8 | 12225 | 247853.2905 |  | 1
115 | 115 | 57 | -4.3353 | 341000 | 623397.5 | 39.8 | 12225 | 247853.2905 |  | 1
115 | 115 | 75 | 15.3648 | 423000 | 644760 | 41.4 | 14000 | 106123.7095 |  | 1
115 | 115 | 72 | 11.5424 | 406000 | 698540 | 40.9 | 14000 | 106123.7095 |  | 1
115 | 115 | 67 | 5.6915 | 377000 | 768540 | 40.1 | 14000 | 94246.0559 |  | 1
115 | 115 | 62 | 0.42275 | 355000 | 751250 | 39.6 | 14000 | 94246.0559 |  | 1
115 | 115 | 57 | -4.3353 | 353000 | 644060 | 39.9 | 14000 | 94246.0559 |  | 1
115 | 115 | 75 | 15.3648 | 425000 | 675325 | 41.5 | 15000 | 110733.0726 |  | 1
115 | 115 | 72 | 11.5424 | 409000 | 732875 | 41 | 15000 | 110733.0726 |  | 1
115 | 115 | 67 | 5.6915 | 380000 | 807875 | 40.2 | 15000 | 99688.9385 |  | 1
115 | 115 | 62 | 0.42275 | 359000 | 786350 | 40 | 15000 | 99688.9385 |  | 1
115 | 115 | 57 | -4.3353 | 359000 | 653525 | 40 | 15000 | 99688.9385 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 3
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Net
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 75 | 75 | 100 | 477000 | 167400 | 24.8 | 8000 | 1521.1732 |  | 1
75 | 75 | 72 | 86.8609 | 458000 | 182400 | 24.5 | 8000 | 1521.1732 |  | 1
75 | 75 | 67 | 66.7494 | 420000 | 218400 | 24 | 8000 | 1521.1732 |  | 1
75 | 75 | 62 | 48.6386 | 383000 | 252840 | 23.6 | 8000 | 1352.3855 |  | 1
75 | 75 | 57 | 32.2833 | 348000 | 284760 | 23.3 | 8000 | 1189.8492 |  | 1
75 | 75 | 75 | 100 | 501000 | 171500 | 25.3 | 10000 | 2413.0391 |  | 1
75 | 75 | 72 | 86.8609 | 483000 | 185500 | 24.9 | 10000 | 2221.3296 |  | 1
75 | 75 | 67 | 66.7494 | 443000 | 237850 | 24.3 | 10000 | 2221.3296 |  | 1
75 | 75 | 62 | 48.6386 | 405000 | 275450 | 23.9 | 10000 | 2221.3296 |  | 1
75 | 75 | 57 | 32.2833 | 367000 | 310450 | 23.5 | 10000 | 2033.7877 |  | 1
75 | 75 | 75 | 100 | 519000 | 165600 | 25.7 | 12000 | 3415.3464 |  | 1
75 | 75 | 72 | 86.8609 | 497000 | 195600 | 25.2 | 12000 | 3194.4637 |  | 1
75 | 75 | 67 | 66.7494 | 458000 | 248240 | 24.6 | 12000 | 3194.4637 |  | 1
75 | 75 | 62 | 48.6386 | 420000 | 294600 | 24.1 | 12000 | 3194.4637 |  | 1
75 | 75 | 57 | 32.2833 | 383000 | 329900 | 23.5 | 12000 | 2975.6648 |  | 1
75 | 75 | 75 | 100 | 533000 | 161700 | 26 | 14000 | 4732.3073 |  | 1
75 | 75 | 72 | 86.8609 | 508000 | 189500 | 25.5 | 14000 | 4732.3073 |  | 1
75 | 75 | 67 | 66.7494 | 469000 | 258280 | 24.8 | 14000 | 4478.0838 |  | 1
75 | 75 | 62 | 48.6386 | 431000 | 312970 | 24.2 | 14000 | 4478.0838 |  | 1
75 | 75 | 57 | 32.2833 | 397000 | 350590 | 23.9 | 14000 | 4223.8603 |  | 1
85 | 85 | 75 | 63.5688 | 467000 | 218600 | 27.5 | 8000 | 1521.1732 |  | 1
85 | 85 | 72 | 54.0993 | 447000 | 233600 | 27.3 | 8000 | 1521.1732 |  | 1
85 | 85 | 67 | 39.6049 | 409000 | 268600 | 26.9 | 8000 | 1521.1732 |  | 1
85 | 85 | 62 | 26.5524 | 371000 | 307040 | 26.6 | 8000 | 1352.3855 |  | 1
85 | 85 | 57 | 14.765 | 338000 | 343240 | 26.3 | 8000 | 1189.8492 |  | 1
85 | 85 | 75 | 63.5688 | 490000 | 236500 | 28 | 10000 | 2221.3296 |  | 1
85 | 85 | 72 | 54.0993 | 471000 | 252500 | 27.7 | 10000 | 2221.3296 |  | 1
85 | 85 | 67 | 39.6049 | 431000 | 300800 | 27.1 | 10000 | 2221.3296 |  | 1
85 | 85 | 62 | 26.5524 | 393000 | 346100 | 26.8 | 10000 | 2033.7877 |  | 1
85 | 85 | 57 | 14.765 | 356000 | 377550 | 26.5 | 10000 | 2033.7877 |  | 1
85 | 85 | 75 | 63.5688 | 507000 | 244400 | 28.3 | 12000 | 3415.3464 |  | 1
85 | 85 | 72 | 54.0993 | 485000 | 274400 | 27.9 | 12000 | 3194.4637 |  | 1
85 | 85 | 67 | 39.6049 | 446000 | 328420 | 27.4 | 12000 | 3194.4637 |  | 1
85 | 85 | 62 | 26.5524 | 407000 | 379060 | 27 | 12000 | 3194.4637 |  | 1
85 | 85 | 57 | 14.765 | 370000 | 409420 | 26.6 | 12000 | 2975.6648 |  | 1
85 | 85 | 75 | 63.5688 | 520000 | 253300 | 28.6 | 14000 | 4732.3073 |  | 1
85 | 85 | 72 | 54.0993 | 497000 | 288560 | 28.2 | 14000 | 4478.0838 |  | 1
85 | 85 | 67 | 39.6049 | 457000 | 350720 | 27.6 | 14000 | 4478.0838 |  | 1
85 | 85 | 62 | 26.5524 | 419000 | 409030 | 27.1 | 14000 | 4478.0838 |  | 1
85 | 85 | 57 | 14.765 | 388000 | 431870 | 26.8 | 14000 | 4223.8603 |  | 1
95 | 95 | 75 | 40.2091 | 455000 | 318000 | 30.7 | 8000 | 1521.1732 |  | 1
95 | 95 | 72 | 33.2947 | 435000 | 331000 | 30.6 | 8000 | 1521.1732 |  | 1
95 | 95 | 67 | 22.7111 | 397000 | 369000 | 30.2 | 8000 | 1352.3855 |  | 1
95 | 95 | 62 | 13.1803 | 359000 | 363400 | 30 | 8000 | 1352.3855 |  | 1
95 | 95 | 57 | 4.5734 | 326000 | 401680 | 29.8 | 8000 | 1189.8492 |  | 1
95 | 95 | 75 | 40.2091 | 479000 | 355000 | 31.2 | 10000 | 2221.3296 |  | 1
95 | 95 | 72 | 33.2947 | 457000 | 379000 | 30.9 | 10000 | 2221.3296 |  | 1
95 | 95 | 67 | 22.7111 | 418000 | 369900 | 30.5 | 10000 | 2221.3296 |  | 1
95 | 95 | 62 | 13.1803 | 379000 | 419150 | 30.2 | 10000 | 2033.7877 |  | 1
95 | 95 | 57 | 4.5734 | 341000 | 449500 | 29.9 | 10000 | 1850.4134 |  | 1
95 | 95 | 75 | 40.2091 | 494000 | 392000 | 31.5 | 12000 | 3194.4637 |  | 1
95 | 95 | 72 | 33.2947 | 470000 | 427000 | 31.1 | 12000 | 3194.4637 |  | 1
95 | 95 | 67 | 22.7111 | 431000 | 410680 | 30.7 | 12000 | 3194.4637 |  | 1
95 | 95 | 62 | 13.1803 | 393000 | 464620 | 30.4 | 12000 | 2975.6648 |  | 1
95 | 95 | 57 | 4.5734 | 360000 | 480740 | 30 | 12000 | 2975.6648 |  | 1
95 | 95 | 75 | 40.2091 | 504000 | 434000 | 31.7 | 14000 | 4732.3073 |  | 1
95 | 95 | 72 | 33.2947 | 482000 | 374980 | 31.3 | 14000 | 4478.0838 |  | 1
95 | 95 | 67 | 22.7111 | 441000 | 446150 | 30.9 | 14000 | 4478.0838 |  | 1
95 | 95 | 62 | 13.1803 | 404000 | 509080 | 30.5 | 14000 | 4478.0838 |  | 1
95 | 95 | 57 | 4.5734 | 377000 | 510980 | 30.3 | 14000 | 4223.8603 |  | 1
105 | 105 | 75 | 25.1345 | 440000 | 400000 | 34.4 | 8000 | 1521.1732 |  | 1
105 | 105 | 72 | 20.0232 | 420000 | 412000 | 34.4 | 8000 | 1521.1732 |  | 1
105 | 105 | 67 | 12.1996 | 382000 | 358600 | 34.1 | 8000 | 1352.3855 |  | 1
105 | 105 | 62 | 5.1542 | 346000 | 421200 | 34.2 | 8000 | 1189.8492 |  | 1
105 | 105 | 57 | -1.2082 | 312000 | 455600 | 34.5 | 8000 | 1189.8492 |  | 1
105 | 105 | 75 | 25.1345 | 463000 | 459000 | 34.9 | 10000 | 2221.3296 |  | 1
105 | 105 | 72 | 20.0232 | 440000 | 484000 | 34.7 | 10000 | 2221.3296 |  | 1
105 | 105 | 67 | 12.1996 | 401000 | 441000 | 34.4 | 10000 | 2221.3296 |  | 1
105 | 105 | 62 | 5.1542 | 364000 | 490250 | 34.2 | 10000 | 2033.7877 |  | 1
105 | 105 | 57 | -1.2082 | 330000 | 505250 | 34.3 | 10000 | 1850.4134 |  | 1
105 | 105 | 75 | 25.1345 | 477000 | 519000 | 35.1 | 12000 | 3194.4637 |  | 1
105 | 105 | 72 | 20.0232 | 453000 | 407800 | 34.9 | 12000 | 3194.4637 |  | 1
105 | 105 | 67 | 12.1996 | 413000 | 490100 | 34.6 | 12000 | 3194.4637 |  | 1
105 | 105 | 62 | 5.1542 | 377000 | 552000 | 34.3 | 12000 | 2975.6648 |  | 1
105 | 105 | 57 | -1.2082 | 347000 | 551600 | 34.4 | 12000 | 2758.9497 |  | 1
105 | 105 | 75 | 25.1345 | 486000 | 584000 | 35.3 | 14000 | 4478.0838 |  | 1
105 | 105 | 72 | 20.0232 | 464000 | 469850 | 35.1 | 14000 | 4478.0838 |  | 1
105 | 105 | 67 | 12.1996 | 424000 | 539250 | 34.8 | 14000 | 4478.0838 |  | 1
105 | 105 | 62 | 5.1542 | 387000 | 606800 | 34.3 | 14000 | 4223.8603 |  | 1
105 | 105 | 57 | -1.2082 | 364000 | 579600 | 34.4 | 14000 | 4223.8603 |  | 1
115 | 115 | 75 | 15.3648 | 422000 | 482000 | 38.7 | 8000 | 1521.1732 |  | 1
115 | 115 | 72 | 11.5424 | 406000 | 495000 | 38.4 | 8000 | 1521.1732 |  | 1
115 | 115 | 67 | 5.6915 | 365000 | 427280 | 38.9 | 8000 | 1352.3855 |  | 1
115 | 115 | 62 | 0.42275 | 330000 | 478760 | 39.4 | 8000 | 1189.8492 |  | 1
115 | 115 | 57 | -4.3353 | 297000 | 501680 | 40.3 | 8000 | 1189.8492 |  | 1
115 | 115 | 75 | 15.3648 | 443000 | 563000 | 39.1 | 10000 | 2221.3296 |  | 1
115 | 115 | 72 | 11.5424 | 420000 | 588000 | 39 | 10000 | 2221.3296 |  | 1
115 | 115 | 67 | 5.6915 | 383000 | 512650 | 38.9 | 10000 | 2033.7877 |  | 1
115 | 115 | 62 | 0.42275 | 347000 | 565200 | 39.2 | 10000 | 1850.4134 |  | 1
115 | 115 | 57 | -4.3353 | 315000 | 566100 | 39.8 | 10000 | 1850.4134 |  | 1
115 | 115 | 75 | 15.3648 | 456000 | 645000 | 39.3 | 12000 | 3194.4637 |  | 1
115 | 115 | 72 | 11.5424 | 434000 | 498820 | 39.2 | 12000 | 3194.4637 |  | 1
115 | 115 | 67 | 5.6915 | 395000 | 579160 | 39.1 | 12000 | 2975.6648 |  | 1
115 | 115 | 62 | 0.42275 | 359000 | 642020 | 39.1 | 12000 | 2975.6648 |  | 1
115 | 115 | 57 | -4.3353 | 334000 | 611200 | 39.6 | 12000 | 2758.9497 |  | 1
115 | 115 | 75 | 15.3648 | 466000 | 732000 | 39.5 | 14000 | 4478.0838 |  | 1
115 | 115 | 72 | 11.5424 | 443000 | 568570 | 39.4 | 14000 | 4478.0838 |  | 1
115 | 115 | 67 | 5.6915 | 404000 | 637740 | 39.1 | 14000 | 4478.0838 |  | 1
115 | 115 | 62 | 0.42275 | 368000 | 702520 | 39.2 | 14000 | 4223.8603 |  | 1
115 | 115 | 57 | -4.3353 | 350000 | 641060 | 39.4 | 14000 | 3969.6369 |  | 1
75 | 75 | 75 | 100 | 542000 | 164800 | 26.2 | 16000 | 6397.2626 |  | 1
75 | 75 | 72 | 86.8609 | 518000 | 211480 | 25.7 | 16000 | 6397.2626 |  | 1
75 | 75 | 67 | 66.7494 | 478000 | 269200 | 24.9 | 16000 | 6105.5307 |  | 1
75 | 75 | 62 | 48.6386 | 440000 | 329440 | 24.4 | 16000 | 6105.5307 |  | 1
75 | 75 | 57 | 32.2833 | 413000 | 365240 | 24 | 16000 | 6105.5307 |  | 1
75 | 75 | 75 | 100 | 549000 | 165900 | 26.4 | 18000 | 8453.9721 |  | 1
75 | 75 | 72 | 86.8609 | 525000 | 214310 | 25.8 | 18000 | 8453.9721 |  | 1
75 | 75 | 67 | 66.7494 | 486000 | 278340 | 25.1 | 18000 | 8124.7318 |  | 1
75 | 75 | 62 | 48.6386 | 447000 | 344350 | 24.5 | 18000 | 8124.7318 |  | 1
75 | 75 | 57 | 32.2833 | 426000 | 376230 | 24.2 | 18000 | 8124.7318 |  | 1
75 | 75 | 75 | 100 | 557000 | 181700 | 26.5 | 20000 | 10948.2793 |  | 1
75 | 75 | 72 | 86.8609 | 531000 | 217900 | 25.9 | 20000 | 10948.2793 |  | 1
75 | 75 | 67 | 66.7494 | 491000 | 287700 | 25.2 | 20000 | 10573.1955 |  | 1
75 | 75 | 62 | 48.6386 | 453000 | 357700 | 24.6 | 20000 | 10573.1955 |  | 1
75 | 75 | 57 | 32.2833 | 438000 | 387100 | 24.4 | 20000 | 10573.1955 |  | 1
85 | 85 | 75 | 63.5688 | 527000 | 271200 | 28.8 | 16000 | 6397.2626 |  | 1
85 | 85 | 72 | 54.0993 | 505000 | 308280 | 28.3 | 16000 | 6397.2626 |  | 1
85 | 85 | 67 | 39.6049 | 465000 | 373800 | 27.7 | 16000 | 6105.5307 |  | 1
85 | 85 | 62 | 26.5524 | 427000 | 436560 | 27.3 | 16000 | 6105.5307 |  | 1
85 | 85 | 57 | 14.765 | 402000 | 448880 | 27 | 16000 | 6105.5307 |  | 1
85 | 85 | 75 | 63.5688 | 535000 | 295540 | 29 | 18000 | 8453.9721 |  | 1
85 | 85 | 72 | 54.0993 | 512000 | 325690 | 28.5 | 18000 | 8453.9721 |  | 1
85 | 85 | 67 | 39.6049 | 472000 | 394660 | 27.8 | 18000 | 8124.7318 |  | 1
85 | 85 | 62 | 26.5524 | 434000 | 463640 | 27.3 | 18000 | 8124.7318 |  | 1
85 | 85 | 57 | 14.765 | 416000 | 464780 | 27.1 | 18000 | 8124.7318 |  | 1
85 | 85 | 75 | 63.5688 | 541000 | 288400 | 29.1 | 20000 | 10948.2793 |  | 1
85 | 85 | 72 | 54.0993 | 518000 | 341100 | 28.6 | 20000 | 10948.2793 |  | 1
85 | 85 | 67 | 39.6049 | 478000 | 416300 | 27.9 | 20000 | 10573.1955 |  | 1
85 | 85 | 62 | 26.5524 | 440000 | 481300 | 27.5 | 20000 | 10573.1955 |  | 1
85 | 85 | 57 | 14.765 | 427000 | 476800 | 27.3 | 20000 | 10573.1955 |  | 1
95 | 95 | 75 | 40.2091 | 512000 | 476000 | 31.8 | 16000 | 6397.2626 |  | 1
95 | 95 | 72 | 33.2947 | 490000 | 410400 | 31.5 | 16000 | 6105.5307 |  | 1
95 | 95 | 67 | 22.7111 | 450000 | 481960 | 31 | 16000 | 6105.5307 |  | 1
95 | 95 | 62 | 13.1803 | 412000 | 544600 | 30.6 | 16000 | 6105.5307 |  | 1
95 | 95 | 57 | 4.5734 | 391000 | 530920 | 30.4 | 16000 | 5811.7151 |  | 1
95 | 95 | 75 | 40.2091 | 520000 | 358590 | 32.1 | 18000 | 8453.9721 |  | 1
95 | 95 | 72 | 33.2947 | 496000 | 441200 | 31.6 | 18000 | 8124.7318 |  | 1
95 | 95 | 67 | 22.7111 | 456000 | 516110 | 31.1 | 18000 | 8124.7318 |  | 1
95 | 95 | 62 | 13.1803 | 419000 | 578110 | 30.7 | 18000 | 8124.7318 |  | 1
95 | 95 | 57 | 4.5734 | 404000 | 546560 | 30.5 | 18000 | 8124.7318 |  | 1
95 | 95 | 75 | 40.2091 | 527000 | 405200 | 32.2 | 20000 | 10948.2793 |  | 1
95 | 95 | 72 | 33.2947 | 502000 | 470000 | 31.8 | 20000 | 10948.2793 |  | 1
95 | 95 | 67 | 22.7111 | 462000 | 548600 | 31.2 | 20000 | 10573.1955 |  | 1
95 | 95 | 62 | 13.1803 | 423000 | 603300 | 30.8 | 20000 | 10573.1955 |  | 1
95 | 95 | 57 | 4.5734 | 415000 | 563500 | 30.7 | 20000 | 10573.1955 |  | 1
105 | 105 | 75 | 25.1345 | 494000 | 428000 | 35.4 | 16000 | 6105.5307 |  | 1
105 | 105 | 72 | 20.0232 | 471000 | 518800 | 35.2 | 16000 | 6105.5307 |  | 1
105 | 105 | 67 | 12.1996 | 432000 | 592000 | 34.8 | 16000 | 6105.5307 |  | 1
105 | 105 | 62 | 5.1542 | 394000 | 651000 | 34.5 | 16000 | 5811.7151 |  | 1
105 | 105 | 57 | -1.2082 | 378000 | 602400 | 34.4 | 16000 | 5811.7151 |  | 1
105 | 105 | 75 | 25.1345 | 502000 | 482300 | 35.7 | 18000 | 8453.9721 |  | 1
105 | 105 | 72 | 20.0232 | 477000 | 569850 | 35.2 | 18000 | 8124.7318 |  | 1
105 | 105 | 67 | 12.1996 | 438000 | 633850 | 34.9 | 18000 | 8124.7318 |  | 1
105 | 105 | 62 | 5.1542 | 401000 | 684900 | 34.5 | 18000 | 8124.7318 |  | 1
105 | 105 | 57 | -1.2082 | 391000 | 623650 | 34.4 | 18000 | 7787.1564 |  | 1
105 | 105 | 75 | 25.1345 | 507000 | 530000 | 35.8 | 20000 | 10948.2793 |  | 1
105 | 105 | 72 | 20.0232 | 483000 | 602500 | 35.5 | 20000 | 10573.1955 |  | 1
105 | 105 | 67 | 12.1996 | 443000 | 678000 | 35 | 20000 | 10573.1955 |  | 1
105 | 105 | 62 | 5.1542 | 405000 | 725000 | 34.6 | 20000 | 10573.1955 |  | 1
105 | 105 | 57 | -1.2082 | 400000 | 636500 | 34.6 | 20000 | 10187.6927 |  | 1
115 | 115 | 75 | 15.3648 | 473000 | 527480 | 39.7 | 16000 | 6105.5307 |  | 1
115 | 115 | 72 | 11.5424 | 450000 | 628080 | 39.6 | 16000 | 6105.5307 |  | 1
115 | 115 | 67 | 5.6915 | 411000 | 699400 | 39.1 | 16000 | 6105.5307 |  | 1
115 | 115 | 62 | 0.42275 | 375000 | 754400 | 39.3 | 16000 | 5811.7151 |  | 1
115 | 115 | 57 | -4.3353 | 365000 | 666840 | 39 | 16000 | 5811.7151 |  | 1
115 | 115 | 75 | 15.3648 | 480000 | 610940 | 39.9 | 18000 | 8124.7318 |  | 1
115 | 115 | 72 | 11.5424 | 456000 | 686590 | 39.7 | 18000 | 8124.7318 |  | 1
115 | 115 | 67 | 5.6915 | 417000 | 757520 | 39.2 | 18000 | 8124.7318 |  | 1
115 | 115 | 62 | 0.42275 | 382000 | 778800 | 39.3 | 18000 | 7787.1564 |  | 1
115 | 115 | 57 | -4.3353 | 375000 | 686850 | 39.3 | 18000 | 7787.1564 |  | 1
115 | 115 | 75 | 15.3648 | 484000 | 661600 | 40 | 20000 | 10573.1955 |  | 1
115 | 115 | 72 | 11.5424 | 461000 | 737400 | 39.7 | 20000 | 10573.1955 |  | 1
115 | 115 | 67 | 5.6915 | 421000 | 815100 | 39.2 | 20000 | 10573.1955 |  | 1
115 | 115 | 62 | 0.42275 | 389000 | 796500 | 39 | 20000 | 10187.6927 |  | 1
115 | 115 | 57 | -4.3353 | 384000 | 699700 | 39.3 | 20000 | 10187.6927 |  | 1
75 | 75 | 75 | 100 | 502000 | 179400 | 25.5 | 8000 | 1696.2123 |  | 2
75 | 75 | 72 | 86.8609 | 480000 | 199400 | 25 | 8000 | 1521.1732 |  | 2
75 | 75 | 67 | 66.7494 | 439000 | 235920 | 24.2 | 8000 | 1521.1732 |  | 2
75 | 75 | 62 | 48.6386 | 404000 | 276160 | 23.5 | 8000 | 1521.1732 |  | 2
75 | 75 | 57 | 32.2833 | 369000 | 313600 | 23.1 | 8000 | 1352.3855 |  | 2
75 | 75 | 75 | 100 | 531000 | 182500 | 26.1 | 10000 | 2413.0391 |  | 2
75 | 75 | 72 | 86.8609 | 504000 | 206500 | 25.5 | 10000 | 2413.0391 |  | 2
75 | 75 | 67 | 66.7494 | 464000 | 254100 | 24.6 | 10000 | 2221.3296 |  | 2
75 | 75 | 62 | 48.6386 | 427000 | 305000 | 24 | 10000 | 2221.3296 |  | 2
75 | 75 | 57 | 32.2833 | 395000 | 344300 | 23.5 | 10000 | 2033.7877 |  | 2
75 | 75 | 75 | 100 | 550000 | 172380 | 26.4 | 12000 | 3415.3464 |  | 2
75 | 75 | 72 | 86.8609 | 523000 | 213020 | 25.9 | 12000 | 3415.3464 |  | 2
75 | 75 | 67 | 66.7494 | 480000 | 270380 | 25 | 12000 | 3194.4637 |  | 2
75 | 75 | 62 | 48.6386 | 443000 | 330060 | 24.2 | 12000 | 3194.4637 |  | 2
75 | 75 | 57 | 32.2833 | 417000 | 367980 | 23.8 | 12000 | 3194.4637 |  | 2
75 | 75 | 75 | 100 | 565000 | 171800 | 26.7 | 14000 | 4732.3073 |  | 2
75 | 75 | 72 | 86.8609 | 537000 | 219420 | 26.1 | 14000 | 4732.3073 |  | 2
75 | 75 | 67 | 66.7494 | 493000 | 284880 | 25.2 | 14000 | 4478.0838 |  | 2
75 | 75 | 62 | 48.6386 | 456000 | 352880 | 24.5 | 14000 | 4478.0838 |  | 2
75 | 75 | 57 | 32.2833 | 436000 | 384970 | 24.2 | 14000 | 4478.0838 |  | 2
85 | 85 | 75 | 63.5688 | 490000 | 229600 | 28 | 8000 | 1521.1732 |  | 2
85 | 85 | 72 | 54.0993 | 469000 | 251600 | 27.6 | 8000 | 1521.1732 |  | 2
85 | 85 | 67 | 39.6049 | 432000 | 307080 | 26.9 | 8000 | 1521.1732 |  | 2
85 | 85 | 62 | 26.5524 | 397000 | 350840 | 26.4 | 8000 | 1352.3855 |  | 2
85 | 85 | 57 | 14.765 | 360000 | 384400 | 26.1 | 8000 | 1352.3855 |  | 2
85 | 85 | 75 | 63.5688 | 518000 | 245500 | 28.6 | 10000 | 2413.0391 |  | 2
85 | 85 | 72 | 54.0993 | 493000 | 288050 | 28.1 | 10000 | 2221.3296 |  | 2
85 | 85 | 67 | 39.6049 | 456000 | 343900 | 27.3 | 10000 | 2221.3296 |  | 2
85 | 85 | 62 | 26.5524 | 419000 | 397000 | 26.8 | 10000 | 2221.3296 |  | 2
85 | 85 | 57 | 14.765 | 386000 | 426150 | 26.3 | 10000 | 2033.7877 |  | 2
85 | 85 | 75 | 63.5688 | 536000 | 279940 | 29 | 12000 | 3415.3464 |  | 2
85 | 85 | 72 | 54.0993 | 511000 | 315640 | 28.4 | 12000 | 3415.3464 |  | 2
85 | 85 | 67 | 39.6049 | 472000 | 377620 | 27.6 | 12000 | 3194.4637 |  | 2
85 | 85 | 62 | 26.5524 | 435000 | 439940 | 27 | 12000 | 3194.4637 |  | 2
85 | 85 | 57 | 14.765 | 410000 | 457700 | 26.7 | 12000 | 3194.4637 |  | 2
85 | 85 | 75 | 63.5688 | 551000 | 291420 | 29.3 | 14000 | 4732.3073 |  | 2
85 | 85 | 72 | 54.0993 | 523000 | 340350 | 28.6 | 14000 | 4732.3073 |  | 2
85 | 85 | 67 | 39.6049 | 484000 | 410120 | 27.9 | 14000 | 4478.0838 |  | 2
85 | 85 | 62 | 26.5524 | 447000 | 476120 | 27.3 | 14000 | 4478.0838 |  | 2
85 | 85 | 57 | 14.765 | 429000 | 479260 | 27 | 14000 | 4478.0838 |  | 2
95 | 95 | 75 | 40.2091 | 480000 | 329000 | 31.1 | 8000 | 1521.1732 |  | 2
95 | 95 | 72 | 33.2947 | 461000 | 353000 | 30.7 | 8000 | 1521.1732 |  | 2
95 | 95 | 67 | 22.7111 | 423000 | 377200 | 30.3 | 8000 | 1521.1732 |  | 2
95 | 95 | 62 | 13.1803 | 387000 | 424480 | 30 | 8000 | 1352.3855 |  | 2
95 | 95 | 57 | 4.5734 | 350000 | 453840 | 29.9 | 8000 | 1189.8492 |  | 2
95 | 95 | 75 | 40.2091 | 507000 | 373000 | 31.7 | 10000 | 2413.0391 |  | 2
95 | 95 | 72 | 33.2947 | 484000 | 374000 | 31.2 | 10000 | 2221.3296 |  | 2
95 | 95 | 67 | 22.7111 | 445000 | 434900 | 30.6 | 10000 | 2221.3296 |  | 2
95 | 95 | 62 | 13.1803 | 408000 | 489200 | 30.3 | 10000 | 2221.3296 |  | 2
95 | 95 | 57 | 4.5734 | 375000 | 508650 | 30.1 | 10000 | 2033.7877 |  | 2
95 | 95 | 75 | 40.2091 | 526000 | 394240 | 32.1 | 12000 | 3415.3464 |  | 2
95 | 95 | 72 | 33.2947 | 501000 | 422340 | 31.6 | 12000 | 3415.3464 |  | 2
95 | 95 | 67 | 22.7111 | 461000 | 486300 | 31 | 12000 | 3194.4637 |  | 2
95 | 95 | 62 | 13.1803 | 423000 | 549260 | 30.6 | 12000 | 3194.4637 |  | 2
95 | 95 | 57 | 4.5734 | 400000 | 542560 | 30.3 | 12000 | 2975.6648 |  | 2
95 | 95 | 75 | 40.2091 | 539000 | 406560 | 32.4 | 14000 | 4732.3073 |  | 2
95 | 95 | 72 | 33.2947 | 514000 | 462420 | 31.9 | 14000 | 4732.3073 |  | 2
95 | 95 | 67 | 22.7111 | 472000 | 535040 | 31.2 | 14000 | 4478.0838 |  | 2
95 | 95 | 62 | 13.1803 | 434000 | 598040 | 30.8 | 14000 | 4478.0838 |  | 2
95 | 95 | 57 | 4.5734 | 419000 | 566840 | 30.6 | 14000 | 4478.0838 |  | 2
105 | 105 | 75 | 25.1345 | 470000 | 413000 | 34.8 | 8000 | 1521.1732 |  | 2
105 | 105 | 72 | 20.0232 | 448000 | 410600 | 34.6 | 8000 | 1521.1732 |  | 2
105 | 105 | 67 | 12.1996 | 409000 | 448200 | 34.5 | 8000 | 1521.1732 |  | 2
105 | 105 | 62 | 5.1542 | 372000 | 498000 | 34.5 | 8000 | 1352.3855 |  | 2
105 | 105 | 57 | -1.2082 | 336000 | 518200 | 35.7 | 8000 | 1189.8492 |  | 2
105 | 105 | 75 | 25.1345 | 495000 | 478000 | 35.5 | 10000 | 2221.3296 |  | 2
105 | 105 | 72 | 20.0232 | 471000 | 462500 | 35.2 | 10000 | 2221.3296 |  | 2
105 | 105 | 67 | 12.1996 | 431000 | 526250 | 34.8 | 10000 | 2221.3296 |  | 2
105 | 105 | 62 | 5.1542 | 393000 | 581750 | 34.7 | 10000 | 2033.7877 |  | 2
105 | 105 | 57 | -1.2082 | 363000 | 577500 | 35 | 10000 | 2033.7877 |  | 2
105 | 105 | 75 | 25.1345 | 512000 | 509700 | 36 | 12000 | 3415.3464 |  | 2
105 | 105 | 72 | 20.0232 | 485000 | 530200 | 35.5 | 12000 | 3194.4637 |  | 2
105 | 105 | 67 | 12.1996 | 445000 | 595800 | 35.1 | 12000 | 3194.4637 |  | 2
105 | 105 | 62 | 5.1542 | 406000 | 656100 | 35 | 12000 | 3194.4637 |  | 2
105 | 105 | 57 | -1.2082 | 387000 | 614700 | 35 | 12000 | 2975.6648 |  | 2
105 | 105 | 75 | 25.1345 | 524000 | 526300 | 36.4 | 14000 | 4732.3073 |  | 2
105 | 105 | 72 | 20.0232 | 498000 | 582700 | 36 | 14000 | 4478.0838 |  | 2
105 | 105 | 67 | 12.1996 | 455000 | 663250 | 35.2 | 14000 | 4478.0838 |  | 2
105 | 105 | 62 | 5.1542 | 416000 | 712550 | 35.2 | 14000 | 4478.0838 |  | 2
105 | 105 | 57 | -1.2082 | 406000 | 644700 | 35.1 | 14000 | 4478.0838 |  | 2
115 | 115 | 75 | 15.3648 | 454000 | 494000 | 39.5 | 8000 | 1521.1732 |  | 2
115 | 115 | 72 | 11.5424 | 431000 | 491280 | 39.6 | 8000 | 1521.1732 |  | 2
115 | 115 | 67 | 5.6915 | 392000 | 519960 | 40.1 | 8000 | 1352.3855 |  | 2
115 | 115 | 62 | 0.42275 | 355000 | 568200 | 41.4 | 8000 | 1352.3855 |  | 2
115 | 115 | 57 | -4.3353 | 319000 | 579800 | 44 | 8000 | 1189.8492 |  | 2
115 | 115 | 75 | 15.3648 | 478000 | 529100 | 40.4 | 10000 | 2221.3296 |  | 2
115 | 115 | 72 | 11.5424 | 452000 | 553400 | 40.1 | 10000 | 2221.3296 |  | 2
115 | 115 | 67 | 5.6915 | 412000 | 613950 | 40.3 | 10000 | 2221.3296 |  | 2
115 | 115 | 62 | 0.42275 | 373000 | 670650 | 41.3 | 10000 | 2033.7877 |  | 2
115 | 115 | 57 | -4.3353 | 349000 | 637750 | 42.6 | 10000 | 1850.4134 |  | 2
115 | 115 | 75 | 15.3648 | 491000 | 564740 | 40.8 | 12000 | 3194.4637 |  | 2
115 | 115 | 72 | 11.5424 | 466000 | 633080 | 40.6 | 12000 | 3194.4637 |  | 2
115 | 115 | 67 | 5.6915 | 425000 | 701320 | 40.5 | 12000 | 3194.4637 |  | 2
115 | 115 | 62 | 0.42275 | 386000 | 755320 | 41.8 | 12000 | 2975.6648 |  | 2
115 | 115 | 57 | -4.3353 | 372000 | 676920 | 41.8 | 12000 | 2975.6648 |  | 2
115 | 115 | 75 | 15.3648 | 502000 | 644810 | 41.3 | 14000 | 4732.3073 |  | 2
115 | 115 | 72 | 11.5424 | 476000 | 707370 | 41 | 14000 | 4478.0838 |  | 2
115 | 115 | 67 | 5.6915 | 433000 | 791540 | 40.5 | 14000 | 4478.0838 |  | 2
115 | 115 | 62 | 0.42275 | 397000 | 809200 | 41.7 | 14000 | 4223.8603 |  | 2
115 | 115 | 57 | -4.3353 | 390000 | 713400 | 40.9 | 14000 | 4223.8603 |  | 2
75 | 75 | 75 | 100 | 577000 | 183760 | 27 | 16000 | 6397.2626 |  | 2
75 | 75 | 72 | 86.8609 | 548000 | 225360 | 26.4 | 16000 | 6397.2626 |  | 2
75 | 75 | 67 | 66.7494 | 503000 | 299600 | 25.4 | 16000 | 6397.2626 |  | 2
75 | 75 | 62 | 48.6386 | 463000 | 367360 | 24.7 | 16000 | 6105.5307 |  | 2
75 | 75 | 57 | 32.2833 | 453000 | 399960 | 24.5 | 16000 | 6105.5307 |  | 2
75 | 75 | 75 | 100 | 585000 | 183490 | 27.2 | 18000 | 8453.9721 |  | 2
75 | 75 | 72 | 86.8609 | 556000 | 231510 | 26.5 | 18000 | 8453.9721 |  | 2
75 | 75 | 67 | 66.7494 | 511000 | 313530 | 25.6 | 18000 | 8453.9721 |  | 2
75 | 75 | 62 | 48.6386 | 474000 | 382490 | 24.9 | 18000 | 8124.7318 |  | 2
75 | 75 | 57 | 32.2833 | 466000 | 411280 | 24.7 | 18000 | 8124.7318 |  | 2
75 | 75 | 75 | 100 | 593000 | 184100 | 27.3 | 20000 | 10948.2793 |  | 2
75 | 75 | 72 | 86.8609 | 563000 | 237000 | 26.7 | 20000 | 10948.2793 |  | 2
75 | 75 | 67 | 66.7494 | 517000 | 325800 | 25.7 | 20000 | 10948.2793 |  | 2
75 | 75 | 62 | 48.6386 | 481000 | 395500 | 25 | 20000 | 10573.1955 |  | 2
75 | 75 | 57 | 32.2833 | 479000 | 423700 | 25 | 20000 | 10573.1955 |  | 2
85 | 85 | 75 | 63.5688 | 563000 | 312120 | 29.5 | 16000 | 6397.2626 |  | 2
85 | 85 | 72 | 54.0993 | 536000 | 360760 | 29 | 16000 | 6397.2626 |  | 2
85 | 85 | 67 | 39.6049 | 493000 | 440400 | 28.1 | 16000 | 6105.5307 |  | 2
85 | 85 | 62 | 26.5524 | 455000 | 502760 | 27.4 | 16000 | 6105.5307 |  | 2
85 | 85 | 57 | 14.765 | 446000 | 498160 | 27.3 | 16000 | 6105.5307 |  | 2
85 | 85 | 75 | 63.5688 | 571000 | 331500 | 29.7 | 18000 | 8453.9721 |  | 2
85 | 85 | 72 | 54.0993 | 544000 | 381490 | 29.1 | 18000 | 8453.9721 |  | 2
85 | 85 | 67 | 39.6049 | 501000 | 468470 | 28.3 | 18000 | 8453.9721 |  | 2
85 | 85 | 62 | 26.5524 | 465000 | 526520 | 27.7 | 18000 | 8124.7318 |  | 2
85 | 85 | 57 | 14.765 | 459000 | 512730 | 27.5 | 18000 | 8124.7318 |  | 2
85 | 85 | 75 | 63.5688 | 579000 | 349000 | 29.9 | 20000 | 10948.2793 |  | 2
85 | 85 | 72 | 54.0993 | 551000 | 402000 | 29.3 | 20000 | 10948.2793 |  | 2
85 | 85 | 67 | 39.6049 | 507000 | 497200 | 28.4 | 20000 | 10948.2793 |  | 2
85 | 85 | 62 | 26.5524 | 472000 | 551500 | 27.7 | 20000 | 10573.1955 |  | 2
85 | 85 | 57 | 14.765 | 471000 | 526300 | 27.7 | 20000 | 10573.1955 |  | 2
95 | 95 | 75 | 40.2091 | 550000 | 446920 | 32.7 | 16000 | 6397.2626 |  | 2
95 | 95 | 72 | 33.2947 | 524000 | 500840 | 32.2 | 16000 | 6397.2626 |  | 2
95 | 95 | 67 | 22.7111 | 481000 | 582120 | 31.4 | 16000 | 6105.5307 |  | 2
95 | 95 | 62 | 13.1803 | 444000 | 626920 | 31 | 16000 | 6105.5307 |  | 2
95 | 95 | 57 | 4.5734 | 436000 | 589120 | 30.8 | 16000 | 6105.5307 |  | 2
95 | 95 | 75 | 40.2091 | 559000 | 482660 | 32.9 | 18000 | 8453.9721 |  | 2
95 | 95 | 72 | 33.2947 | 532000 | 537600 | 32.4 | 18000 | 8453.9721 |  | 2
95 | 95 | 67 | 22.7111 | 487000 | 637480 | 31.4 | 18000 | 8124.7318 |  | 2
95 | 95 | 62 | 13.1803 | 453000 | 660780 | 31.1 | 18000 | 8124.7318 |  | 2
95 | 95 | 57 | 4.5734 | 449000 | 609380 | 31 | 18000 | 8124.7318 |  | 2
95 | 95 | 75 | 40.2091 | 566000 | 517400 | 33.1 | 20000 | 10948.2793 |  | 2
95 | 95 | 72 | 33.2947 | 538000 | 573700 | 32.5 | 20000 | 10948.2793 |  | 2
95 | 95 | 67 | 22.7111 | 494000 | 668000 | 31.7 | 20000 | 10573.1955 |  | 2
95 | 95 | 62 | 13.1803 | 461000 | 695300 | 31.2 | 20000 | 10573.1955 |  | 2
95 | 95 | 57 | 4.5734 | 461000 | 622700 | 31.2 | 20000 | 10573.1955 |  | 2
105 | 105 | 75 | 25.1345 | 533000 | 583600 | 36.7 | 16000 | 6397.2626 |  | 2
105 | 105 | 72 | 20.0232 | 507000 | 637400 | 36.3 | 16000 | 6397.2626 |  | 2
105 | 105 | 67 | 12.1996 | 462000 | 734000 | 35.3 | 16000 | 6105.5307 |  | 2
105 | 105 | 62 | 5.1542 | 427000 | 757200 | 35.4 | 16000 | 6105.5307 |  | 2
105 | 105 | 57 | -1.2082 | 422000 | 672800 | 35 | 16000 | 6105.5307 |  | 2
105 | 105 | 75 | 25.1345 | 541000 | 636050 | 37 | 18000 | 8453.9721 |  | 2
105 | 105 | 72 | 20.0232 | 514000 | 690000 | 36.5 | 18000 | 8453.9721 |  | 2
105 | 105 | 67 | 12.1996 | 470000 | 790850 | 35.6 | 18000 | 8124.7318 |  | 2
105 | 105 | 62 | 5.1542 | 437000 | 792350 | 35.2 | 18000 | 8124.7318 |  | 2
105 | 105 | 57 | -1.2082 | 435000 | 692400 | 35.3 | 18000 | 8124.7318 |  | 2
105 | 105 | 75 | 25.1345 | 547000 | 688500 | 37.2 | 20000 | 10948.2793 |  | 2
105 | 105 | 72 | 20.0232 | 520000 | 741500 | 36.6 | 20000 | 10948.2793 |  | 2
105 | 105 | 67 | 12.1996 | 476000 | 836000 | 35.9 | 20000 | 10573.1955 |  | 2
105 | 105 | 62 | 5.1542 | 447000 | 825500 | 35.5 | 20000 | 10573.1955 |  | 2
105 | 105 | 57 | -1.2082 | 446000 | 710000 | 35.5 | 20000 | 10573.1955 |  | 2
115 | 115 | 75 | 15.3648 | 511000 | 721800 | 41.8 | 16000 | 6397.2626 |  | 2
115 | 115 | 72 | 11.5424 | 484000 | 771960 | 41.4 | 16000 | 6105.5307 |  | 2
115 | 115 | 67 | 5.6915 | 441000 | 867440 | 40.7 | 16000 | 6105.5307 |  | 2
115 | 115 | 62 | 0.42275 | 407000 | 875320 | 41.6 | 16000 | 6105.5307 |  | 2
115 | 115 | 57 | -4.3353 | 405000 | 737640 | 41.4 | 16000 | 6105.5307 |  | 2
115 | 115 | 75 | 15.3648 | 517000 | 792400 | 42.1 | 18000 | 8453.9721 |  | 2
115 | 115 | 72 | 11.5424 | 491000 | 840400 | 41.6 | 18000 | 8124.7318 |  | 2
115 | 115 | 67 | 5.6915 | 447000 | 946190 | 41 | 18000 | 8124.7318 |  | 2
115 | 115 | 62 | 0.42275 | 418000 | 908030 | 41.2 | 18000 | 8124.7318 |  | 2
115 | 115 | 57 | -4.3353 | 417000 | 763500 | 41.3 | 18000 | 8124.7318 |  | 2
115 | 115 | 75 | 15.3648 | 523000 | 845600 | 42.7 | 20000 | 10948.2793 |  | 2
115 | 115 | 72 | 11.5424 | 496000 | 907300 | 41.8 | 20000 | 10573.1955 |  | 2
115 | 115 | 67 | 5.6915 | 452000 | 1023400 | 41 | 20000 | 10573.1955 |  | 2
115 | 115 | 62 | 0.42275 | 428000 | 936200 | 41.3 | 20000 | 10573.1955 |  | 2
115 | 115 | 57 | -4.3353 | 428000 | 782200 | 41.3 | 20000 | 10573.1955 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 4
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Net
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 75 | 75 | 100 | 633000 | 225500 | 33.8 | 10000 | 2477.6369 |  | 1
75 | 75 | 72 | 86.8609 | 606000 | 246500 | 33.3 | 10000 | 2477.6369 |  | 1
75 | 75 | 67 | 66.7494 | 558000 | 290360 | 32.5 | 10000 | 2477.6369 |  | 1
75 | 75 | 62 | 48.6386 | 512000 | 344300 | 32.1 | 10000 | 2477.6369 |  | 1
75 | 75 | 57 | 32.2833 | 466000 | 389650 | 31.9 | 10000 | 2281.7598 |  | 1
75 | 75 | 75 | 100 | 665000 | 229875 | 34.3 | 12500 | 3852.9441 |  | 1
75 | 75 | 72 | 86.8609 | 635000 | 259875 | 33.8 | 12500 | 3852.9441 |  | 1
75 | 75 | 67 | 66.7494 | 587000 | 316562.5 | 33 | 12500 | 3852.9441 |  | 1
75 | 75 | 62 | 48.6386 | 541000 | 375812.5 | 32.5 | 12500 | 3852.9441 |  | 1
75 | 75 | 57 | 32.2833 | 494000 | 426187.5 | 32.2 | 12500 | 3623.7263 |  | 1
75 | 75 | 75 | 100 | 690000 | 225250 | 34.7 | 15000 | 5749.2011 |  | 1
75 | 75 | 72 | 86.8609 | 656000 | 251825 | 34.2 | 15000 | 5749.2011 |  | 1
75 | 75 | 67 | 66.7494 | 607000 | 335075 | 33.3 | 15000 | 5749.2011 |  | 1
75 | 75 | 62 | 48.6386 | 561000 | 404600 | 32.8 | 15000 | 5749.2011 |  | 1
75 | 75 | 57 | 32.2833 | 520000 | 459200 | 32.4 | 15000 | 5749.2011 |  | 1
75 | 75 | 75 | 100 | 707000 | 227625 | 35 | 17500 | 8233.0894 |  | 1
75 | 75 | 72 | 86.8609 | 672000 | 274325 | 34.4 | 17500 | 8233.0894 |  | 1
75 | 75 | 67 | 66.7494 | 622000 | 350550 | 33.6 | 17500 | 8233.0894 |  | 1
75 | 75 | 62 | 48.6386 | 576000 | 430662.5 | 33 | 17500 | 8233.0894 |  | 1
75 | 75 | 57 | 32.2833 | 541000 | 477212.5 | 32.6 | 17500 | 8233.0894 |  | 1
85 | 85 | 75 | 63.5688 | 614000 | 285500 | 37.4 | 10000 | 2477.6369 |  | 1
85 | 85 | 72 | 54.0993 | 592000 | 307500 | 37 | 10000 | 2477.6369 |  | 1
85 | 85 | 67 | 39.6049 | 543000 | 371300 | 36.4 | 10000 | 2477.6369 |  | 1
85 | 85 | 62 | 26.5524 | 495000 | 426250 | 36.2 | 10000 | 2281.7598 |  | 1
85 | 85 | 57 | 14.765 | 450000 | 473350 | 36 | 10000 | 2281.7598 |  | 1
85 | 85 | 75 | 63.5688 | 646000 | 300125 | 38 | 12500 | 3852.9441 |  | 1
85 | 85 | 72 | 54.0993 | 618000 | 340125 | 37.5 | 12500 | 3852.9441 |  | 1
85 | 85 | 67 | 39.6049 | 571000 | 416125 | 36.8 | 12500 | 3852.9441 |  | 1
85 | 85 | 62 | 26.5524 | 523000 | 478875 | 36.5 | 12500 | 3852.9441 |  | 1
85 | 85 | 57 | 14.765 | 477000 | 512750 | 36 | 12500 | 3623.7263 |  | 1
85 | 85 | 75 | 63.5688 | 667000 | 319750 | 38.4 | 15000 | 5749.2011 |  | 1
85 | 85 | 72 | 54.0993 | 637000 | 371500 | 37.8 | 15000 | 5749.2011 |  | 1
85 | 85 | 67 | 39.6049 | 590000 | 454750 | 37.1 | 15000 | 5749.2011 |  | 1
85 | 85 | 62 | 26.5524 | 542000 | 526400 | 36.7 | 15000 | 5749.2011 |  | 1
85 | 85 | 57 | 14.765 | 501000 | 557975 | 36.5 | 15000 | 5749.2011 |  | 1
85 | 85 | 75 | 63.5688 | 681000 | 358300 | 38.7 | 17500 | 8233.0894 |  | 1
85 | 85 | 72 | 54.0993 | 650000 | 401600 | 38.1 | 17500 | 8233.0894 |  | 1
85 | 85 | 67 | 39.6049 | 605000 | 490412.5 | 37.4 | 17500 | 8233.0894 |  | 1
85 | 85 | 62 | 26.5524 | 557000 | 572337.5 | 36.9 | 17500 | 8233.0894 |  | 1
85 | 85 | 57 | 14.765 | 526000 | 587862.5 | 36.7 | 17500 | 8233.0894 |  | 1
95 | 95 | 75 | 40.2091 | 598000 | 410000 | 41.8 | 10000 | 2477.6369 |  | 1
95 | 95 | 72 | 33.2947 | 573000 | 433000 | 41.4 | 10000 | 2477.6369 |  | 1
95 | 95 | 67 | 22.7111 | 525000 | 450050 | 41.2 | 10000 | 2477.6369 |  | 1
95 | 95 | 62 | 13.1803 | 476000 | 509600 | 41.1 | 10000 | 2281.7598 |  | 1
95 | 95 | 57 | 4.5734 | 428000 | 551600 | 41.2 | 10000 | 2281.7598 |  | 1
95 | 95 | 75 | 40.2091 | 628000 | 457250 | 42.4 | 12500 | 3852.9441 |  | 1
95 | 95 | 72 | 33.2947 | 600000 | 468375 | 42 | 12500 | 3852.9441 |  | 1
95 | 95 | 67 | 22.7111 | 551000 | 517937.5 | 41.5 | 12500 | 3852.9441 |  | 1
95 | 95 | 62 | 13.1803 | 502000 | 582125 | 41.4 | 12500 | 3852.9441 |  | 1
95 | 95 | 57 | 4.5734 | 458000 | 614750 | 41.3 | 12500 | 3623.7263 |  | 1
95 | 95 | 75 | 40.2091 | 646000 | 509500 | 42.7 | 15000 | 5749.2011 |  | 1
95 | 95 | 72 | 33.2947 | 618000 | 485725 | 42.3 | 15000 | 5749.2011 |  | 1
95 | 95 | 67 | 22.7111 | 570000 | 578525 | 41.8 | 15000 | 5749.2011 |  | 1
95 | 95 | 62 | 13.1803 | 520000 | 652475 | 41.6 | 15000 | 5749.2011 |  | 1
95 | 95 | 57 | 4.5734 | 484000 | 654775 | 41.4 | 15000 | 5478.3073 |  | 1
95 | 95 | 75 | 40.2091 | 658000 | 514662.5 | 43 | 17500 | 8233.0894 |  | 1
95 | 95 | 72 | 33.2947 | 632000 | 537787.5 | 42.6 | 17500 | 8233.0894 |  | 1
95 | 95 | 67 | 22.7111 | 583000 | 630337.5 | 42.1 | 17500 | 8233.0894 |  | 1
95 | 95 | 62 | 13.1803 | 534000 | 715112.5 | 41.8 | 17500 | 8233.0894 |  | 1
95 | 95 | 57 | 4.5734 | 508000 | 687025 | 41.7 | 17500 | 8233.0894 |  | 1
105 | 105 | 75 | 25.1345 | 578000 | 512000 | 47.1 | 10000 | 2477.6369 |  | 1
105 | 105 | 72 | 20.0232 | 552000 | 536000 | 46.9 | 10000 | 2477.6369 |  | 1
105 | 105 | 67 | 12.1996 | 502000 | 534000 | 46.8 | 10000 | 2477.6369 |  | 1
105 | 105 | 62 | 5.1542 | 454000 | 591000 | 47.2 | 10000 | 2281.7598 |  | 1
105 | 105 | 57 | -1.2082 | 408000 | 626250 | 48.7 | 10000 | 2281.7598 |  | 1
105 | 105 | 75 | 25.1345 | 606000 | 586750 | 47.6 | 12500 | 3852.9441 |  | 1
105 | 105 | 72 | 20.0232 | 577000 | 585500 | 47.4 | 12500 | 3852.9441 |  | 1
105 | 105 | 67 | 12.1996 | 527000 | 620000 | 47.2 | 12500 | 3852.9441 |  | 1
105 | 105 | 62 | 5.1542 | 478000 | 687312.5 | 47.3 | 12500 | 3623.7263 |  | 1
105 | 105 | 57 | -1.2082 | 436000 | 693812.5 | 48.2 | 12500 | 3623.7263 |  | 1
105 | 105 | 75 | 25.1345 | 623000 | 668500 | 47.9 | 15000 | 5749.2011 |  | 1
105 | 105 | 72 | 20.0232 | 594000 | 603125 | 47.6 | 15000 | 5749.2011 |  | 1
105 | 105 | 67 | 12.1996 | 544000 | 697875 | 47.5 | 15000 | 5749.2011 |  | 1
105 | 105 | 62 | 5.1542 | 495000 | 775125 | 47.3 | 15000 | 5478.3073 |  | 1
105 | 105 | 57 | -1.2082 | 465000 | 741375 | 47.8 | 15000 | 5478.3073 |  | 1
105 | 105 | 75 | 25.1345 | 635000 | 681875 | 48.1 | 17500 | 8233.0894 |  | 1
105 | 105 | 72 | 20.0232 | 608000 | 675125 | 47.9 | 17500 | 8233.0894 |  | 1
105 | 105 | 67 | 12.1996 | 557000 | 773375 | 47.7 | 17500 | 8233.0894 |  | 1
105 | 105 | 62 | 5.1542 | 508000 | 849375 | 47.5 | 17500 | 8233.0894 |  | 1
105 | 105 | 57 | -1.2082 | 488000 | 776750 | 47.6 | 17500 | 7912.1844 |  | 1
115 | 115 | 75 | 15.3648 | 553000 | 612000 | 53.2 | 10000 | 2477.6369 |  | 1
115 | 115 | 72 | 11.5424 | 526000 | 638000 | 53.3 | 10000 | 2477.6369 |  | 1
115 | 115 | 67 | 5.6915 | 477000 | 618700 | 53.8 | 10000 | 2281.7598 |  | 1
115 | 115 | 62 | 0.42275 | 429000 | 676250 | 55.5 | 10000 | 2281.7598 |  | 1
115 | 115 | 57 | -4.3353 | 382000 | 687000 | 58 | 10000 | 2090.0503 |  | 1
115 | 115 | 75 | 15.3648 | 580000 | 715250 | 53.7 | 12500 | 3852.9441 |  | 1
115 | 115 | 72 | 11.5424 | 549000 | 624312.5 | 53.6 | 12500 | 3852.9441 |  | 1
115 | 115 | 67 | 5.6915 | 500000 | 723812.5 | 53.9 | 12500 | 3623.7263 |  | 1
115 | 115 | 62 | 0.42275 | 451000 | 789437.5 | 55.3 | 12500 | 3623.7263 |  | 1
115 | 115 | 57 | -4.3353 | 416000 | 762500 | 56.9 | 12500 | 3623.7263 |  | 1
115 | 115 | 75 | 15.3648 | 595000 | 733100 | 53.9 | 15000 | 5749.2011 |  | 1
115 | 115 | 72 | 11.5424 | 566000 | 725125 | 53.9 | 15000 | 5749.2011 |  | 1
115 | 115 | 67 | 5.6915 | 516000 | 823000 | 54.1 | 15000 | 5749.2011 |  | 1
115 | 115 | 62 | 0.42275 | 467000 | 895775 | 55.3 | 15000 | 5478.3073 |  | 1
115 | 115 | 57 | -4.3353 | 443000 | 812600 | 56 | 15000 | 5478.3073 |  | 1
115 | 115 | 75 | 15.3648 | 607000 | 710412.5 | 54.1 | 17500 | 8233.0894 |  | 1
115 | 115 | 72 | 11.5424 | 578000 | 821050 | 54.1 | 17500 | 8233.0894 |  | 1
115 | 115 | 67 | 5.6915 | 528000 | 912525 | 54.1 | 17500 | 8233.0894 |  | 1
115 | 115 | 62 | 0.42275 | 479000 | 973787.5 | 55 | 17500 | 7912.1844 |  | 1
115 | 115 | 57 | -4.3353 | 466000 | 850037.5 | 55.5 | 17500 | 7912.1844 |  | 1
75 | 75 | 75 | 100 | 719000 | 210500 | 35.2 | 20000 | 11383.7933 |  | 1
75 | 75 | 72 | 86.8609 | 685000 | 279700 | 34.7 | 20000 | 11383.7933 |  | 1
75 | 75 | 67 | 66.7494 | 633000 | 366300 | 33.8 | 20000 | 11383.7933 |  | 1
75 | 75 | 62 | 48.6386 | 587000 | 455100 | 33.2 | 20000 | 11383.7933 |  | 1
75 | 75 | 57 | 32.2833 | 562000 | 496800 | 32.9 | 20000 | 11383.7933 |  | 1
85 | 85 | 75 | 63.5688 | 693000 | 385700 | 38.9 | 20000 | 11383.7933 |  | 1
85 | 85 | 72 | 54.0993 | 662000 | 428400 | 38.3 | 20000 | 11383.7933 |  | 1
85 | 85 | 67 | 39.6049 | 616000 | 523800 | 37.6 | 20000 | 11383.7933 |  | 1
85 | 85 | 62 | 26.5524 | 568000 | 611800 | 37.1 | 20000 | 11383.7933 |  | 1
85 | 85 | 57 | 14.765 | 547000 | 611100 | 36.9 | 20000 | 11383.7933 |  | 1
95 | 95 | 75 | 40.2091 | 668000 | 500500 | 43.2 | 20000 | 11383.7933 |  | 1
95 | 95 | 72 | 33.2947 | 643000 | 583900 | 42.8 | 20000 | 11383.7933 |  | 1
95 | 95 | 67 | 22.7111 | 594000 | 683800 | 42.2 | 20000 | 11383.7933 |  | 1
95 | 95 | 62 | 13.1803 | 543000 | 765800 | 41.9 | 20000 | 11383.7933 |  | 1
95 | 95 | 57 | 4.5734 | 528000 | 716100 | 41.8 | 20000 | 11383.7933 |  | 1
105 | 105 | 75 | 25.1345 | 645000 | 653000 | 48.3 | 20000 | 11383.7933 |  | 1
105 | 105 | 72 | 20.0232 | 618000 | 742000 | 48.1 | 20000 | 11383.7933 |  | 1
105 | 105 | 67 | 12.1996 | 568000 | 841000 | 47.8 | 20000 | 11383.7933 |  | 1
105 | 105 | 62 | 5.1542 | 519000 | 905000 | 47.5 | 20000 | 11383.7933 |  | 1
105 | 105 | 57 | -1.2082 | 507000 | 809500 | 47.5 | 20000 | 11383.7933 |  | 1
115 | 115 | 75 | 15.3648 | 615000 | 809000 | 54.2 | 20000 | 11383.7933 |  | 1
115 | 115 | 72 | 11.5424 | 587000 | 902500 | 54.3 | 20000 | 11383.7933 |  | 1
115 | 115 | 67 | 5.6915 | 537000 | 1004900 | 54.1 | 20000 | 11383.7933 |  | 1
115 | 115 | 62 | 0.42275 | 491000 | 1034400 | 55 | 20000 | 11012.8771 |  | 1
115 | 115 | 57 | -4.3353 | 484000 | 884400 | 55.1 | 20000 | 11012.8771 |  | 1
75 | 75 | 75 | 100 | 638000 | 229500 | 33.7 | 10000 | 2477.6369 |  | 2
75 | 75 | 72 | 86.8609 | 609000 | 254500 | 33.3 | 10000 | 2477.6369 |  | 2
75 | 75 | 67 | 66.7494 | 560000 | 299400 | 32.4 | 10000 | 2477.6369 |  | 2
75 | 75 | 62 | 48.6386 | 517000 | 350100 | 31.7 | 10000 | 2477.6369 |  | 2
75 | 75 | 57 | 32.2833 | 476000 | 398550 | 31.3 | 10000 | 2281.7598 |  | 2
75 | 75 | 75 | 100 | 673000 | 230875 | 34.3 | 12500 | 3852.9441 |  | 2
75 | 75 | 72 | 86.8609 | 643000 | 252687.5 | 33.8 | 12500 | 3852.9441 |  | 2
75 | 75 | 67 | 66.7494 | 590000 | 320812.5 | 32.9 | 12500 | 3852.9441 |  | 2
75 | 75 | 62 | 48.6386 | 546000 | 383062.5 | 32.2 | 12500 | 3852.9441 |  | 2
75 | 75 | 57 | 32.2833 | 503000 | 434125 | 31.6 | 12500 | 3852.9441 |  | 2
75 | 75 | 75 | 100 | 698000 | 232250 | 34.8 | 15000 | 5749.2011 |  | 2
75 | 75 | 72 | 86.8609 | 665000 | 270725 | 34.2 | 15000 | 5749.2011 |  | 2
75 | 75 | 67 | 66.7494 | 611000 | 339775 | 33.3 | 15000 | 5749.2011 |  | 2
75 | 75 | 62 | 48.6386 | 566000 | 413125 | 32.5 | 15000 | 5749.2011 |  | 2
75 | 75 | 57 | 32.2833 | 527000 | 464725 | 31.9 | 15000 | 5749.2011 |  | 2
75 | 75 | 75 | 100 | 715000 | 217850 | 35.1 | 17500 | 8233.0894 |  | 2
75 | 75 | 72 | 86.8609 | 677000 | 276625 | 34.5 | 17500 | 8233.0894 |  | 2
75 | 75 | 67 | 66.7494 | 627000 | 357700 | 33.5 | 17500 | 8233.0894 |  | 2
75 | 75 | 62 | 48.6386 | 581000 | 439775 | 32.8 | 17500 | 8233.0894 |  | 2
75 | 75 | 57 | 32.2833 | 552000 | 487250 | 32.3 | 17500 | 8233.0894 |  | 2
85 | 85 | 75 | 63.5688 | 622000 | 290500 | 37.4 | 10000 | 2477.6369 |  | 2
85 | 85 | 72 | 54.0993 | 595000 | 314500 | 36.9 | 10000 | 2477.6369 |  | 2
85 | 85 | 67 | 39.6049 | 549000 | 382150 | 36.1 | 10000 | 2477.6369 |  | 2
85 | 85 | 62 | 26.5524 | 505000 | 437900 | 35.5 | 10000 | 2477.6369 |  | 2
85 | 85 | 57 | 14.765 | 461000 | 484450 | 35.4 | 10000 | 2281.7598 |  | 2
85 | 85 | 75 | 63.5688 | 654000 | 309125 | 38 | 12500 | 3852.9441 |  | 2
85 | 85 | 72 | 54.0993 | 624000 | 365000 | 37.4 | 12500 | 3852.9441 |  | 2
85 | 85 | 67 | 39.6049 | 578000 | 426875 | 36.6 | 12500 | 3852.9441 |  | 2
85 | 85 | 62 | 26.5524 | 533000 | 492937.5 | 36 | 12500 | 3852.9441 |  | 2
85 | 85 | 57 | 14.765 | 489000 | 536187.5 | 35.6 | 12500 | 3623.7263 |  | 2
85 | 85 | 75 | 63.5688 | 678000 | 328750 | 38.4 | 15000 | 5749.2011 |  | 2
85 | 85 | 72 | 54.0993 | 646000 | 388925 | 37.8 | 15000 | 5749.2011 |  | 2
85 | 85 | 67 | 39.6049 | 598000 | 466225 | 37 | 15000 | 5749.2011 |  | 2
85 | 85 | 62 | 26.5524 | 552000 | 543700 | 36.3 | 15000 | 5749.2011 |  | 2
85 | 85 | 57 | 14.765 | 515000 | 575450 | 35.9 | 15000 | 5749.2011 |  | 2
85 | 85 | 75 | 63.5688 | 695000 | 374075 | 38.8 | 17500 | 8233.0894 |  | 2
85 | 85 | 72 | 54.0993 | 661000 | 419375 | 38.1 | 17500 | 8233.0894 |  | 2
85 | 85 | 67 | 39.6049 | 613000 | 504300 | 37.2 | 17500 | 8233.0894 |  | 2
85 | 85 | 62 | 26.5524 | 567000 | 588262.5 | 36.6 | 17500 | 8233.0894 |  | 2
85 | 85 | 57 | 14.765 | 540000 | 602825 | 36.2 | 17500 | 8233.0894 |  | 2
95 | 95 | 75 | 40.2091 | 606000 | 413000 | 41.6 | 10000 | 2477.6369 |  | 2
95 | 95 | 72 | 33.2947 | 582000 | 442000 | 41.3 | 10000 | 2477.6369 |  | 2
95 | 95 | 67 | 22.7111 | 535000 | 467300 | 40.7 | 10000 | 2477.6369 |  | 2
95 | 95 | 62 | 13.1803 | 488000 | 526550 | 40.5 | 10000 | 2281.7598 |  | 2
95 | 95 | 57 | 4.5734 | 440000 | 567550 | 40.4 | 10000 | 2281.7598 |  | 2
95 | 95 | 75 | 40.2091 | 638000 | 463250 | 42.3 | 12500 | 3852.9441 |  | 2
95 | 95 | 72 | 33.2947 | 610000 | 483562.5 | 41.9 | 12500 | 3852.9441 |  | 2
95 | 95 | 67 | 22.7111 | 562000 | 535187.5 | 41.3 | 12500 | 3852.9441 |  | 2
95 | 95 | 62 | 13.1803 | 515000 | 601312.5 | 40.9 | 12500 | 3852.9441 |  | 2
95 | 95 | 57 | 4.5734 | 472000 | 625875 | 40.5 | 12500 | 3623.7263 |  | 2
95 | 95 | 75 | 40.2091 | 658000 | 520500 | 42.7 | 15000 | 5749.2011 |  | 2
95 | 95 | 72 | 33.2947 | 630000 | 510575 | 42.3 | 15000 | 5749.2011 |  | 2
95 | 95 | 67 | 22.7111 | 582000 | 596950 | 41.6 | 15000 | 5749.2011 |  | 2
95 | 95 | 62 | 13.1803 | 534000 | 673900 | 41.3 | 15000 | 5749.2011 |  | 2
95 | 95 | 57 | 4.5734 | 500000 | 678200 | 41 | 15000 | 5478.3073 |  | 2
95 | 95 | 75 | 40.2091 | 677000 | 486237.5 | 43.2 | 17500 | 8233.0894 |  | 2
95 | 95 | 72 | 33.2947 | 646000 | 567112.5 | 42.7 | 17500 | 8233.0894 |  | 2
95 | 95 | 67 | 22.7111 | 596000 | 654887.5 | 41.9 | 17500 | 8233.0894 |  | 2
95 | 95 | 62 | 13.1803 | 548000 | 735887.5 | 41.6 | 17500 | 8233.0894 |  | 2
95 | 95 | 57 | 4.5734 | 525000 | 709800 | 41.2 | 17500 | 8233.0894 |  | 2
105 | 105 | 75 | 25.1345 | 591000 | 517000 | 46.9 | 10000 | 2477.6369 |  | 2
105 | 105 | 72 | 20.0232 | 564000 | 546000 | 46.8 | 10000 | 2477.6369 |  | 2
105 | 105 | 67 | 12.1996 | 515000 | 554000 | 46.6 | 10000 | 2477.6369 |  | 2
105 | 105 | 62 | 5.1542 | 467000 | 611250 | 46.6 | 10000 | 2281.7598 |  | 2
105 | 105 | 57 | -1.2082 | 423000 | 635250 | 47.6 | 10000 | 2281.7598 |  | 2
105 | 105 | 75 | 25.1345 | 621000 | 596750 | 47.7 | 12500 | 3852.9441 |  | 2
105 | 105 | 72 | 20.0232 | 591000 | 558687.5 | 47.5 | 12500 | 3852.9441 |  | 2
105 | 105 | 67 | 12.1996 | 541000 | 640312.5 | 47.1 | 12500 | 3852.9441 |  | 2
105 | 105 | 62 | 5.1542 | 492000 | 711625 | 46.9 | 12500 | 3623.7263 |  | 2
105 | 105 | 57 | -1.2082 | 452000 | 715687.5 | 47.4 | 12500 | 3623.7263 |  | 2
105 | 105 | 75 | 25.1345 | 641000 | 613500 | 48.3 | 15000 | 5749.2011 |  | 2
105 | 105 | 72 | 20.0232 | 611000 | 638875 | 48 | 15000 | 5749.2011 |  | 2
105 | 105 | 67 | 12.1996 | 560000 | 722250 | 47.5 | 15000 | 5749.2011 |  | 2
105 | 105 | 62 | 5.1542 | 510000 | 801500 | 47.2 | 15000 | 5749.2011 |  | 2
105 | 105 | 57 | -1.2082 | 481000 | 765625 | 47.3 | 15000 | 5478.3073 |  | 2
105 | 105 | 75 | 25.1345 | 656000 | 626500 | 48.7 | 17500 | 8233.0894 |  | 2
105 | 105 | 72 | 20.0232 | 625000 | 711187.5 | 48.3 | 17500 | 8233.0894 |  | 2
105 | 105 | 67 | 12.1996 | 573000 | 801812.5 | 47.7 | 17500 | 8233.0894 |  | 2
105 | 105 | 62 | 5.1542 | 523000 | 877812.5 | 47.5 | 17500 | 8233.0894 |  | 2
105 | 105 | 57 | -1.2082 | 505000 | 803375 | 47.3 | 17500 | 8233.0894 |  | 2
115 | 115 | 75 | 15.3648 | 569000 | 619000 | 53.4 | 10000 | 2477.6369 |  | 2
115 | 115 | 72 | 11.5424 | 540000 | 600800 | 53.5 | 10000 | 2477.6369 |  | 2
115 | 115 | 67 | 5.6915 | 490000 | 639250 | 54.2 | 10000 | 2281.7598 |  | 2
115 | 115 | 62 | 0.42275 | 443000 | 698800 | 55.9 | 10000 | 2281.7598 |  | 2
115 | 115 | 57 | -4.3353 | 400000 | 713550 | 59.3 | 10000 | 2090.0503 |  | 2
115 | 115 | 75 | 15.3648 | 596000 | 725250 | 54.2 | 12500 | 3852.9441 |  | 2
115 | 115 | 72 | 11.5424 | 565000 | 664187.5 | 54.1 | 12500 | 3852.9441 |  | 2
115 | 115 | 67 | 5.6915 | 514000 | 748250 | 54.4 | 12500 | 3852.9441 |  | 2
115 | 115 | 62 | 0.42275 | 466000 | 816875 | 55.9 | 12500 | 3623.7263 |  | 2
115 | 115 | 57 | -4.3353 | 431000 | 787125 | 57.2 | 12500 | 3623.7263 |  | 2
115 | 115 | 75 | 15.3648 | 614000 | 761425 | 54.9 | 15000 | 5749.2011 |  | 2
115 | 115 | 72 | 11.5424 | 583000 | 766000 | 54.6 | 15000 | 5749.2011 |  | 2
115 | 115 | 67 | 5.6915 | 531000 | 853325 | 54.7 | 15000 | 5749.2011 |  | 2
115 | 115 | 62 | 0.42275 | 479000 | 927100 | 55.7 | 15000 | 5478.3073 |  | 2
115 | 115 | 57 | -4.3353 | 459000 | 840150 | 56.4 | 15000 | 5478.3073 |  | 2
115 | 115 | 75 | 15.3648 | 627000 | 776312.5 | 55.4 | 17500 | 8233.0894 |  | 2
115 | 115 | 72 | 11.5424 | 595000 | 853262.5 | 55.1 | 17500 | 8233.0894 |  | 2
115 | 115 | 67 | 5.6915 | 542000 | 954475 | 54.6 | 17500 | 8233.0894 |  | 2
115 | 115 | 62 | 0.42275 | 493000 | 1009000 | 55.8 | 17500 | 7912.1844 |  | 2
115 | 115 | 57 | -4.3353 | 483000 | 880512.5 | 56 | 17500 | 7912.1844 |  | 2
75 | 75 | 75 | 100 | 730000 | 235900 | 35.3 | 20000 | 11383.7933 |  | 2
75 | 75 | 72 | 86.8609 | 695000 | 285200 | 34.7 | 20000 | 11383.7933 |  | 2
75 | 75 | 67 | 66.7494 | 639000 | 373900 | 33.8 | 20000 | 11383.7933 |  | 2
75 | 75 | 62 | 48.6386 | 593000 | 462900 | 33 | 20000 | 11383.7933 |  | 2
75 | 75 | 57 | 32.2833 | 572000 | 505700 | 32.6 | 20000 | 11383.7933 |  | 2
85 | 85 | 75 | 63.5688 | 707000 | 383400 | 39 | 20000 | 11383.7933 |  | 2
85 | 85 | 72 | 54.0993 | 675000 | 444900 | 38.4 | 20000 | 11383.7933 |  | 2
85 | 85 | 67 | 39.6049 | 624000 | 540100 | 37.5 | 20000 | 11383.7933 |  | 2
85 | 85 | 62 | 26.5524 | 578000 | 626000 | 36.8 | 20000 | 11383.7933 |  | 2
85 | 85 | 57 | 14.765 | 561000 | 626200 | 36.5 | 20000 | 11383.7933 |  | 2
95 | 95 | 75 | 40.2091 | 690000 | 539900 | 43.5 | 20000 | 11383.7933 |  | 2
95 | 95 | 72 | 33.2947 | 658000 | 610100 | 42.9 | 20000 | 11383.7933 |  | 2
95 | 95 | 67 | 22.7111 | 606000 | 714000 | 42.1 | 20000 | 11383.7933 |  | 2
95 | 95 | 62 | 13.1803 | 558000 | 778100 | 41.5 | 20000 | 11383.7933 |  | 2
95 | 95 | 57 | 4.5734 | 545000 | 736400 | 41.4 | 20000 | 11383.7933 |  | 2
105 | 105 | 75 | 25.1345 | 668000 | 704500 | 49.1 | 20000 | 11383.7933 |  | 2
105 | 105 | 72 | 20.0232 | 635000 | 777000 | 48.6 | 20000 | 11383.7933 |  | 2
105 | 105 | 67 | 12.1996 | 582000 | 880000 | 47.8 | 20000 | 11383.7933 |  | 2
105 | 105 | 62 | 5.1542 | 534000 | 937500 | 47.7 | 20000 | 11383.7933 |  | 2
105 | 105 | 57 | -1.2082 | 525000 | 833000 | 47.4 | 20000 | 11383.7933 |  | 2
115 | 115 | 75 | 15.3648 | 638000 | 868200 | 55.8 | 20000 | 11383.7933 |  | 2
115 | 115 | 72 | 11.5424 | 606000 | 937600 | 55.4 | 20000 | 11383.7933 |  | 2
115 | 115 | 67 | 5.6915 | 553000 | 1044000 | 55.2 | 20000 | 11383.7933 |  | 2
115 | 115 | 62 | 0.42275 | 507000 | 1073500 | 56 | 20000 | 11383.7933 |  | 2
115 | 115 | 57 | -4.3353 | 502000 | 917800 | 55.7 | 20000 | 11383.7933 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 5
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Net
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 75 | 75 | 100 | 685000 | 243050 | 37.2 | 11000 | 2335.9385 |  | 1
75 | 75 | 72 | 86.8609 | 654000 | 273050 | 36.5 | 11000 | 2335.9385 |  | 1
75 | 75 | 67 | 66.7494 | 604000 | 324015 | 35.5 | 11000 | 2335.9385 |  | 1
75 | 75 | 62 | 48.6386 | 558000 | 380595 | 34.8 | 11000 | 2335.9385 |  | 1
75 | 75 | 57 | 32.2833 | 510000 | 432595 | 34.6 | 11000 | 2335.9385 |  | 1
75 | 75 | 75 | 100 | 722000 | 244562.5 | 37.9 | 13750 | 3165.2905 |  | 1
75 | 75 | 72 | 86.8609 | 686000 | 281075 | 37.2 | 13750 | 3165.2905 |  | 1
75 | 75 | 67 | 66.7494 | 636000 | 347512.5 | 36.1 | 13750 | 3165.2905 |  | 1
75 | 75 | 62 | 48.6386 | 588000 | 419000 | 35.3 | 13750 | 3165.2905 |  | 1
75 | 75 | 57 | 32.2833 | 538000 | 463537.5 | 34.6 | 13750 | 3165.2905 |  | 1
75 | 75 | 75 | 100 | 744000 | 250075 | 38.4 | 16500 | 4344.7207 |  | 1
75 | 75 | 72 | 86.8609 | 709000 | 288152.5 | 37.6 | 16500 | 4344.7207 |  | 1
75 | 75 | 67 | 66.7494 | 656000 | 369522.5 | 36.5 | 16500 | 4344.7207 |  | 1
75 | 75 | 62 | 48.6386 | 609000 | 452707.5 | 35.7 | 16500 | 4344.7207 |  | 1
75 | 75 | 57 | 32.2833 | 572000 | 504597.5 | 35.2 | 16500 | 4344.7207 |  | 1
75 | 75 | 75 | 100 | 761000 | 247598.75 | 38.8 | 19250 | 5872.1453 |  | 1
75 | 75 | 72 | 86.8609 | 726000 | 296011.25 | 38 | 19250 | 5872.1453 |  | 1
75 | 75 | 67 | 66.7494 | 672000 | 388835 | 36.9 | 19250 | 5872.1453 |  | 1
75 | 75 | 62 | 48.6386 | 625000 | 482776.25 | 36.1 | 19250 | 5872.1453 |  | 1
75 | 75 | 57 | 32.2833 | 598000 | 527833.75 | 35.6 | 19250 | 5872.1453 |  | 1
85 | 85 | 75 | 63.5688 | 663000 | 308950 | 41 | 11000 | 2335.9385 |  | 1
85 | 85 | 72 | 54.0993 | 636000 | 341950 | 40.5 | 11000 | 2335.9385 |  | 1
85 | 85 | 67 | 39.6049 | 588000 | 418985 | 39.7 | 11000 | 2335.9385 |  | 1
85 | 85 | 62 | 26.5524 | 540000 | 478405 | 39.3 | 11000 | 2335.9385 |  | 1
85 | 85 | 57 | 14.765 | 491000 | 527405 | 39.2 | 11000 | 2073.3799 |  | 1
85 | 85 | 75 | 63.5688 | 697000 | 328437.5 | 41.8 | 13750 | 3165.2905 |  | 1
85 | 85 | 72 | 54.0993 | 665000 | 389193.75 | 41.1 | 13750 | 3165.2905 |  | 1
85 | 85 | 67 | 39.6049 | 618000 | 469487.5 | 40.3 | 13750 | 3165.2905 |  | 1
85 | 85 | 62 | 26.5524 | 570000 | 542000 | 39.8 | 13750 | 3165.2905 |  | 1
85 | 85 | 57 | 14.765 | 519000 | 566706.25 | 39.1 | 13750 | 3165.2905 |  | 1
85 | 85 | 75 | 63.5688 | 717000 | 377292.5 | 42.3 | 16500 | 4344.7207 |  | 1
85 | 85 | 72 | 54.0993 | 687000 | 424847.5 | 41.6 | 16500 | 4344.7207 |  | 1
85 | 85 | 67 | 39.6049 | 638000 | 514477.5 | 40.7 | 16500 | 4344.7207 |  | 1
85 | 85 | 62 | 26.5524 | 589000 | 600292.5 | 40.1 | 16500 | 4344.7207 |  | 1
85 | 85 | 57 | 14.765 | 556000 | 620680 | 39.7 | 16500 | 4344.7207 |  | 1
85 | 85 | 75 | 63.5688 | 732000 | 390577.5 | 42.6 | 19250 | 5872.1453 |  | 1
85 | 85 | 72 | 54.0993 | 702000 | 459047.5 | 41.9 | 19250 | 5872.1453 |  | 1
85 | 85 | 67 | 39.6049 | 653000 | 558165 | 41 | 19250 | 5872.1453 |  | 1
85 | 85 | 62 | 26.5524 | 604000 | 650165 | 40.5 | 19250 | 5872.1453 |  | 1
85 | 85 | 57 | 14.765 | 582000 | 650048.75 | 40 | 19250 | 5872.1453 |  | 1
95 | 95 | 75 | 40.2091 | 646000 | 445500 | 45.7 | 11000 | 2335.9385 |  | 1
95 | 95 | 72 | 33.2947 | 619000 | 479500 | 45.3 | 11000 | 2335.9385 |  | 1
95 | 95 | 67 | 22.7111 | 570000 | 515090 | 44.9 | 11000 | 2335.9385 |  | 1
95 | 95 | 62 | 13.1803 | 520000 | 576535 | 44.7 | 11000 | 2335.9385 |  | 1
95 | 95 | 57 | 4.5734 | 466000 | 610720 | 45.6 | 11000 | 2073.3799 |  | 1
95 | 95 | 75 | 40.2091 | 676000 | 502875 | 46.4 | 13750 | 3165.2905 |  | 1
95 | 95 | 72 | 33.2947 | 647000 | 506768.75 | 45.9 | 13750 | 3165.2905 |  | 1
95 | 95 | 67 | 22.7111 | 598000 | 593381.25 | 45.4 | 13750 | 3165.2905 |  | 1
95 | 95 | 62 | 13.1803 | 547000 | 667918.75 | 45.2 | 13750 | 3165.2905 |  | 1
95 | 95 | 57 | 4.5734 | 504000 | 683231.25 | 45.2 | 13750 | 3165.2905 |  | 1
95 | 95 | 75 | 40.2091 | 694000 | 534302.5 | 46.8 | 16500 | 4344.7207 |  | 1
95 | 95 | 72 | 33.2947 | 667000 | 569245 | 46.4 | 16500 | 4344.7207 |  | 1
95 | 95 | 67 | 22.7111 | 617000 | 664135 | 45.8 | 16500 | 4344.7207 |  | 1
95 | 95 | 62 | 13.1803 | 566000 | 741857.5 | 45.5 | 16500 | 4344.7207 |  | 1
95 | 95 | 57 | 4.5734 | 537000 | 727575 | 45.2 | 16500 | 4344.7207 |  | 1
95 | 95 | 75 | 40.2091 | 708000 | 550571.25 | 47.1 | 19250 | 5872.1453 |  | 1
95 | 95 | 72 | 33.2947 | 681000 | 626452.5 | 46.7 | 19250 | 5872.1453 |  | 1
95 | 95 | 67 | 22.7111 | 631000 | 727805 | 46.1 | 19250 | 5872.1453 |  | 1
95 | 95 | 62 | 13.1803 | 580000 | 815805 | 45.9 | 19250 | 5872.1453 |  | 1
95 | 95 | 57 | 4.5734 | 563000 | 763103.75 | 45.4 | 19250 | 5872.1453 |  | 1
105 | 105 | 75 | 25.1345 | 626000 | 558500 | 51.3 | 11000 | 2335.9385 |  | 1
105 | 105 | 72 | 20.0232 | 597000 | 562250 | 51.2 | 11000 | 2335.9385 |  | 1
105 | 105 | 67 | 12.1996 | 546000 | 612175 | 51.1 | 11000 | 2335.9385 |  | 1
105 | 105 | 62 | 5.1542 | 495000 | 676250 | 52.1 | 11000 | 2073.3799 |  | 1
105 | 105 | 57 | -1.2082 | 443000 | 706175 | 54.4 | 11000 | 2073.3799 |  | 1
105 | 105 | 75 | 25.1345 | 654000 | 647125 | 51.9 | 13750 | 3165.2905 |  | 1
105 | 105 | 72 | 20.0232 | 624000 | 625062.5 | 51.7 | 13750 | 3165.2905 |  | 1
105 | 105 | 67 | 12.1996 | 572000 | 714968.75 | 51.6 | 13750 | 3165.2905 |  | 1
105 | 105 | 62 | 5.1542 | 522000 | 790531.25 | 52 | 13750 | 3165.2905 |  | 1
105 | 105 | 57 | -1.2082 | 485000 | 772375 | 53 | 13750 | 2894.3966 |  | 1
105 | 105 | 75 | 25.1345 | 671000 | 619775 | 52.4 | 16500 | 4344.7207 |  | 1
105 | 105 | 72 | 20.0232 | 642000 | 713612.5 | 52.2 | 16500 | 4344.7207 |  | 1
105 | 105 | 67 | 12.1996 | 590000 | 809225 | 51.9 | 16500 | 4344.7207 |  | 1
105 | 105 | 62 | 5.1542 | 539000 | 887225 | 52.5 | 16500 | 4344.7207 |  | 1
105 | 105 | 57 | -1.2082 | 516000 | 820012.5 | 52.5 | 16500 | 4344.7207 |  | 1
105 | 105 | 75 | 25.1345 | 686000 | 711912.5 | 52.8 | 19250 | 5872.1453 |  | 1
105 | 105 | 72 | 20.0232 | 655000 | 796381.25 | 52.5 | 19250 | 5872.1453 |  | 1
105 | 105 | 67 | 12.1996 | 604000 | 900968.75 | 52.2 | 19250 | 5872.1453 |  | 1
105 | 105 | 62 | 5.1542 | 552000 | 972381.25 | 52.5 | 19250 | 5872.1453 |  | 1
105 | 105 | 57 | -1.2082 | 542000 | 864918.75 | 51.9 | 19250 | 5872.1453 |  | 1
115 | 115 | 75 | 15.3648 | 602000 | 666500 | 58.1 | 11000 | 2335.9385 |  | 1
115 | 115 | 72 | 11.5424 | 570000 | 610330 | 58.2 | 11000 | 2335.9385 |  | 1
115 | 115 | 67 | 5.6915 | 519000 | 709680 | 59.6 | 11000 | 2335.9385 |  | 1
115 | 115 | 62 | 0.42275 | 468000 | 771150 | 62.5 | 11000 | 2073.3799 |  | 1
115 | 115 | 75 | 15.3648 | 626000 | 726850 | 58.5 | 13750 | 3165.2905 |  | 1
115 | 115 | 72 | 11.5424 | 595000 | 749675 | 58.6 | 13750 | 3165.2905 |  | 1
115 | 115 | 67 | 5.6915 | 544000 | 839850 | 59.7 | 13750 | 3165.2905 |  | 1
115 | 115 | 62 | 0.42275 | 492000 | 911143.75 | 62.3 | 13750 | 2894.3966 |  | 1
115 | 115 | 75 | 15.3648 | 643000 | 764142.5 | 58.9 | 16500 | 4344.7207 |  | 1
115 | 115 | 72 | 11.5424 | 612000 | 859610 | 59 | 16500 | 4344.7207 |  | 1
115 | 115 | 67 | 5.6915 | 561000 | 953315 | 59.8 | 16500 | 4344.7207 |  | 1
115 | 115 | 62 | 0.42275 | 508000 | 1027315 | 62.2 | 16500 | 4344.7207 |  | 1
115 | 115 | 57 | -4.3353 | 494000 | 900560 | 61 | 16500 | 4048.8212 |  | 1
115 | 115 | 75 | 15.3648 | 657000 | 881900 | 59.5 | 19250 | 5872.1453 |  | 1
115 | 115 | 72 | 11.5424 | 625000 | 969545 | 59.3 | 19250 | 5872.1453 |  | 1
115 | 115 | 67 | 5.6915 | 573000 | 1068956.25 | 59.9 | 19250 | 5872.1453 |  | 1
115 | 115 | 62 | 0.42275 | 521000 | 1113311.25 | 61.3 | 19250 | 5872.1453 |  | 1
115 | 115 | 57 | -4.3353 | 517000 | 946852.5 | 61.1 | 19250 | 5872.1453 |  | 1
75 | 75 | 75 | 100 | 773000 | 245130 | 39.1 | 22000 | 7782.9888 |  | 1
75 | 75 | 72 | 86.8609 | 738000 | 303870 | 38.3 | 22000 | 7782.9888 |  | 1
75 | 75 | 67 | 66.7494 | 684000 | 408450 | 37.1 | 22000 | 7782.9888 |  | 1
75 | 75 | 62 | 48.6386 | 636000 | 508660 | 36.3 | 22000 | 7782.9888 |  | 1
75 | 75 | 57 | 32.2833 | 620000 | 547070 | 35.9 | 22000 | 7782.9888 |  | 1
75 | 75 | 75 | 100 | 785000 | 245535 | 39.3 | 24750 | 10108.5084 |  | 1
75 | 75 | 72 | 86.8609 | 748000 | 311090 | 38.5 | 24750 | 10108.5084 |  | 1
75 | 75 | 67 | 66.7494 | 693000 | 425367.5 | 37.3 | 24750 | 10108.5084 |  | 1
75 | 75 | 62 | 48.6386 | 642000 | 523173.75 | 36.3 | 24750 | 10108.5084 |  | 1
75 | 75 | 57 | 32.2833 | 638000 | 564121.25 | 36.3 | 24750 | 10108.5084 |  | 1
85 | 85 | 75 | 63.5688 | 745000 | 418290 | 42.9 | 22000 | 7782.9888 |  | 1
85 | 85 | 72 | 54.0993 | 712000 | 489130 | 42.2 | 22000 | 7782.9888 |  | 1
85 | 85 | 67 | 39.6049 | 664000 | 599550 | 41.3 | 22000 | 7782.9888 |  | 1
85 | 85 | 62 | 26.5524 | 615000 | 691130 | 40.6 | 22000 | 7782.9888 |  | 1
85 | 85 | 57 | 14.765 | 604000 | 674510 | 40.2 | 22000 | 7782.9888 |  | 1
85 | 85 | 75 | 63.5688 | 755000 | 442826.25 | 43.2 | 24750 | 10108.5084 |  | 1
85 | 85 | 72 | 54.0993 | 721000 | 520271.25 | 42.3 | 24750 | 10108.5084 |  | 1
85 | 85 | 67 | 39.6049 | 673000 | 639632.5 | 41.5 | 24750 | 10108.5084 |  | 1
85 | 85 | 62 | 26.5524 | 623000 | 717826.25 | 40.6 | 24750 | 10108.5084 |  | 1
85 | 85 | 57 | 14.765 | 621000 | 693517.5 | 40.6 | 24750 | 10108.5084 |  | 1
95 | 95 | 75 | 40.2091 | 722000 | 602140 | 47.5 | 22000 | 7782.9888 |  | 1
95 | 95 | 72 | 33.2947 | 691000 | 682660 | 46.9 | 22000 | 7782.9888 |  | 1
95 | 95 | 67 | 22.7111 | 642000 | 792290 | 46.3 | 22000 | 7782.9888 |  | 1
95 | 95 | 62 | 13.1803 | 592000 | 869400 | 45.9 | 22000 | 7782.9888 |  | 1
95 | 95 | 57 | 4.5734 | 585000 | 791910 | 45.6 | 22000 | 7782.9888 |  | 1
95 | 95 | 75 | 40.2091 | 732000 | 649532.5 | 47.8 | 24750 | 10108.5084 |  | 1
95 | 95 | 72 | 33.2947 | 701000 | 728700 | 47.2 | 24750 | 10108.5084 |  | 1
95 | 95 | 67 | 22.7111 | 650000 | 854867.5 | 46.5 | 24750 | 10108.5084 |  | 1
95 | 95 | 62 | 13.1803 | 602000 | 901281.25 | 45.8 | 24750 | 10108.5084 |  | 1
95 | 95 | 57 | 4.5734 | 602000 | 814355 | 45.9 | 24750 | 10108.5084 |  | 1
105 | 105 | 75 | 25.1345 | 697000 | 788950 | 53.1 | 22000 | 7782.9888 |  | 1
105 | 105 | 72 | 20.0232 | 664000 | 879150 | 52.6 | 22000 | 7782.9888 |  | 1
105 | 105 | 67 | 12.1996 | 614000 | 983150 | 52.4 | 22000 | 7782.9888 |  | 1
105 | 105 | 62 | 5.1542 | 565000 | 1020850 | 51.9 | 22000 | 7782.9888 |  | 1
105 | 105 | 57 | -1.2082 | 562000 | 894750 | 52 | 22000 | 7782.9888 |  | 1
105 | 105 | 75 | 25.1345 | 706000 | 861693.75 | 53.4 | 24750 | 10108.5084 |  | 1
105 | 105 | 72 | 20.0232 | 674000 | 944306.25 | 53 | 24750 | 10108.5084 |  | 1
105 | 105 | 67 | 12.1996 | 622000 | 1067112.5 | 52.6 | 24750 | 10108.5084 |  | 1
105 | 105 | 62 | 5.1542 | 578000 | 1062050 | 52.1 | 24750 | 10108.5084 |  | 1
105 | 105 | 57 | -1.2082 | 578000 | 918312.5 | 52.1 | 24750 | 10108.5084 |  | 1
115 | 115 | 75 | 15.3648 | 666000 | 979600 | 59.8 | 22000 | 7782.9888 |  | 1
115 | 115 | 72 | 11.5424 | 633000 | 1068010 | 59.1 | 22000 | 7782.9888 |  | 1
115 | 115 | 67 | 5.6915 | 582000 | 1180480 | 59.9 | 22000 | 7782.9888 |  | 1
115 | 115 | 62 | 0.42275 | 539000 | 1158780 | 60.4 | 22000 | 7782.9888 |  | 1
115 | 115 | 57 | -4.3353 | 536000 | 976440 | 60.8 | 22000 | 7782.9888 |  | 1
115 | 115 | 75 | 15.3648 | 674000 | 1076300 | 60 | 24750 | 10108.5084 |  | 1
115 | 115 | 72 | 11.5424 | 640000 | 1164357.5 | 59.2 | 24750 | 10108.5084 |  | 1
115 | 115 | 67 | 5.6915 | 590000 | 1278357.5 | 60 | 24750 | 10108.5084 |  | 1
115 | 115 | 62 | 0.42275 | 554000 | 1197955 | 60.4 | 24750 | 10108.5084 |  | 1
115 | 115 | 57 | -4.3353 | 553000 | 1010380 | 60.5 | 24750 | 10108.5084 |  | 1
75 | 75 | 75 | 100 | 693000 | 247050 | 37.2 | 11000 | 2335.9385 |  | 2
75 | 75 | 72 | 86.8609 | 657000 | 267202 | 36.5 | 11000 | 2335.9385 |  | 2
75 | 75 | 67 | 66.7494 | 606000 | 326200 | 35.4 | 11000 | 2335.9385 |  | 2
75 | 75 | 62 | 48.6386 | 556000 | 385596 | 34.4 | 11000 | 2335.9385 |  | 2
75 | 75 | 57 | 32.2833 | 513000 | 441596 | 33.6 | 11000 | 2335.9385 |  | 2
75 | 75 | 75 | 100 | 731000 | 251562.5 | 38 | 13750 | 3165.2905 |  | 2
75 | 75 | 72 | 86.8609 | 694000 | 282268.75 | 37.2 | 13750 | 3165.2905 |  | 2
75 | 75 | 67 | 66.7494 | 639000 | 352243.75 | 36.1 | 13750 | 3165.2905 |  | 2
75 | 75 | 62 | 48.6386 | 586000 | 424495 | 35 | 13750 | 3165.2905 |  | 2
75 | 75 | 57 | 32.2833 | 542000 | 478268.75 | 34.2 | 13750 | 3165.2905 |  | 2
75 | 75 | 75 | 100 | 757000 | 241803 | 38.5 | 16500 | 4344.7207 |  | 2
75 | 75 | 72 | 86.8609 | 719000 | 292522.5 | 37.7 | 16500 | 4344.7207 |  | 2
75 | 75 | 67 | 66.7494 | 661000 | 374800 | 36.5 | 16500 | 4344.7207 |  | 2
75 | 75 | 62 | 48.6386 | 609000 | 458892.5 | 35.5 | 16500 | 4344.7207 |  | 2
75 | 75 | 57 | 32.2833 | 575000 | 507597.5 | 34.9 | 16500 | 4344.7207 |  | 2
75 | 75 | 75 | 100 | 776000 | 247952.5 | 38.8 | 19250 | 5872.1453 |  | 2
75 | 75 | 72 | 86.8609 | 737000 | 301835 | 38.1 | 19250 | 5872.1453 |  | 2
75 | 75 | 67 | 66.7494 | 678000 | 396658.75 | 36.9 | 19250 | 5872.1453 |  | 2
75 | 75 | 62 | 48.6386 | 625000 | 489658.75 | 35.8 | 19250 | 5872.1453 |  | 2
75 | 75 | 57 | 32.2833 | 602000 | 531833.75 | 35.4 | 19250 | 5872.1453 |  | 2
85 | 85 | 75 | 63.5688 | 675000 | 314950 | 41.1 | 11000 | 2335.9385 |  | 2
85 | 85 | 72 | 54.0993 | 641000 | 362798 | 40.4 | 11000 | 2335.9385 |  | 2
85 | 85 | 67 | 39.6049 | 591000 | 425405 | 39.3 | 11000 | 2335.9385 |  | 2
85 | 85 | 62 | 26.5524 | 544000 | 482798 | 38.5 | 11000 | 2335.9385 |  | 2
85 | 85 | 57 | 14.765 | 501000 | 538404 | 37.9 | 11000 | 2335.9385 |  | 2
85 | 85 | 75 | 63.5688 | 709000 | 339437.5 | 41.9 | 13750 | 3165.2905 |  | 2
85 | 85 | 72 | 54.0993 | 674000 | 403487.5 | 41.1 | 13750 | 3165.2905 |  | 2
85 | 85 | 67 | 39.6049 | 623000 | 478756.25 | 40 | 13750 | 3165.2905 |  | 2
85 | 85 | 62 | 26.5524 | 573000 | 549505 | 39 | 13750 | 3165.2905 |  | 2
85 | 85 | 57 | 14.765 | 532000 | 594218.75 | 38.3 | 13750 | 3165.2905 |  | 2
85 | 85 | 75 | 63.5688 | 735000 | 382032.5 | 42.4 | 16500 | 4344.7207 |  | 2
85 | 85 | 72 | 54.0993 | 699000 | 437477.5 | 41.6 | 16500 | 4344.7207 |  | 2
85 | 85 | 67 | 39.6049 | 645000 | 526200 | 40.5 | 16500 | 4344.7207 |  | 2
85 | 85 | 62 | 26.5524 | 596000 | 612107.5 | 39.6 | 16500 | 4344.7207 |  | 2
85 | 85 | 57 | 14.765 | 565000 | 630587.5 | 38.9 | 16500 | 4344.7207 |  | 2
85 | 85 | 75 | 63.5688 | 757000 | 414106.25 | 42.9 | 19250 | 5872.1453 |  | 2
85 | 85 | 72 | 54.0993 | 717000 | 472223.75 | 42 | 19250 | 5872.1453 |  | 2
85 | 85 | 67 | 39.6049 | 661000 | 572341.25 | 40.9 | 19250 | 5872.1453 |  | 2
85 | 85 | 62 | 26.5524 | 609000 | 666341.25 | 39.8 | 19250 | 5872.1453 |  | 2
85 | 85 | 57 | 14.765 | 591000 | 660107.5 | 39.5 | 19250 | 5872.1453 |  | 2
95 | 95 | 75 | 40.2091 | 659000 | 452500 | 45.7 | 11000 | 2335.9385 |  | 2
95 | 95 | 72 | 33.2947 | 627000 | 476610 | 45.1 | 11000 | 2335.9385 |  | 2
95 | 95 | 67 | 22.7111 | 578000 | 528535 | 44.3 | 11000 | 2335.9385 |  | 2
95 | 95 | 62 | 13.1803 | 530000 | 591980 | 43.5 | 11000 | 2335.9385 |  | 2
95 | 95 | 57 | 4.5734 | 487000 | 641535 | 43.4 | 11000 | 2073.3799 |  | 2
95 | 95 | 75 | 40.2091 | 692000 | 488918.75 | 46.5 | 13750 | 3165.2905 |  | 2
95 | 95 | 72 | 33.2947 | 659000 | 530381.25 | 45.9 | 13750 | 3165.2905 |  | 2
95 | 95 | 67 | 22.7111 | 608000 | 606918.75 | 44.9 | 13750 | 3165.2905 |  | 2
95 | 95 | 62 | 13.1803 | 558000 | 680187.5 | 44.1 | 13750 | 3165.2905 |  | 2
95 | 95 | 57 | 4.5734 | 519000 | 702768.75 | 43.5 | 13750 | 3165.2905 |  | 2
95 | 95 | 75 | 40.2091 | 719000 | 525522.5 | 47.4 | 16500 | 4344.7207 |  | 2
95 | 95 | 72 | 33.2947 | 682000 | 589135 | 46.5 | 16500 | 4344.7207 |  | 2
95 | 95 | 67 | 22.7111 | 628000 | 679580 | 45.5 | 16500 | 4344.7207 |  | 2
95 | 95 | 62 | 13.1803 | 576000 | 770025 | 44.5 | 16500 | 4344.7207 |  | 2
95 | 95 | 57 | 4.5734 | 551000 | 747020 | 44.1 | 16500 | 4344.7207 |  | 2
95 | 95 | 75 | 40.2091 | 737000 | 584628.75 | 48 | 19250 | 5872.1453 |  | 2
95 | 95 | 72 | 33.2947 | 699000 | 645981.25 | 47 | 19250 | 5872.1453 |  | 2
95 | 95 | 67 | 22.7111 | 644000 | 750333.75 | 45.9 | 19250 | 5872.1453 |  | 2
95 | 95 | 62 | 13.1803 | 592000 | 830981.25 | 44.9 | 19250 | 5872.1453 |  | 2
95 | 95 | 57 | 4.5734 | 577000 | 780280 | 44.6 | 19250 | 5872.1453 |  | 2
105 | 105 | 75 | 25.1345 | 641000 | 566500 | 51.6 | 11000 | 2335.9385 |  | 2
105 | 105 | 72 | 20.0232 | 610000 | 547050 | 51.1 | 11000 | 2335.9385 |  | 2
105 | 105 | 67 | 12.1996 | 558000 | 630250 | 50.6 | 11000 | 2335.9385 |  | 2
105 | 105 | 62 | 5.1542 | 507000 | 696325 | 49.7 | 11000 | 2335.9385 |  | 2
105 | 105 | 57 | -1.2082 | 463000 | 724200 | 50.7 | 11000 | 2073.3799 |  | 2
105 | 105 | 75 | 25.1345 | 674000 | 625093.75 | 52.9 | 13750 | 3165.2905 |  | 2
105 | 105 | 72 | 20.0232 | 639000 | 657750 | 51.9 | 13750 | 3165.2905 |  | 2
105 | 105 | 67 | 12.1996 | 586000 | 736312.5 | 51.3 | 13750 | 3165.2905 |  | 2
105 | 105 | 62 | 5.1542 | 534000 | 814875 | 50.2 | 13750 | 3165.2905 |  | 2
105 | 105 | 57 | -1.2082 | 503000 | 801718.75 | 49.3 | 13750 | 3165.2905 |  | 2
105 | 105 | 75 | 25.1345 | 696000 | 674612.5 | 54 | 16500 | 4344.7207 |  | 2
105 | 105 | 72 | 20.0232 | 659000 | 737225 | 52.9 | 16500 | 4344.7207 |  | 2
105 | 105 | 67 | 12.1996 | 605000 | 834837.5 | 51.9 | 16500 | 4344.7207 |  | 2
105 | 105 | 62 | 5.1542 | 555000 | 908300 | 51.2 | 16500 | 4344.7207 |  | 2
105 | 105 | 57 | -1.2082 | 533000 | 846087.5 | 50.7 | 16500 | 4344.7207 |  | 2
105 | 105 | 75 | 25.1345 | 711000 | 761968.75 | 54.8 | 19250 | 5872.1453 |  | 2
105 | 105 | 72 | 20.0232 | 674000 | 816968.75 | 53.5 | 19250 | 5872.1453 |  | 2
105 | 105 | 67 | 12.1996 | 619000 | 924556.25 | 52.3 | 19250 | 5872.1453 |  | 2
105 | 105 | 62 | 5.1542 | 568000 | 997968.75 | 51.4 | 19250 | 5872.1453 |  | 2
105 | 105 | 57 | -1.2082 | 558000 | 886212.5 | 51.1 | 19250 | 5872.1453 |  | 2
115 | 115 | 75 | 15.3648 | 615000 | 675500 | 60.1 | 11000 | 2335.9385 |  | 2
115 | 115 | 72 | 11.5424 | 581000 | 653210 | 59.8 | 11000 | 2335.9385 |  | 2
115 | 115 | 67 | 5.6915 | 528000 | 730385 | 59.8 | 11000 | 2335.9385 |  | 2
115 | 115 | 62 | 0.42275 | 476000 | 793855 | 58.7 | 11000 | 2073.3799 |  | 2
115 | 115 | 57 | -4.3353 | 436000 | 788740 | 60.6 | 11000 | 2073.3799 |  | 2
115 | 115 | 75 | 15.3648 | 644000 | 694500 | 62.3 | 13750 | 3165.2905 |  | 2
115 | 115 | 72 | 11.5424 | 609000 | 779850 | 61 | 13750 | 3165.2905 |  | 2
115 | 115 | 67 | 5.6915 | 554000 | 859437.5 | 60.6 | 13750 | 3165.2905 |  | 2
115 | 115 | 62 | 0.42275 | 502000 | 931731.25 | 61 | 13750 | 3165.2905 |  | 2
115 | 115 | 57 | -4.3353 | 475000 | 866737.5 | 60.4 | 13750 | 2894.3966 |  | 2
115 | 115 | 75 | 15.3648 | 663000 | 826962.5 | 64.3 | 16500 | 4344.7207 |  | 2
115 | 115 | 72 | 11.5424 | 627000 | 887667.5 | 62.2 | 16500 | 4344.7207 |  | 2
115 | 115 | 67 | 5.6915 | 572000 | 983372.5 | 61.4 | 16500 | 4344.7207 |  | 2
115 | 115 | 62 | 0.42275 | 519000 | 1053020 | 61.3 | 16500 | 4344.7207 |  | 2
115 | 115 | 57 | -4.3353 | 505000 | 924265 | 60.6 | 16500 | 4344.7207 |  | 2
115 | 115 | 72 | 11.5424 | 641000 | 993367.5 | 63.6 | 19250 | 5872.1453 |  | 2
115 | 115 | 67 | 5.6915 | 585000 | 1095778.75 | 61.9 | 19250 | 5872.1453 |  | 2
115 | 115 | 62 | 0.42275 | 537000 | 1130722.5 | 60.8 | 19250 | 5872.1453 |  | 2
115 | 115 | 57 | -4.3353 | 529000 | 966263.75 | 61.1 | 19250 | 5872.1453 |  | 2
75 | 75 | 75 | 100 | 791000 | 248450 | 39.1 | 22000 | 7782.9888 |  | 2
75 | 75 | 72 | 86.8609 | 751000 | 309240 | 38.3 | 22000 | 7782.9888 |  | 2
75 | 75 | 67 | 66.7494 | 691000 | 416820 | 37.2 | 22000 | 7782.9888 |  | 2
75 | 75 | 62 | 48.6386 | 637000 | 514450 | 36.1 | 22000 | 7782.9888 |  | 2
75 | 75 | 57 | 32.2833 | 625000 | 552070 | 35.8 | 22000 | 7782.9888 |  | 2
75 | 75 | 75 | 100 | 805000 | 251090 | 39.4 | 24750 | 10108.5084 |  | 2
75 | 75 | 72 | 86.8609 | 762000 | 317006.25 | 38.6 | 24750 | 10108.5084 |  | 2
75 | 75 | 67 | 66.7494 | 702000 | 435283.75 | 37.4 | 24750 | 10108.5084 |  | 2
75 | 75 | 62 | 48.6386 | 650000 | 533812.5 | 36.4 | 24750 | 10108.5084 |  | 2
75 | 75 | 57 | 32.2833 | 644000 | 568760 | 36.2 | 24750 | 10108.5084 |  | 2
85 | 85 | 75 | 63.5688 | 771000 | 440550 | 43.2 | 22000 | 7782.9888 |  | 2
85 | 85 | 72 | 54.0993 | 730000 | 503760 | 42.4 | 22000 | 7782.9888 |  | 2
85 | 85 | 67 | 39.6049 | 673000 | 615180 | 41.2 | 22000 | 7782.9888 |  | 2
85 | 85 | 62 | 26.5524 | 621000 | 705550 | 40.1 | 22000 | 7782.9888 |  | 2
85 | 85 | 57 | 14.765 | 612000 | 683720 | 39.9 | 22000 | 7782.9888 |  | 2
85 | 85 | 75 | 63.5688 | 787000 | 463271.25 | 43.7 | 24750 | 10108.5084 |  | 2
85 | 85 | 72 | 54.0993 | 743000 | 532632.5 | 42.7 | 24750 | 10108.5084 |  | 2
85 | 85 | 67 | 39.6049 | 684000 | 657716.25 | 41.4 | 24750 | 10108.5084 |  | 2
85 | 85 | 62 | 26.5524 | 634000 | 722465 | 40.4 | 24750 | 10108.5084 |  | 2
85 | 85 | 57 | 14.765 | 632000 | 705878.75 | 40.3 | 24750 | 10108.5084 |  | 2
95 | 95 | 75 | 40.2091 | 753000 | 630660 | 48.8 | 22000 | 7782.9888 |  | 2
95 | 95 | 72 | 33.2947 | 713000 | 697290 | 47.6 | 22000 | 7782.9888 |  | 2
95 | 95 | 67 | 22.7111 | 655000 | 817180 | 46.2 | 22000 | 7782.9888 |  | 2
95 | 95 | 62 | 13.1803 | 606000 | 879400 | 45.2 | 22000 | 7782.9888 |  | 2
95 | 95 | 57 | 4.5734 | 598000 | 808540 | 45 | 22000 | 7782.9888 |  | 2
95 | 95 | 75 | 40.2091 | 764000 | 676783.75 | 49.3 | 24750 | 10108.5084 |  | 2
95 | 95 | 72 | 33.2947 | 723000 | 754951.25 | 47.8 | 24750 | 10108.5084 |  | 2
95 | 95 | 67 | 22.7111 | 665000 | 883118.75 | 46.5 | 24750 | 10108.5084 |  | 2
95 | 95 | 62 | 13.1803 | 617000 | 916281.25 | 45.3 | 24750 | 10108.5084 |  | 2
95 | 95 | 57 | 4.5734 | 616000 | 832438.75 | 45.4 | 24750 | 10108.5084 |  | 2
105 | 105 | 75 | 25.1345 | 724000 | 820100 | 56.4 | 22000 | 7782.9888 |  | 2
105 | 105 | 72 | 20.0232 | 686000 | 895200 | 54.1 | 22000 | 7782.9888 |  | 2
105 | 105 | 67 | 12.1996 | 630000 | 1015300 | 52.7 | 22000 | 7782.9888 |  | 2
105 | 105 | 62 | 5.1542 | 584000 | 1041900 | 51.4 | 22000 | 7782.9888 |  | 2
105 | 105 | 57 | -1.2082 | 578000 | 916800 | 51.6 | 22000 | 7782.9888 |  | 2
105 | 105 | 75 | 25.1345 | 733000 | 894112.5 | 57.1 | 24750 | 10108.5084 |  | 2
105 | 105 | 72 | 20.0232 | 696000 | 970918.75 | 54.8 | 24750 | 10108.5084 |  | 2
105 | 105 | 67 | 12.1996 | 638000 | 1103531.25 | 52.9 | 24750 | 10108.5084 |  | 2
105 | 105 | 62 | 5.1542 | 596000 | 1099662.5 | 52 | 24750 | 10108.5084 |  | 2
105 | 105 | 57 | -1.2082 | 596000 | 949925 | 51.9 | 24750 | 10108.5084 |  | 2
115 | 115 | 72 | 11.5424 | 652000 | 1086480 | 65 | 22000 | 7782.9888 |  | 2
115 | 115 | 67 | 5.6915 | 595000 | 1210420 | 62.3 | 22000 | 7782.9888 |  | 2
115 | 115 | 62 | 0.42275 | 551000 | 1191720 | 61.3 | 22000 | 7782.9888 |  | 2
115 | 115 | 57 | -4.3353 | 550000 | 1007380 | 61.4 | 22000 | 7782.9888 |  | 2
115 | 115 | 67 | 5.6915 | 603000 | 1311415 | 63.1 | 24750 | 10108.5084 |  | 2
115 | 115 | 62 | 0.42275 | 570000 | 1218483.75 | 61.2 | 24750 | 10108.5084 |  | 2
115 | 115 | 57 | -4.3353 | 567000 | 1033908.75 | 61.7 | 24750 | 10108.5084 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 6
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 75 | 75 | 100 | 751000 | 266600 | 43.7 | 12000 | 2535.9832 |  | 1
75 | 75 | 72 | 86.8609 | 718000 | 297600 | 42.9 | 12000 | 2535.9832 |  | 1
75 | 75 | 67 | 66.7494 | 664000 | 355700 | 41.6 | 12000 | 2535.9832 |  | 1
75 | 75 | 62 | 48.6386 | 611000 | 416400 | 40.7 | 12000 | 2535.9832 |  | 1
75 | 75 | 57 | 32.2833 | 558000 | 471740 | 40.4 | 12000 | 2535.9832 |  | 1
75 | 75 | 75 | 100 | 791000 | 266250 | 44.7 | 15000 | 3640.3966 |  | 1
75 | 75 | 72 | 86.8609 | 752000 | 294350 | 43.7 | 15000 | 3640.3966 |  | 1
75 | 75 | 67 | 66.7494 | 698000 | 380300 | 42.4 | 15000 | 3640.3966 |  | 1
75 | 75 | 62 | 48.6386 | 644000 | 456825 | 41.4 | 15000 | 3640.3966 |  | 1
75 | 75 | 57 | 32.2833 | 589000 | 507950 | 40.5 | 15000 | 3640.3966 |  | 1
75 | 75 | 75 | 100 | 816000 | 272900 | 45.4 | 18000 | 5232.419 |  | 1
75 | 75 | 72 | 86.8609 | 777000 | 316500 | 44.4 | 18000 | 5232.419 |  | 1
75 | 75 | 67 | 66.7494 | 721000 | 402560 | 43 | 18000 | 5232.419 |  | 1
75 | 75 | 62 | 48.6386 | 667000 | 492580 | 41.9 | 18000 | 5232.419 |  | 1
75 | 75 | 57 | 32.2833 | 624000 | 551460 | 41.2 | 18000 | 5232.419 |  | 1
75 | 75 | 75 | 100 | 834000 | 250200 | 45.9 | 21000 | 7355.8101 |  | 1
75 | 75 | 72 | 86.8609 | 796000 | 324595 | 44.8 | 21000 | 7355.8101 |  | 1
75 | 75 | 67 | 66.7494 | 739000 | 424975 | 43.4 | 21000 | 7355.8101 |  | 1
75 | 75 | 62 | 48.6386 | 684000 | 525975 | 42.4 | 21000 | 7355.8101 |  | 1
75 | 75 | 57 | 32.2833 | 653000 | 576455 | 41.7 | 21000 | 7355.8101 |  | 1
85 | 85 | 75 | 63.5688 | 730000 | 339400 | 48.1 | 12000 | 2535.9832 |  | 1
85 | 85 | 72 | 54.0993 | 701000 | 375400 | 47.4 | 12000 | 2535.9832 |  | 1
85 | 85 | 67 | 39.6049 | 647000 | 457960 | 46.4 | 12000 | 2535.9832 |  | 1
85 | 85 | 62 | 26.5524 | 593000 | 522600 | 46 | 12000 | 2535.9832 |  | 1
85 | 85 | 57 | 14.765 | 539000 | 575600 | 46 | 12000 | 2535.9832 |  | 1
85 | 85 | 75 | 63.5688 | 765000 | 357750 | 49.1 | 15000 | 3640.3966 |  | 1
85 | 85 | 72 | 54.0993 | 733000 | 422275 | 48.2 | 15000 | 3640.3966 |  | 1
85 | 85 | 67 | 39.6049 | 679000 | 511525 | 47.3 | 15000 | 3640.3966 |  | 1
85 | 85 | 62 | 26.5524 | 625000 | 590175 | 46.6 | 15000 | 3640.3966 |  | 1
85 | 85 | 57 | 14.765 | 573000 | 622575 | 45.7 | 15000 | 3640.3966 |  | 1
85 | 85 | 75 | 63.5688 | 787000 | 388100 | 49.7 | 18000 | 5232.419 |  | 1
85 | 85 | 72 | 54.0993 | 756000 | 463480 | 48.9 | 18000 | 5232.419 |  | 1
85 | 85 | 67 | 39.6049 | 701000 | 560440 | 47.8 | 18000 | 5232.419 |  | 1
85 | 85 | 62 | 26.5524 | 647000 | 652420 | 47 | 18000 | 5232.419 |  | 1
85 | 85 | 57 | 14.765 | 607000 | 678550 | 46.6 | 18000 | 5232.419 |  | 1
85 | 85 | 75 | 63.5688 | 803000 | 422165 | 50.1 | 21000 | 7355.8101 |  | 1
85 | 85 | 72 | 54.0993 | 773000 | 498560 | 49.3 | 21000 | 7355.8101 |  | 1
85 | 85 | 67 | 39.6049 | 718000 | 606025 | 48.2 | 21000 | 7355.8101 |  | 1
85 | 85 | 62 | 26.5524 | 663000 | 706025 | 47.5 | 21000 | 7355.8101 |  | 1
85 | 85 | 57 | 14.765 | 636000 | 710235 | 47 | 21000 | 7355.8101 |  | 1
95 | 95 | 75 | 40.2091 | 711000 | 489000 | 53.5 | 12000 | 2535.9832 |  | 1
95 | 95 | 72 | 33.2947 | 681000 | 525000 | 53 | 12000 | 2535.9832 |  | 1
95 | 95 | 67 | 22.7111 | 626000 | 563280 | 52.5 | 12000 | 2535.9832 |  | 1
95 | 95 | 62 | 13.1803 | 572000 | 630220 | 52.3 | 12000 | 2535.9832 |  | 1
95 | 95 | 57 | 4.5734 | 515000 | 668280 | 53.8 | 12000 | 2535.9832 |  | 1
95 | 95 | 75 | 40.2091 | 744000 | 547500 | 54.4 | 15000 | 3640.3966 |  | 1
95 | 95 | 72 | 33.2947 | 711000 | 546050 | 53.8 | 15000 | 3640.3966 |  | 1
95 | 95 | 67 | 22.7111 | 656000 | 642375 | 53.3 | 15000 | 3640.3966 |  | 1
95 | 95 | 62 | 13.1803 | 601000 | 724800 | 52.7 | 15000 | 3640.3966 |  | 1
95 | 95 | 57 | 4.5734 | 554000 | 748525 | 53.2 | 15000 | 3640.3966 |  | 1
95 | 95 | 75 | 40.2091 | 764000 | 577390 | 54.9 | 18000 | 5232.419 |  | 1
95 | 95 | 72 | 33.2947 | 733000 | 617570 | 54.4 | 18000 | 5232.419 |  | 1
95 | 95 | 67 | 22.7111 | 677000 | 717480 | 53.7 | 18000 | 5232.419 |  | 1
95 | 95 | 62 | 13.1803 | 622000 | 811420 | 53.3 | 18000 | 5232.419 |  | 1
95 | 95 | 57 | 4.5734 | 587000 | 794900 | 53.2 | 18000 | 5232.419 |  | 1
95 | 95 | 75 | 40.2091 | 779000 | 590410 | 55.4 | 21000 | 7355.8101 |  | 1
95 | 95 | 72 | 33.2947 | 748000 | 679665 | 54.8 | 21000 | 7355.8101 |  | 1
95 | 95 | 67 | 22.7111 | 692000 | 788595 | 54.1 | 21000 | 7355.8101 |  | 1
95 | 95 | 62 | 13.1803 | 636000 | 885595 | 53.6 | 21000 | 7355.8101 |  | 1
95 | 95 | 57 | 4.5734 | 616000 | 834295 | 53.1 | 21000 | 7355.8101 |  | 1
105 | 105 | 75 | 25.1345 | 686000 | 611000 | 60 | 12000 | 2535.9832 |  | 1
105 | 105 | 72 | 20.0232 | 655000 | 607400 | 59.8 | 12000 | 2535.9832 |  | 1
105 | 105 | 67 | 12.1996 | 600000 | 669100 | 59.8 | 12000 | 2535.9832 |  | 1
105 | 105 | 62 | 5.1542 | 546000 | 735700 | 61.6 | 12000 | 2535.9832 |  | 1
105 | 105 | 57 | -1.2082 | 489000 | 767800 | 64.9 | 12000 | 2273.4246 |  | 1
105 | 105 | 75 | 25.1345 | 716000 | 705500 | 60.8 | 15000 | 3640.3966 |  | 1
105 | 105 | 72 | 20.0232 | 683000 | 673000 | 60.5 | 15000 | 3640.3966 |  | 1
105 | 105 | 67 | 12.1996 | 627000 | 774750 | 60.5 | 15000 | 3640.3966 |  | 1
105 | 105 | 62 | 5.1542 | 573000 | 858000 | 61.6 | 15000 | 3640.3966 |  | 1
105 | 105 | 57 | -1.2082 | 531000 | 844500 | 63 | 15000 | 3640.3966 |  | 1
105 | 105 | 75 | 25.1345 | 735000 | 656500 | 61.3 | 18000 | 5232.419 |  | 1
105 | 105 | 72 | 20.0232 | 703000 | 772900 | 61.1 | 18000 | 5232.419 |  | 1
105 | 105 | 67 | 12.1996 | 647000 | 876750 | 60.8 | 18000 | 5232.419 |  | 1
105 | 105 | 62 | 5.1542 | 591000 | 961750 | 62.3 | 18000 | 5232.419 |  | 1
105 | 105 | 57 | -1.2082 | 564000 | 895650 | 62.4 | 18000 | 5232.419 |  | 1
105 | 105 | 75 | 25.1345 | 748000 | 768675 | 61.6 | 21000 | 7355.8101 |  | 1
105 | 105 | 72 | 20.0232 | 717000 | 855775 | 61.4 | 21000 | 7355.8101 |  | 1
105 | 105 | 67 | 12.1996 | 661000 | 968325 | 61.1 | 21000 | 7355.8101 |  | 1
105 | 105 | 62 | 5.1542 | 605000 | 1055325 | 62.2 | 21000 | 7355.8101 |  | 1
105 | 105 | 57 | -1.2082 | 591000 | 943275 | 61.8 | 21000 | 7355.8101 |  | 1
115 | 115 | 75 | 15.3648 | 657000 | 727000 | 67.5 | 12000 | 2535.9832 |  | 1
115 | 115 | 72 | 11.5424 | 624000 | 652500 | 68 | 12000 | 2535.9832 |  | 1
115 | 115 | 67 | 5.6915 | 569000 | 775560 | 69.8 | 12000 | 2535.9832 |  | 1
115 | 115 | 75 | 15.3648 | 682000 | 860500 | 68.1 | 15000 | 3640.3966 |  | 1
115 | 115 | 72 | 11.5424 | 650000 | 805550 | 68.7 | 15000 | 3640.3966 |  | 1
115 | 115 | 67 | 5.6915 | 594000 | 903650 | 70.2 | 15000 | 3640.3966 |  | 1
115 | 115 | 75 | 15.3648 | 700000 | 825680 | 68.8 | 18000 | 5232.419 |  | 1
115 | 115 | 72 | 11.5424 | 668000 | 929190 | 69.1 | 18000 | 5232.419 |  | 1
115 | 115 | 67 | 5.6915 | 612000 | 1031050 | 70.3 | 18000 | 5232.419 |  | 1
115 | 115 | 62 | 0.42275 | 554000 | 1111050 | 73.7 | 18000 | 5232.419 |  | 1
115 | 115 | 75 | 15.3648 | 714000 | 943630 | 69.4 | 21000 | 7355.8101 |  | 1
115 | 115 | 72 | 11.5424 | 681000 | 1038970 | 69.5 | 21000 | 7355.8101 |  | 1
115 | 115 | 67 | 5.6915 | 625000 | 1155140 | 70.4 | 21000 | 7355.8101 |  | 1
115 | 115 | 62 | 0.42275 | 570000 | 1202800 | 72.7 | 21000 | 7355.8101 |  | 1
115 | 115 | 57 | -4.3353 | 562000 | 1030930 | 72.3 | 21000 | 7355.8101 |  | 1
75 | 75 | 75 | 100 | 848000 | 270920 | 46.2 | 24000 | 10035.5754 |  | 1
75 | 75 | 72 | 86.8609 | 809000 | 332680 | 45.2 | 24000 | 10035.5754 |  | 1
75 | 75 | 67 | 66.7494 | 752000 | 446040 | 43.7 | 24000 | 10035.5754 |  | 1
75 | 75 | 62 | 48.6386 | 697000 | 554040 | 42.7 | 24000 | 10035.5754 |  | 1
75 | 75 | 57 | 32.2833 | 677000 | 597440 | 42.2 | 24000 | 10035.5754 |  | 1
75 | 75 | 75 | 100 | 861000 | 270190 | 46.6 | 27000 | 13344.648 |  | 1
75 | 75 | 72 | 86.8609 | 820000 | 339765 | 45.5 | 27000 | 13344.648 |  | 1
75 | 75 | 67 | 66.7494 | 762000 | 465280 | 44 | 27000 | 13344.648 |  | 1
75 | 75 | 62 | 48.6386 | 707000 | 576735 | 42.8 | 27000 | 13344.648 |  | 1
75 | 75 | 57 | 32.2833 | 698000 | 615920 | 42.5 | 27000 | 13344.648 |  | 1
85 | 85 | 75 | 63.5688 | 816000 | 454040 | 50.4 | 24000 | 10035.5754 |  | 1
85 | 85 | 72 | 54.0993 | 785000 | 532640 | 49.7 | 24000 | 10035.5754 |  | 1
85 | 85 | 67 | 39.6049 | 730000 | 651280 | 48.5 | 24000 | 10035.5754 |  | 1
85 | 85 | 62 | 26.5524 | 675000 | 752640 | 47.8 | 24000 | 10035.5754 |  | 1
85 | 85 | 57 | 14.765 | 660000 | 736920 | 47.2 | 24000 | 10035.5754 |  | 1
85 | 85 | 75 | 63.5688 | 829000 | 479295 | 50.8 | 27000 | 13344.648 |  | 1
85 | 85 | 72 | 54.0993 | 794000 | 563235 | 49.9 | 27000 | 13344.648 |  | 1
85 | 85 | 67 | 39.6049 | 740000 | 694205 | 48.8 | 27000 | 13344.648 |  | 1
85 | 85 | 62 | 26.5524 | 686000 | 779295 | 47.7 | 27000 | 13344.648 |  | 1
85 | 85 | 57 | 14.765 | 680000 | 759110 | 47.7 | 27000 | 13344.648 |  | 1
95 | 95 | 75 | 40.2091 | 793000 | 648960 | 55.8 | 24000 | 10035.5754 |  | 1
95 | 95 | 72 | 33.2947 | 759000 | 735800 | 55.1 | 24000 | 10035.5754 |  | 1
95 | 95 | 67 | 22.7111 | 704000 | 858720 | 54.4 | 24000 | 10035.5754 |  | 1
95 | 95 | 62 | 13.1803 | 648000 | 942840 | 53.8 | 24000 | 10035.5754 |  | 1
95 | 95 | 57 | 4.5734 | 638000 | 863720 | 53.5 | 24000 | 10035.5754 |  | 1
95 | 95 | 75 | 40.2091 | 803000 | 699580 | 56.1 | 27000 | 13344.648 |  | 1
95 | 95 | 72 | 33.2947 | 768000 | 790945 | 55.3 | 27000 | 13344.648 |  | 1
95 | 95 | 67 | 22.7111 | 713000 | 925855 | 54.6 | 27000 | 13344.648 |  | 1
95 | 95 | 62 | 13.1803 | 660000 | 981670 | 53.7 | 27000 | 13344.648 |  | 1
95 | 95 | 57 | 4.5734 | 658000 | 889660 | 53.8 | 27000 | 13344.648 |  | 1
105 | 105 | 75 | 25.1345 | 762000 | 846200 | 62.2 | 24000 | 10035.5754 |  | 1
105 | 105 | 72 | 20.0232 | 728000 | 936000 | 61.7 | 24000 | 10035.5754 |  | 1
105 | 105 | 67 | 12.1996 | 671000 | 1062200 | 61.3 | 24000 | 10035.5754 |  | 1
105 | 105 | 62 | 5.1542 | 620000 | 1106600 | 61.2 | 24000 | 10035.5754 |  | 1
105 | 105 | 57 | -1.2082 | 614000 | 977000 | 61.4 | 24000 | 10035.5754 |  | 1
105 | 105 | 75 | 25.1345 | 771000 | 923725 | 62.6 | 27000 | 13344.648 |  | 1
105 | 105 | 72 | 20.0232 | 736000 | 1013575 | 62.1 | 27000 | 13344.648 |  | 1
105 | 105 | 67 | 12.1996 | 680000 | 1153425 | 61.5 | 27000 | 13344.648 |  | 1
105 | 105 | 62 | 5.1542 | 632000 | 1159600 | 61.2 | 27000 | 13344.648 |  | 1
105 | 105 | 57 | -1.2082 | 632000 | 1003250 | 61.5 | 27000 | 13344.648 |  | 1
115 | 115 | 75 | 15.3648 | 724000 | 1047720 | 69.8 | 24000 | 10035.5754 |  | 1
115 | 115 | 72 | 11.5424 | 691000 | 1144440 | 69.5 | 24000 | 10035.5754 |  | 1
115 | 115 | 67 | 5.6915 | 635000 | 1265680 | 70.3 | 24000 | 10035.5754 |  | 1
115 | 115 | 62 | 0.42275 | 586000 | 1264760 | 71.2 | 24000 | 10035.5754 |  | 1
115 | 115 | 57 | -4.3353 | 584000 | 1064480 | 71.7 | 24000 | 10035.5754 |  | 1
115 | 115 | 75 | 15.3648 | 732000 | 1150810 | 70.1 | 27000 | 13344.648 |  | 1
115 | 115 | 72 | 11.5424 | 697000 | 1246600 | 69.2 | 27000 | 13344.648 |  | 1
115 | 115 | 67 | 5.6915 | 643000 | 1379995 | 70.4 | 27000 | 13344.648 |  | 1
115 | 115 | 62 | 0.42275 | 602000 | 1319255 | 71.3 | 27000 | 13344.648 |  | 1
115 | 115 | 57 | -4.3353 | 602000 | 1100960 | 71.3 | 27000 | 13344.648 |  | 1
75 | 75 | 75 | 100 | 761000 | 271600 | 43.9 | 12000 | 2535.9832 |  | 2
75 | 75 | 72 | 86.8609 | 725000 | 307600 | 43 | 12000 | 2535.9832 |  | 2
75 | 75 | 67 | 66.7494 | 664000 | 357400 | 41.4 | 12000 | 2535.9832 |  | 2
75 | 75 | 62 | 48.6386 | 610000 | 421832 | 40.1 | 12000 | 2535.9832 |  | 2
75 | 75 | 57 | 32.2833 | 561000 | 483584 | 39 | 12000 | 2535.9832 |  | 2
75 | 75 | 75 | 100 | 802000 | 276250 | 44.9 | 15000 | 3640.3966 |  | 2
75 | 75 | 72 | 86.8609 | 762000 | 310125 | 43.9 | 15000 | 3640.3966 |  | 2
75 | 75 | 67 | 66.7494 | 700000 | 385000 | 42.3 | 15000 | 3640.3966 |  | 2
75 | 75 | 62 | 48.6386 | 643000 | 460350 | 40.9 | 15000 | 3640.3966 |  | 2
75 | 75 | 57 | 32.2833 | 594000 | 524475 | 39.8 | 15000 | 3640.3966 |  | 2
75 | 75 | 75 | 100 | 830000 | 258620 | 45.5 | 18000 | 5232.419 |  | 2
75 | 75 | 72 | 86.8609 | 789000 | 321560 | 44.5 | 18000 | 5232.419 |  | 2
75 | 75 | 67 | 66.7494 | 725000 | 409590 | 42.9 | 18000 | 5232.419 |  | 2
75 | 75 | 62 | 48.6386 | 666000 | 500610 | 41.4 | 18000 | 5232.419 |  | 2
75 | 75 | 57 | 32.2833 | 628000 | 554470 | 40.7 | 18000 | 5232.419 |  | 2
75 | 75 | 75 | 100 | 851000 | 273595 | 46 | 21000 | 7355.8101 |  | 2
75 | 75 | 72 | 86.8609 | 809000 | 330975 | 45 | 21000 | 7355.8101 |  | 2
75 | 75 | 67 | 66.7494 | 744000 | 432510 | 43.4 | 21000 | 7355.8101 |  | 2
75 | 75 | 62 | 48.6386 | 685000 | 531665 | 42 | 21000 | 7355.8101 |  | 2
75 | 75 | 57 | 32.2833 | 659000 | 582455 | 41.3 | 21000 | 7355.8101 |  | 2
85 | 85 | 75 | 63.5688 | 741000 | 345400 | 48.2 | 12000 | 2535.9832 |  | 2
85 | 85 | 72 | 54.0993 | 705000 | 399168 | 47.3 | 12000 | 2535.9832 |  | 2
85 | 85 | 67 | 39.6049 | 651000 | 465600 | 45.9 | 12000 | 2535.9832 |  | 2
85 | 85 | 62 | 26.5524 | 599000 | 530168 | 44.8 | 12000 | 2535.9832 |  | 2
85 | 85 | 57 | 14.765 | 549000 | 582168 | 44.1 | 12000 | 2535.9832 |  | 2
85 | 85 | 75 | 63.5688 | 779000 | 370750 | 49.2 | 15000 | 3640.3966 |  | 2
85 | 85 | 72 | 54.0993 | 741000 | 438700 | 48.2 | 15000 | 3640.3966 |  | 2
85 | 85 | 67 | 39.6049 | 685000 | 522000 | 46.8 | 15000 | 3640.3966 |  | 2
85 | 85 | 62 | 26.5524 | 631000 | 601650 | 45.5 | 15000 | 3640.3966 |  | 2
85 | 85 | 57 | 14.765 | 584000 | 652700 | 44.6 | 15000 | 3640.3966 |  | 2
85 | 85 | 75 | 63.5688 | 808000 | 413530 | 49.9 | 18000 | 5232.419 |  | 2
85 | 85 | 72 | 54.0993 | 768000 | 479430 | 48.9 | 18000 | 5232.419 |  | 2
85 | 85 | 67 | 39.6049 | 709000 | 573410 | 47.5 | 18000 | 5232.419 |  | 2
85 | 85 | 62 | 26.5524 | 656000 | 666400 | 46.3 | 18000 | 5232.419 |  | 2
85 | 85 | 57 | 14.765 | 619000 | 691540 | 45.3 | 18000 | 5232.419 |  | 2
85 | 85 | 75 | 63.5688 | 831000 | 450715 | 50.5 | 21000 | 7355.8101 |  | 2
85 | 85 | 72 | 54.0993 | 788000 | 513025 | 49.4 | 21000 | 7355.8101 |  | 2
85 | 85 | 67 | 39.6049 | 727000 | 622490 | 48 | 21000 | 7355.8101 |  | 2
85 | 85 | 62 | 26.5524 | 672000 | 723490 | 46.7 | 21000 | 7355.8101 |  | 2
85 | 85 | 57 | 14.765 | 647000 | 722390 | 46 | 21000 | 7355.8101 |  | 2
95 | 95 | 75 | 40.2091 | 725000 | 496000 | 53.5 | 12000 | 2535.9832 |  | 2
95 | 95 | 72 | 33.2947 | 690000 | 520140 | 52.6 | 12000 | 2535.9832 |  | 2
95 | 95 | 67 | 22.7111 | 636000 | 575240 | 51.5 | 12000 | 2535.9832 |  | 2
95 | 95 | 62 | 13.1803 | 584000 | 645180 | 50.6 | 12000 | 2535.9832 |  | 2
95 | 95 | 57 | 4.5734 | 534000 | 696220 | 50.3 | 12000 | 2535.9832 |  | 2
95 | 95 | 75 | 40.2091 | 761000 | 560500 | 54.6 | 15000 | 3640.3966 |  | 2
95 | 95 | 72 | 33.2947 | 724000 | 574375 | 53.7 | 15000 | 3640.3966 |  | 2
95 | 95 | 67 | 22.7111 | 668000 | 660800 | 52.5 | 15000 | 3640.3966 |  | 2
95 | 95 | 62 | 13.1803 | 615000 | 743750 | 51.6 | 15000 | 3640.3966 |  | 2
95 | 95 | 57 | 4.5734 | 571000 | 770475 | 50.7 | 15000 | 3640.3966 |  | 2
95 | 95 | 75 | 40.2091 | 787000 | 567630 | 55.5 | 18000 | 5232.419 |  | 2
95 | 95 | 72 | 33.2947 | 749000 | 637480 | 54.5 | 18000 | 5232.419 |  | 2
95 | 95 | 67 | 22.7111 | 691000 | 739390 | 53.2 | 18000 | 5232.419 |  | 2
95 | 95 | 62 | 13.1803 | 637000 | 832360 | 52.3 | 18000 | 5232.419 |  | 2
95 | 95 | 57 | 4.5734 | 605000 | 818840 | 51.3 | 18000 | 5232.419 |  | 2
95 | 95 | 75 | 40.2091 | 808000 | 634130 | 56.4 | 21000 | 7355.8101 |  | 2
95 | 95 | 72 | 33.2947 | 766000 | 701060 | 55.1 | 21000 | 7355.8101 |  | 2
95 | 95 | 67 | 22.7111 | 707000 | 813990 | 53.7 | 21000 | 7355.8101 |  | 2
95 | 95 | 62 | 13.1803 | 652000 | 907525 | 52.7 | 21000 | 7355.8101 |  | 2
95 | 95 | 57 | 4.5734 | 633000 | 858225 | 52 | 21000 | 7355.8101 |  | 2
105 | 105 | 75 | 25.1345 | 703000 | 620000 | 60.2 | 12000 | 2535.9832 |  | 2
105 | 105 | 72 | 20.0232 | 669000 | 638200 | 59.4 | 12000 | 2535.9832 |  | 2
105 | 105 | 67 | 12.1996 | 614000 | 685700 | 58.7 | 12000 | 2535.9832 |  | 2
105 | 105 | 62 | 5.1542 | 560000 | 761900 | 57.7 | 12000 | 2535.9832 |  | 2
105 | 105 | 57 | -1.2082 | 508000 | 791700 | 59.7 | 12000 | 2535.9832 |  | 2
105 | 105 | 75 | 25.1345 | 736000 | 677250 | 61.6 | 15000 | 3640.3966 |  | 2
105 | 105 | 72 | 20.0232 | 700000 | 709750 | 60.6 | 15000 | 3640.3966 |  | 2
105 | 105 | 67 | 12.1996 | 643000 | 799125 | 59.7 | 15000 | 3640.3966 |  | 2
105 | 105 | 62 | 5.1542 | 588000 | 885375 | 58.5 | 15000 | 3640.3966 |  | 2
105 | 105 | 57 | -1.2082 | 554000 | 879875 | 57 | 15000 | 3640.3966 |  | 2
105 | 105 | 75 | 25.1345 | 760000 | 724950 | 63.1 | 18000 | 5232.419 |  | 2
105 | 105 | 72 | 20.0232 | 721000 | 798750 | 61.7 | 18000 | 5232.419 |  | 2
105 | 105 | 67 | 12.1996 | 664000 | 905600 | 60.4 | 18000 | 5232.419 |  | 2
105 | 105 | 62 | 5.1542 | 610000 | 986650 | 60.2 | 18000 | 5232.419 |  | 2
105 | 105 | 57 | -1.2082 | 584000 | 930500 | 59 | 18000 | 5232.419 |  | 2
105 | 105 | 75 | 25.1345 | 775000 | 818325 | 64.1 | 21000 | 7355.8101 |  | 2
105 | 105 | 72 | 20.0232 | 736000 | 885100 | 62.4 | 21000 | 7355.8101 |  | 2
105 | 105 | 67 | 12.1996 | 679000 | 1001650 | 61 | 21000 | 7355.8101 |  | 2
105 | 105 | 62 | 5.1542 | 624000 | 1083100 | 60.2 | 21000 | 7355.8101 |  | 2
105 | 105 | 57 | -1.2082 | 611000 | 969050 | 59.6 | 21000 | 7355.8101 |  | 2
115 | 115 | 75 | 15.3648 | 675000 | 738000 | 70.1 | 12000 | 2535.9832 |  | 2
115 | 115 | 72 | 11.5424 | 639000 | 708700 | 69.7 | 12000 | 2535.9832 |  | 2
115 | 115 | 67 | 5.6915 | 582000 | 793800 | 69.6 | 12000 | 2535.9832 |  | 2
115 | 115 | 62 | 0.42275 | 527000 | 869660 | 68 | 12000 | 2535.9832 |  | 2
115 | 115 | 57 | -4.3353 | 482000 | 864080 | 71.2 | 12000 | 2273.4246 |  | 2
115 | 115 | 75 | 15.3648 | 706000 | 833075 | 72.8 | 15000 | 3640.3966 |  | 2
115 | 115 | 72 | 11.5424 | 668000 | 845425 | 70.9 | 15000 | 3640.3966 |  | 2
115 | 115 | 67 | 5.6915 | 610000 | 932975 | 70.6 | 15000 | 3640.3966 |  | 2
115 | 115 | 62 | 0.42275 | 554000 | 1012750 | 71.2 | 15000 | 3640.3966 |  | 2
115 | 115 | 57 | -4.3353 | 523000 | 956125 | 70.6 | 15000 | 3640.3966 |  | 2
115 | 115 | 72 | 11.5424 | 688000 | 955050 | 72.6 | 18000 | 5232.419 |  | 2
115 | 115 | 67 | 5.6915 | 630000 | 1065840 | 71.6 | 18000 | 5232.419 |  | 2
115 | 115 | 62 | 0.42275 | 574000 | 1142910 | 71.7 | 18000 | 5232.419 |  | 2
115 | 115 | 57 | -4.3353 | 555000 | 1012380 | 70.8 | 18000 | 5232.419 |  | 2
115 | 115 | 67 | 5.6915 | 644000 | 1186310 | 72.2 | 21000 | 7355.8101 |  | 2
115 | 115 | 62 | 0.42275 | 590000 | 1235970 | 71.6 | 21000 | 7355.8101 |  | 2
115 | 115 | 57 | -4.3353 | 582000 | 1059015 | 71.3 | 21000 | 7355.8101 |  | 2
75 | 75 | 75 | 100 | 868000 | 274040 | 46.4 | 24000 | 10035.5754 |  | 2
75 | 75 | 72 | 86.8609 | 824000 | 340720 | 45.4 | 24000 | 10035.5754 |  | 2
75 | 75 | 67 | 66.7494 | 759000 | 453760 | 43.8 | 24000 | 10035.5754 |  | 2
75 | 75 | 62 | 48.6386 | 700000 | 561720 | 42.3 | 24000 | 10035.5754 |  | 2
75 | 75 | 57 | 32.2833 | 684000 | 604440 | 42 | 24000 | 10035.5754 |  | 2
75 | 75 | 75 | 100 | 882000 | 275280 | 46.7 | 27000 | 13344.648 |  | 2
75 | 75 | 72 | 86.8609 | 836000 | 348795 | 45.7 | 27000 | 13344.648 |  | 2
75 | 75 | 67 | 66.7494 | 770000 | 475825 | 44.1 | 27000 | 13344.648 |  | 2
75 | 75 | 62 | 48.6386 | 714000 | 574250 | 42.7 | 27000 | 13344.648 |  | 2
75 | 75 | 57 | 32.2833 | 705000 | 622920 | 42.5 | 27000 | 13344.648 |  | 2
85 | 85 | 75 | 63.5688 | 847000 | 480280 | 51 | 24000 | 10035.5754 |  | 2
85 | 85 | 72 | 54.0993 | 803000 | 548600 | 49.9 | 24000 | 10035.5754 |  | 2
85 | 85 | 67 | 39.6049 | 741000 | 669240 | 48.3 | 24000 | 10035.5754 |  | 2
85 | 85 | 62 | 26.5524 | 685000 | 757640 | 47 | 24000 | 10035.5754 |  | 2
85 | 85 | 57 | 14.765 | 671000 | 749240 | 46.6 | 24000 | 10035.5754 |  | 2
85 | 85 | 75 | 63.5688 | 861000 | 506205 | 51.5 | 27000 | 13344.648 |  | 2
85 | 85 | 72 | 54.0993 | 814000 | 580690 | 50.2 | 27000 | 13344.648 |  | 2
85 | 85 | 67 | 39.6049 | 752000 | 713175 | 48.7 | 27000 | 13344.648 |  | 2
85 | 85 | 62 | 26.5524 | 698000 | 801265 | 47.3 | 27000 | 13344.648 |  | 2
85 | 85 | 57 | 14.765 | 692000 | 772595 | 47.2 | 27000 | 13344.648 |  | 2
95 | 95 | 75 | 40.2091 | 822000 | 684760 | 57.1 | 24000 | 10035.5754 |  | 2
95 | 95 | 72 | 33.2947 | 780000 | 760680 | 55.6 | 24000 | 10035.5754 |  | 2
95 | 95 | 67 | 22.7111 | 720000 | 886600 | 54.1 | 24000 | 10035.5754 |  | 2
95 | 95 | 62 | 13.1803 | 666000 | 957800 | 52.9 | 24000 | 10035.5754 |  | 2
95 | 95 | 57 | 4.5734 | 656000 | 889640 | 52.5 | 24000 | 10035.5754 |  | 2
95 | 95 | 75 | 40.2091 | 835000 | 733400 | 57.9 | 27000 | 13344.648 |  | 2
95 | 95 | 72 | 33.2947 | 792000 | 818310 | 56.2 | 27000 | 13344.648 |  | 2
95 | 95 | 67 | 22.7111 | 730000 | 951765 | 54.5 | 27000 | 13344.648 |  | 2
95 | 95 | 62 | 13.1803 | 679000 | 993670 | 52.9 | 27000 | 13344.648 |  | 2
95 | 95 | 57 | 4.5734 | 675000 | 915570 | 53.1 | 27000 | 13344.648 |  | 2
105 | 105 | 75 | 25.1345 | 789000 | 894200 | 65.4 | 24000 | 10035.5754 |  | 2
105 | 105 | 72 | 20.0232 | 749000 | 968800 | 63.2 | 24000 | 10035.5754 |  | 2
105 | 105 | 67 | 12.1996 | 690000 | 1099000 | 61.4 | 24000 | 10035.5754 |  | 2
105 | 105 | 62 | 5.1542 | 639000 | 1149400 | 60.4 | 24000 | 10035.5754 |  | 2
105 | 105 | 57 | -1.2082 | 633000 | 1009200 | 60.1 | 24000 | 10035.5754 |  | 2
105 | 105 | 75 | 25.1345 | 798000 | 966425 | 66.8 | 27000 | 13344.648 |  | 2
105 | 105 | 72 | 20.0232 | 757000 | 1058275 | 63.5 | 27000 | 13344.648 |  | 2
105 | 105 | 67 | 12.1996 | 699000 | 1193700 | 61.7 | 27000 | 13344.648 |  | 2
105 | 105 | 62 | 5.1542 | 653000 | 1190025 | 60.5 | 27000 | 13344.648 |  | 2
105 | 105 | 57 | -1.2082 | 652000 | 1038100 | 60.5 | 27000 | 13344.648 |  | 2
115 | 115 | 67 | 5.6915 | 655000 | 1309400 | 72.8 | 24000 | 10035.5754 |  | 2
115 | 115 | 62 | 0.42275 | 606000 | 1301240 | 71 | 24000 | 10035.5754 |  | 2
115 | 115 | 57 | -4.3353 | 603000 | 1101960 | 71.9 | 24000 | 10035.5754 |  | 2
115 | 115 | 67 | 5.6915 | 663000 | 1429180 | 72.8 | 27000 | 13344.648 |  | 2
115 | 115 | 62 | 0.42275 | 622000 | 1360045 | 72.1 | 27000 | 13344.648 |  | 2
115 | 115 | 57 | -4.3353 | 622000 | 1131355 | 72 | 27000 | 13344.648 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 7
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 75 | 75 | 100 | 843000 | 296700 | 46.7 | 14000 | 3217.3855 |  | 1
75 | 75 | 72 | 86.8609 | 802000 | 330190 | 45.7 | 14000 | 3217.3855 |  | 1
75 | 75 | 67 | 66.7494 | 744000 | 405304 | 44.2 | 14000 | 3217.3855 |  | 1
75 | 75 | 62 | 48.6386 | 685000 | 486392 | 42.9 | 14000 | 3217.3855 |  | 1
75 | 75 | 57 | 32.2833 | 629000 | 536030 | 41.9 | 14000 | 3217.3855 |  | 1
75 | 75 | 75 | 100 | 880000 | 302625 | 47.7 | 17500 | 4936.5196 |  | 1
75 | 75 | 72 | 86.8609 | 839000 | 340925 | 46.6 | 17500 | 4936.5196 |  | 1
75 | 75 | 67 | 66.7494 | 779000 | 434075 | 45 | 17500 | 4936.5196 |  | 1
75 | 75 | 62 | 48.6386 | 720000 | 533185 | 43.7 | 17500 | 4936.5196 |  | 1
75 | 75 | 57 | 32.2833 | 675000 | 586700 | 42.7 | 17500 | 4936.5196 |  | 1
75 | 75 | 75 | 100 | 905000 | 293595 | 48.4 | 21000 | 7355.8101 |  | 1
75 | 75 | 72 | 86.8609 | 863000 | 352200 | 47.3 | 21000 | 7355.8101 |  | 1
75 | 75 | 67 | 66.7494 | 803000 | 462045 | 45.6 | 21000 | 7355.8101 |  | 1
75 | 75 | 62 | 48.6386 | 744000 | 568890 | 44.3 | 21000 | 7355.8101 |  | 1
75 | 75 | 57 | 32.2833 | 710000 | 626525 | 43.5 | 21000 | 7355.8101 |  | 1
75 | 75 | 75 | 100 | 924000 | 291137.5 | 48.9 | 24500 | 10546.1061 |  | 1
75 | 75 | 72 | 86.8609 | 882000 | 362747.5 | 47.7 | 24500 | 10546.1061 |  | 1
75 | 75 | 67 | 66.7494 | 820000 | 488400 | 46.1 | 24500 | 10546.1061 |  | 1
75 | 75 | 62 | 48.6386 | 761000 | 605747.5 | 44.7 | 24500 | 10546.1061 |  | 1
75 | 75 | 57 | 32.2833 | 741000 | 654392.5 | 44.2 | 24500 | 10546.1061 |  | 1
85 | 85 | 75 | 63.5688 | 822000 | 382300 | 51.3 | 14000 | 3217.3855 |  | 1
85 | 85 | 72 | 54.0993 | 783000 | 447350 | 50.2 | 14000 | 3217.3855 |  | 1
85 | 85 | 67 | 39.6049 | 726000 | 530696 | 48.9 | 14000 | 3217.3855 |  | 1
85 | 85 | 62 | 26.5524 | 667000 | 602608 | 47.7 | 14000 | 3217.3855 |  | 1
85 | 85 | 57 | 14.765 | 612000 | 666970 | 46.8 | 14000 | 3217.3855 |  | 1
85 | 85 | 75 | 63.5688 | 857000 | 416375 | 52.2 | 17500 | 4936.5196 |  | 1
85 | 85 | 72 | 54.0993 | 819000 | 499037.5 | 51.2 | 17500 | 4936.5196 |  | 1
85 | 85 | 67 | 39.6049 | 759000 | 596925 | 49.7 | 17500 | 4936.5196 |  | 1
85 | 85 | 62 | 26.5524 | 700000 | 684815 | 48.5 | 17500 | 4936.5196 |  | 1
85 | 85 | 57 | 14.765 | 655000 | 731300 | 47.6 | 17500 | 4936.5196 |  | 1
85 | 85 | 75 | 63.5688 | 880000 | 468715 | 52.9 | 21000 | 7355.8101 |  | 1
85 | 85 | 72 | 54.0993 | 839000 | 544800 | 51.8 | 21000 | 7355.8101 |  | 1
85 | 85 | 67 | 39.6049 | 782000 | 656955 | 50.3 | 21000 | 7355.8101 |  | 1
85 | 85 | 62 | 26.5524 | 722000 | 761955 | 49.1 | 21000 | 7355.8101 |  | 1
85 | 85 | 57 | 14.765 | 694000 | 775165 | 48.3 | 21000 | 7355.8101 |  | 1
85 | 85 | 75 | 63.5688 | 900000 | 506210 | 53.4 | 24500 | 10546.1061 |  | 1
85 | 85 | 72 | 54.0993 | 860000 | 587252.5 | 52.3 | 24500 | 10546.1061 |  | 1
85 | 85 | 67 | 39.6049 | 798000 | 714600 | 50.8 | 24500 | 10546.1061 |  | 1
85 | 85 | 62 | 26.5524 | 739000 | 823905 | 49.5 | 24500 | 10546.1061 |  | 1
85 | 85 | 57 | 14.765 | 724000 | 809260 | 49 | 24500 | 10546.1061 |  | 1
95 | 95 | 75 | 40.2091 | 799000 | 557000 | 56.7 | 14000 | 3217.3855 |  | 1
95 | 95 | 72 | 33.2947 | 763000 | 572350 | 55.8 | 14000 | 3217.3855 |  | 1
95 | 95 | 67 | 22.7111 | 703000 | 664210 | 54.6 | 14000 | 3217.3855 |  | 1
95 | 95 | 62 | 13.1803 | 645000 | 748140 | 53.2 | 14000 | 3217.3855 |  | 1
95 | 95 | 57 | 4.5734 | 588000 | 789590 | 52.7 | 14000 | 3217.3855 |  | 1
95 | 95 | 75 | 40.2091 | 830000 | 557787.5 | 57.6 | 17500 | 4936.5196 |  | 1
95 | 95 | 72 | 33.2947 | 791000 | 662987.5 | 56.5 | 17500 | 4936.5196 |  | 1
95 | 95 | 67 | 22.7111 | 734000 | 763762.5 | 55.4 | 17500 | 4936.5196 |  | 1
95 | 95 | 62 | 13.1803 | 674000 | 856650 | 54.3 | 17500 | 4936.5196 |  | 1
95 | 95 | 57 | 4.5734 | 635000 | 860225 | 53.4 | 17500 | 4936.5196 |  | 1
95 | 95 | 75 | 40.2091 | 854000 | 654595 | 58.3 | 21000 | 7355.8101 |  | 1
95 | 95 | 72 | 33.2947 | 816000 | 739920 | 57.4 | 21000 | 7355.8101 |  | 1
95 | 95 | 67 | 22.7111 | 755000 | 856850 | 55.9 | 21000 | 7355.8101 |  | 1
95 | 95 | 62 | 13.1803 | 695000 | 955385 | 54.8 | 21000 | 7355.8101 |  | 1
95 | 95 | 57 | 4.5734 | 673000 | 912085 | 54.1 | 21000 | 7355.8101 |  | 1
95 | 95 | 75 | 40.2091 | 871000 | 724570 | 58.9 | 24500 | 10546.1061 |  | 1
95 | 95 | 72 | 33.2947 | 832000 | 812697.5 | 57.9 | 24500 | 10546.1061 |  | 1
95 | 95 | 67 | 22.7111 | 771000 | 941740 | 56.4 | 24500 | 10546.1061 |  | 1
95 | 95 | 62 | 13.1803 | 711000 | 1031612.5 | 55.1 | 24500 | 10546.1061 |  | 1
95 | 95 | 57 | 4.5734 | 702000 | 952635 | 54.8 | 24500 | 10546.1061 |  | 1
105 | 105 | 75 | 25.1345 | 771000 | 698000 | 63.1 | 14000 | 3217.3855 |  | 1
105 | 105 | 72 | 20.0232 | 734000 | 699950 | 62.3 | 14000 | 3217.3855 |  | 1
105 | 105 | 67 | 12.1996 | 674000 | 800050 | 61.1 | 14000 | 3217.3855 |  | 1
105 | 105 | 62 | 5.1542 | 618000 | 878900 | 60.4 | 14000 | 3217.3855 |  | 1
105 | 105 | 57 | -1.2082 | 569000 | 888250 | 60.1 | 14000 | 3217.3855 |  | 1
105 | 105 | 75 | 25.1345 | 799000 | 722000 | 64 | 17500 | 4936.5196 |  | 1
105 | 105 | 72 | 20.0232 | 764000 | 823312.5 | 63.2 | 17500 | 4936.5196 |  | 1
105 | 105 | 67 | 12.1996 | 703000 | 925937.5 | 62 | 17500 | 4936.5196 |  | 1
105 | 105 | 62 | 5.1542 | 644000 | 1019750 | 61.8 | 17500 | 4936.5196 |  | 1
105 | 105 | 57 | -1.2082 | 612000 | 972937.5 | 61.1 | 17500 | 4936.5196 |  | 1
105 | 105 | 75 | 25.1345 | 821000 | 846875 | 64.8 | 21000 | 7355.8101 |  | 1
105 | 105 | 72 | 20.0232 | 784000 | 937975 | 63.8 | 21000 | 7355.8101 |  | 1
105 | 105 | 67 | 12.1996 | 722000 | 1050750 | 62.5 | 21000 | 7355.8101 |  | 1
105 | 105 | 62 | 5.1542 | 664000 | 1144975 | 62 | 21000 | 7355.8101 |  | 1
105 | 105 | 57 | -1.2082 | 648000 | 1029150 | 61.4 | 21000 | 7355.8101 |  | 1
105 | 105 | 75 | 25.1345 | 836000 | 946687.5 | 65.3 | 24500 | 10546.1061 |  | 1
105 | 105 | 72 | 20.0232 | 798000 | 1035162.5 | 64.4 | 24500 | 10546.1061 |  | 1
105 | 105 | 67 | 12.1996 | 737000 | 1172637.5 | 62.9 | 24500 | 10546.1061 |  | 1
105 | 105 | 62 | 5.1542 | 679000 | 1237950 | 62 | 24500 | 10546.1061 |  | 1
105 | 105 | 57 | -1.2082 | 676000 | 1073512.5 | 61.8 | 24500 | 10546.1061 |  | 1
115 | 115 | 75 | 15.3648 | 736000 | 843000 | 70.7 | 14000 | 3217.3855 |  | 1
115 | 115 | 72 | 11.5424 | 699000 | 838100 | 69.4 | 14000 | 3217.3855 |  | 1
115 | 115 | 67 | 5.6915 | 642000 | 922880 | 70.3 | 14000 | 3217.3855 |  | 1
115 | 115 | 62 | 0.42275 | 587000 | 1015050 | 69.2 | 14000 | 3217.3855 |  | 1
115 | 115 | 57 | -4.3353 | 541000 | 988370 | 71 | 14000 | 3217.3855 |  | 1
115 | 115 | 75 | 15.3648 | 763000 | 890950 | 71.7 | 17500 | 4936.5196 |  | 1
115 | 115 | 72 | 11.5424 | 728000 | 989375 | 71.3 | 17500 | 4936.5196 |  | 1
115 | 115 | 67 | 5.6915 | 669000 | 1087112.5 | 70.8 | 17500 | 4936.5196 |  | 1
115 | 115 | 62 | 0.42275 | 610000 | 1173112.5 | 71.4 | 17500 | 4936.5196 |  | 1
115 | 115 | 57 | -4.3353 | 587000 | 1072100 | 70.3 | 17500 | 4936.5196 |  | 1
115 | 115 | 75 | 15.3648 | 782000 | 1039310 | 72.5 | 21000 | 7355.8101 |  | 1
115 | 115 | 72 | 11.5424 | 747000 | 1130565 | 72.1 | 21000 | 7355.8101 |  | 1
115 | 115 | 67 | 5.6915 | 687000 | 1244650 | 71.4 | 21000 | 7355.8101 |  | 1
115 | 115 | 62 | 0.42275 | 629000 | 1297310 | 71.1 | 21000 | 7355.8101 |  | 1
115 | 115 | 57 | -4.3353 | 620000 | 1129355 | 71 | 21000 | 7355.8101 |  | 1
115 | 115 | 75 | 15.3648 | 796000 | 1172195 | 73 | 24500 | 10546.1061 |  | 1
115 | 115 | 72 | 11.5424 | 760000 | 1255627.5 | 72.4 | 24500 | 10546.1061 |  | 1
115 | 115 | 67 | 5.6915 | 700000 | 1398492.5 | 71.7 | 24500 | 10546.1061 |  | 1
115 | 115 | 62 | 0.42275 | 650000 | 1395600 | 70.8 | 24500 | 10546.1061 |  | 1
115 | 115 | 57 | -4.3353 | 646000 | 1183652.5 | 71.1 | 24500 | 10546.1061 |  | 1
75 | 75 | 75 | 100 | 938000 | 292300 | 49.3 | 28000 | 14599.095 |  | 1
75 | 75 | 72 | 86.8609 | 897000 | 374220 | 48.1 | 28000 | 14599.095 |  | 1
75 | 75 | 67 | 66.7494 | 834000 | 513140 | 46.4 | 28000 | 14599.095 |  | 1
75 | 75 | 62 | 48.6386 | 774000 | 632840 | 45 | 28000 | 14599.095 |  | 1
75 | 75 | 57 | 32.2833 | 767000 | 677260 | 44.8 | 28000 | 14599.095 |  | 1
75 | 75 | 75 | 100 | 945000 | 292250 | 49.5 | 30000 | 17351.7933 |  | 1
75 | 75 | 72 | 86.8609 | 903000 | 378950 | 48.3 | 30000 | 17351.7933 |  | 1
75 | 75 | 67 | 66.7494 | 840000 | 527300 | 46.6 | 30000 | 17351.7933 |  | 1
75 | 75 | 62 | 48.6386 | 782000 | 646850 | 45.1 | 30000 | 17351.7933 |  | 1
75 | 75 | 57 | 32.2833 | 779000 | 687800 | 45.1 | 30000 | 17351.7933 |  | 1
85 | 85 | 75 | 63.5688 | 913000 | 539240 | 53.8 | 28000 | 14599.095 |  | 1
85 | 85 | 72 | 54.0993 | 874000 | 627320 | 52.8 | 28000 | 14599.095 |  | 1
85 | 85 | 67 | 39.6049 | 811000 | 769860 | 51.1 | 28000 | 14599.095 |  | 1
85 | 85 | 62 | 26.5524 | 751000 | 870160 | 49.7 | 28000 | 14599.095 |  | 1
85 | 85 | 57 | 14.765 | 749000 | 835660 | 49.6 | 28000 | 14599.095 |  | 1
85 | 85 | 75 | 63.5688 | 919000 | 557400 | 54 | 30000 | 17351.7933 |  | 1
85 | 85 | 72 | 54.0993 | 880000 | 649050 | 52.9 | 30000 | 17351.7933 |  | 1
85 | 85 | 67 | 39.6049 | 816000 | 799700 | 51.3 | 30000 | 17351.7933 |  | 1
85 | 85 | 62 | 26.5524 | 763000 | 881850 | 50 | 30000 | 17351.7933 |  | 1
85 | 85 | 57 | 14.765 | 761000 | 850550 | 49.9 | 30000 | 17351.7933 |  | 1
95 | 95 | 75 | 40.2091 | 883000 | 789080 | 59.3 | 28000 | 14599.095 |  | 1
95 | 95 | 72 | 33.2947 | 845000 | 883320 | 58.3 | 28000 | 14599.095 |  | 1
95 | 95 | 67 | 22.7111 | 782000 | 1027940 | 56.7 | 28000 | 14599.095 |  | 1
95 | 95 | 62 | 13.1803 | 728000 | 1087980 | 55.4 | 28000 | 14599.095 |  | 1
95 | 95 | 57 | 4.5734 | 726000 | 984720 | 55.4 | 28000 | 14599.095 |  | 1
95 | 95 | 75 | 40.2091 | 889000 | 826800 | 59.5 | 30000 | 17351.7933 |  | 1
95 | 95 | 72 | 33.2947 | 850000 | 920750 | 58.4 | 30000 | 17351.7933 |  | 1
95 | 95 | 67 | 22.7111 | 788000 | 1073700 | 56.9 | 30000 | 17351.7933 |  | 1
95 | 95 | 62 | 13.1803 | 741000 | 1088350 | 55.7 | 30000 | 17351.7933 |  | 1
95 | 95 | 57 | 4.5734 | 738000 | 1000350 | 55.7 | 30000 | 17351.7933 |  | 1
105 | 105 | 75 | 25.1345 | 847000 | 1044500 | 65.7 | 28000 | 14599.095 |  | 1
105 | 105 | 72 | 20.0232 | 809000 | 1136200 | 64.7 | 28000 | 14599.095 |  | 1
105 | 105 | 67 | 12.1996 | 747000 | 1292600 | 63.1 | 28000 | 14599.095 |  | 1
105 | 105 | 62 | 5.1542 | 701000 | 1277200 | 62.1 | 28000 | 14599.095 |  | 1
105 | 105 | 57 | -1.2082 | 698000 | 1113800 | 62.2 | 28000 | 14599.095 |  | 1
105 | 105 | 75 | 25.1345 | 853000 | 1101250 | 65.9 | 30000 | 17351.7933 |  | 1
105 | 105 | 72 | 20.0232 | 815000 | 1197500 | 64.9 | 30000 | 17351.7933 |  | 1
105 | 105 | 67 | 12.1996 | 753000 | 1344500 | 63.4 | 30000 | 17351.7933 |  | 1
105 | 105 | 62 | 5.1542 | 710000 | 1312250 | 62.4 | 30000 | 17351.7933 |  | 1
105 | 105 | 57 | -1.2082 | 710000 | 1130750 | 62.4 | 30000 | 17351.7933 |  | 1
115 | 115 | 75 | 15.3648 | 806000 | 1305080 | 73.5 | 28000 | 14599.095 |  | 1
115 | 115 | 72 | 11.5424 | 770000 | 1387080 | 72.8 | 28000 | 14599.095 |  | 1
115 | 115 | 67 | 5.6915 | 710000 | 1535860 | 71.9 | 28000 | 14599.095 |  | 1
115 | 115 | 62 | 0.42275 | 673000 | 1420380 | 71.1 | 28000 | 14599.095 |  | 1
115 | 115 | 57 | -4.3353 | 668000 | 1217780 | 71.2 | 28000 | 14599.095 |  | 1
115 | 115 | 75 | 15.3648 | 811000 | 1368750 | 73.7 | 30000 | 17351.7933 |  | 1
115 | 115 | 72 | 11.5424 | 774000 | 1467300 | 72.9 | 30000 | 17351.7933 |  | 1
115 | 115 | 67 | 5.6915 | 714000 | 1612300 | 72.2 | 30000 | 17351.7933 |  | 1
115 | 115 | 62 | 0.42275 | 680000 | 1488500 | 71.3 | 30000 | 17351.7933 |  | 1
115 | 115 | 57 | -4.3353 | 679000 | 1244950 | 71.4 | 30000 | 17351.7933 |  | 1
75 | 75 | 75 | 100 | 863000 | 304700 | 47.8 | 14000 | 3217.3855 |  | 2
75 | 75 | 72 | 86.8609 | 814000 | 345480 | 46.6 | 14000 | 3217.3855 |  | 2
75 | 75 | 67 | 66.7494 | 754000 | 430568 | 44.8 | 14000 | 3217.3855 |  | 2
75 | 75 | 62 | 48.6386 | 690000 | 512656 | 43.2 | 14000 | 3217.3855 |  | 2
75 | 75 | 57 | 32.2833 | 636000 | 571480 | 42 | 14000 | 3217.3855 |  | 2
75 | 75 | 75 | 100 | 905000 | 296000 | 48.8 | 17500 | 4936.5196 |  | 2
75 | 75 | 72 | 86.8609 | 862000 | 367850 | 47.6 | 17500 | 4936.5196 |  | 2
75 | 75 | 67 | 66.7494 | 793000 | 470960 | 45.7 | 17500 | 4936.5196 |  | 2
75 | 75 | 62 | 48.6386 | 728000 | 569515 | 44.1 | 17500 | 4936.5196 |  | 2
75 | 75 | 57 | 32.2833 | 686000 | 605850 | 43.1 | 17500 | 4936.5196 |  | 2
75 | 75 | 75 | 100 | 934000 | 306022 | 49.6 | 21000 | 7355.8101 |  | 2
75 | 75 | 72 | 86.8609 | 889000 | 385220 | 48.3 | 21000 | 7355.8101 |  | 2
75 | 75 | 67 | 66.7494 | 820000 | 504286 | 46.4 | 21000 | 7355.8101 |  | 2
75 | 75 | 62 | 48.6386 | 753000 | 615286 | 44.7 | 21000 | 7355.8101 |  | 2
75 | 75 | 57 | 32.2833 | 729000 | 643215 | 44.2 | 21000 | 7355.8101 |  | 2
75 | 75 | 75 | 100 | 956000 | 313436 | 50.2 | 24500 | 10546.1061 |  | 2
75 | 75 | 72 | 86.8609 | 911000 | 401590 | 48.9 | 24500 | 10546.1061 |  | 2
75 | 75 | 67 | 66.7494 | 839000 | 540167 | 46.9 | 24500 | 10546.1061 |  | 2
75 | 75 | 62 | 48.6386 | 771000 | 651013 | 45.3 | 24500 | 10546.1061 |  | 2
75 | 75 | 57 | 32.2833 | 764000 | 674697.5 | 45.1 | 24500 | 10546.1061 |  | 2
85 | 85 | 75 | 63.5688 | 838000 | 393300 | 52.1 | 14000 | 3217.3855 |  | 2
85 | 85 | 72 | 54.0993 | 797000 | 456564 | 50.9 | 14000 | 3217.3855 |  | 2
85 | 85 | 67 | 39.6049 | 729000 | 527388 | 49.1 | 14000 | 3217.3855 |  | 2
85 | 85 | 62 | 26.5524 | 678000 | 608388 | 47.7 | 14000 | 3217.3855 |  | 2
85 | 85 | 57 | 14.765 | 623000 | 679520 | 46.4 | 14000 | 3217.3855 |  | 2
85 | 85 | 75 | 63.5688 | 876000 | 455925 | 53.2 | 17500 | 4936.5196 |  | 2
85 | 85 | 72 | 54.0993 | 834000 | 503150 | 51.9 | 17500 | 4936.5196 |  | 2
85 | 85 | 67 | 39.6049 | 772000 | 598040 | 50.1 | 17500 | 4936.5196 |  | 2
85 | 85 | 62 | 26.5524 | 715000 | 696040 | 48.7 | 17500 | 4936.5196 |  | 2
85 | 85 | 57 | 14.765 | 673000 | 752187.5 | 47.7 | 17500 | 4936.5196 |  | 2
85 | 85 | 75 | 63.5688 | 903000 | 485912 | 53.9 | 21000 | 7355.8101 |  | 2
85 | 85 | 72 | 54.0993 | 861000 | 550780 | 52.7 | 21000 | 7355.8101 |  | 2
85 | 85 | 67 | 39.6049 | 798000 | 662648 | 50.9 | 21000 | 7355.8101 |  | 2
85 | 85 | 62 | 26.5524 | 734000 | 776714 | 49.2 | 21000 | 7355.8101 |  | 2
85 | 85 | 57 | 14.765 | 714000 | 797475 | 48.7 | 21000 | 7355.8101 |  | 2
85 | 85 | 75 | 63.5688 | 926000 | 522564 | 54.5 | 24500 | 10546.1061 |  | 2
85 | 85 | 72 | 54.0993 | 882000 | 596410 | 53.3 | 24500 | 10546.1061 |  | 2
85 | 85 | 67 | 39.6049 | 817000 | 728833 | 51.4 | 24500 | 10546.1061 |  | 2
85 | 85 | 62 | 26.5524 | 753000 | 855141 | 49.7 | 24500 | 10546.1061 |  | 2
85 | 85 | 57 | 14.765 | 746000 | 832607.5 | 49.6 | 24500 | 10546.1061 |  | 2
95 | 95 | 75 | 40.2091 | 814000 | 568000 | 57.3 | 14000 | 3217.3855 |  | 2
95 | 95 | 72 | 33.2947 | 777000 | 607450 | 56.2 | 14000 | 3217.3855 |  | 2
95 | 95 | 67 | 22.7111 | 711000 | 693380 | 54.4 | 14000 | 3217.3855 |  | 2
95 | 95 | 62 | 13.1803 | 662000 | 774380 | 53.2 | 14000 | 3217.3855 |  | 2
95 | 95 | 57 | 4.5734 | 611000 | 822830 | 51.9 | 14000 | 3217.3855 |  | 2
95 | 95 | 75 | 40.2091 | 853000 | 627650 | 58.4 | 17500 | 4936.5196 |  | 2
95 | 95 | 72 | 33.2947 | 813000 | 696312.5 | 57.3 | 17500 | 4936.5196 |  | 2
95 | 95 | 67 | 22.7111 | 753000 | 802087.5 | 55.6 | 17500 | 4936.5196 |  | 2
95 | 95 | 62 | 13.1803 | 693000 | 900975 | 54.1 | 17500 | 4936.5196 |  | 2
95 | 95 | 57 | 4.5734 | 660000 | 893887.5 | 53.1 | 17500 | 4936.5196 |  | 2
95 | 95 | 75 | 40.2091 | 879000 | 709710 | 59.3 | 21000 | 7355.8101 |  | 2
95 | 95 | 72 | 33.2947 | 841000 | 784175 | 58.1 | 21000 | 7355.8101 |  | 2
95 | 95 | 67 | 22.7111 | 777000 | 908105 | 56.3 | 21000 | 7355.8101 |  | 2
95 | 95 | 62 | 13.1803 | 718000 | 1015640 | 54.8 | 21000 | 7355.8101 |  | 2
95 | 95 | 57 | 4.5734 | 699000 | 945015 | 54.2 | 21000 | 7355.8101 |  | 2
95 | 95 | 75 | 40.2091 | 902000 | 780952.5 | 60 | 24500 | 10546.1061 |  | 2
95 | 95 | 72 | 33.2947 | 860000 | 870037.5 | 58.7 | 24500 | 10546.1061 |  | 2
95 | 95 | 67 | 22.7111 | 795000 | 1009080 | 56.9 | 24500 | 10546.1061 |  | 2
95 | 95 | 62 | 13.1803 | 734000 | 1097867.5 | 55.2 | 24500 | 10546.1061 |  | 2
95 | 95 | 57 | 4.5734 | 730000 | 988720 | 55.1 | 24500 | 10546.1061 |  | 2
105 | 105 | 75 | 25.1345 | 791000 | 715000 | 63.6 | 14000 | 3217.3855 |  | 2
105 | 105 | 72 | 20.0232 | 755000 | 744750 | 62.6 | 14000 | 3217.3855 |  | 2
105 | 105 | 67 | 12.1996 | 691000 | 835300 | 60.7 | 14000 | 3217.3855 |  | 2
105 | 105 | 62 | 5.1542 | 640000 | 914300 | 59.9 | 14000 | 3217.3855 |  | 2
105 | 105 | 57 | -1.2082 | 593000 | 943350 | 58.6 | 14000 | 3217.3855 |  | 2
105 | 105 | 75 | 25.1345 | 828000 | 801562.5 | 64.9 | 17500 | 4936.5196 |  | 2
105 | 105 | 72 | 20.0232 | 788000 | 875000 | 63.7 | 17500 | 4936.5196 |  | 2
105 | 105 | 67 | 12.1996 | 728000 | 978812.5 | 62.1 | 17500 | 4936.5196 |  | 2
105 | 105 | 62 | 5.1542 | 667000 | 1078625 | 60.4 | 17500 | 4936.5196 |  | 2
105 | 105 | 57 | -1.2082 | 642000 | 1022187.5 | 59.8 | 17500 | 4936.5196 |  | 2
105 | 105 | 75 | 25.1345 | 852000 | 917850 | 65.8 | 21000 | 7355.8101 |  | 2
105 | 105 | 72 | 20.0232 | 813000 | 999400 | 64.7 | 21000 | 7355.8101 |  | 2
105 | 105 | 67 | 12.1996 | 750000 | 1121175 | 63 | 21000 | 7355.8101 |  | 2
105 | 105 | 62 | 5.1542 | 691000 | 1216625 | 61.3 | 21000 | 7355.8101 |  | 2
105 | 105 | 57 | -1.2082 | 680000 | 1078475 | 60.8 | 21000 | 7355.8101 |  | 2
105 | 105 | 75 | 25.1345 | 871000 | 1028325 | 66.6 | 24500 | 10546.1061 |  | 2
105 | 105 | 72 | 20.0232 | 831000 | 1116062.5 | 65.4 | 24500 | 10546.1061 |  | 2
105 | 105 | 67 | 12.1996 | 766000 | 1256800 | 63.5 | 24500 | 10546.1061 |  | 2
105 | 105 | 62 | 5.1542 | 711000 | 1288162.5 | 61.6 | 24500 | 10546.1061 |  | 2
105 | 105 | 57 | -1.2082 | 709000 | 1126725 | 61.6 | 24500 | 10546.1061 |  | 2
115 | 115 | 75 | 15.3648 | 761000 | 793320 | 71.2 | 14000 | 3217.3855 |  | 2
115 | 115 | 72 | 11.5424 | 725000 | 884440 | 70.3 | 14000 | 3217.3855 |  | 2
115 | 115 | 67 | 5.6915 | 664000 | 974220 | 68.2 | 14000 | 3217.3855 |  | 2
115 | 115 | 62 | 0.42275 | 611000 | 1051220 | 69.1 | 14000 | 3217.3855 |  | 2
115 | 115 | 57 | -4.3353 | 571000 | 1039930 | 67.5 | 14000 | 3217.3855 |  | 2
115 | 115 | 75 | 15.3648 | 794000 | 974325 | 72.7 | 17500 | 4936.5196 |  | 2
115 | 115 | 72 | 11.5424 | 758000 | 1047800 | 71.9 | 17500 | 4936.5196 |  | 2
115 | 115 | 67 | 5.6915 | 697000 | 1151537.5 | 70.5 | 17500 | 4936.5196 |  | 2
115 | 115 | 62 | 0.42275 | 639000 | 1244537.5 | 69.9 | 17500 | 4936.5196 |  | 2
115 | 115 | 57 | -4.3353 | 618000 | 1130050 | 68.5 | 17500 | 4936.5196 |  | 2
115 | 115 | 75 | 15.3648 | 817000 | 1122990 | 73.9 | 21000 | 7355.8101 |  | 2
115 | 115 | 72 | 11.5424 | 779000 | 1209160 | 73 | 21000 | 7355.8101 |  | 2
115 | 115 | 67 | 5.6915 | 717000 | 1332245 | 71.5 | 21000 | 7355.8101 |  | 2
115 | 115 | 62 | 0.42275 | 659000 | 1397905 | 69.6 | 21000 | 7355.8101 |  | 2
115 | 115 | 57 | -4.3353 | 654000 | 1195695 | 69.2 | 21000 | 7355.8101 |  | 2
115 | 115 | 75 | 15.3648 | 834000 | 1268655 | 75 | 24500 | 10546.1061 |  | 2
115 | 115 | 72 | 11.5424 | 795000 | 1359087.5 | 73.8 | 24500 | 10546.1061 |  | 2
115 | 115 | 67 | 5.6915 | 731000 | 1500520 | 72 | 24500 | 10546.1061 |  | 2
115 | 115 | 62 | 0.42275 | 682000 | 1493195 | 69.2 | 24500 | 10546.1061 |  | 2
115 | 115 | 57 | -4.3353 | 682000 | 1247950 | 70 | 24500 | 10546.1061 |  | 2
75 | 75 | 75 | 100 | 973000 | 316784 | 50.6 | 28000 | 14599.095 |  | 2
75 | 75 | 72 | 86.8609 | 926000 | 412872 | 49.3 | 28000 | 14599.095 |  | 2
75 | 75 | 67 | 66.7494 | 853000 | 567960 | 47.4 | 28000 | 14599.095 |  | 2
75 | 75 | 62 | 48.6386 | 795000 | 655680 | 45.9 | 28000 | 14599.095 |  | 2
75 | 75 | 57 | 32.2833 | 792000 | 699180 | 45.9 | 28000 | 14599.095 |  | 2
75 | 75 | 75 | 100 | 980000 | 318840 | 50.8 | 30000 | 17351.7933 |  | 2
75 | 75 | 72 | 86.8609 | 934000 | 421220 | 49.5 | 30000 | 17351.7933 |  | 2
75 | 75 | 67 | 66.7494 | 860000 | 585600 | 47.5 | 30000 | 17351.7933 |  | 2
75 | 75 | 62 | 48.6386 | 809000 | 667900 | 46.3 | 30000 | 17351.7933 |  | 2
75 | 75 | 57 | 32.2833 | 806000 | 711500 | 46.2 | 30000 | 17351.7933 |  | 2
85 | 85 | 75 | 63.5688 | 942000 | 557216 | 55 | 28000 | 14599.095 |  | 2
85 | 85 | 72 | 54.0993 | 898000 | 641040 | 53.7 | 28000 | 14599.095 |  | 2
85 | 85 | 67 | 39.6049 | 830000 | 793040 | 51.8 | 28000 | 14599.095 |  | 2
85 | 85 | 62 | 26.5524 | 773000 | 897240 | 50.4 | 28000 | 14599.095 |  | 2
85 | 85 | 57 | 14.765 | 772000 | 861740 | 50.3 | 28000 | 14599.095 |  | 2
85 | 85 | 75 | 63.5688 | 950000 | 577160 | 55.2 | 30000 | 17351.7933 |  | 2
85 | 85 | 72 | 54.0993 | 905000 | 670780 | 54 | 30000 | 17351.7933 |  | 2
85 | 85 | 67 | 39.6049 | 839000 | 826400 | 52 | 30000 | 17351.7933 |  | 2
85 | 85 | 62 | 26.5524 | 783000 | 913800 | 50.7 | 30000 | 17351.7933 |  | 2
85 | 85 | 57 | 14.765 | 785000 | 876200 | 50.7 | 30000 | 17351.7933 |  | 2
95 | 95 | 75 | 40.2091 | 918000 | 853660 | 60.5 | 28000 | 14599.095 |  | 2
95 | 95 | 72 | 33.2947 | 874000 | 954900 | 59.2 | 28000 | 14599.095 |  | 2
95 | 95 | 67 | 22.7111 | 808000 | 1105900 | 57.3 | 28000 | 14599.095 |  | 2
95 | 95 | 62 | 13.1803 | 753000 | 1136460 | 55.7 | 28000 | 14599.095 |  | 2
95 | 95 | 57 | 4.5734 | 756000 | 1023960 | 55.8 | 28000 | 14599.095 |  | 2
95 | 95 | 75 | 40.2091 | 924000 | 895350 | 60.7 | 30000 | 17351.7933 |  | 2
95 | 95 | 72 | 33.2947 | 881000 | 997300 | 59.5 | 30000 | 17351.7933 |  | 2
95 | 95 | 67 | 22.7111 | 815000 | 1162250 | 57.6 | 30000 | 17351.7933 |  | 2
95 | 95 | 62 | 13.1803 | 766000 | 1157050 | 56.1 | 30000 | 17351.7933 |  | 2
95 | 95 | 57 | 4.5734 | 768000 | 1040250 | 56.2 | 30000 | 17351.7933 |  | 2
105 | 105 | 75 | 25.1345 | 885000 | 1130100 | 67.1 | 28000 | 14599.095 |  | 2
105 | 105 | 72 | 20.0232 | 843000 | 1236500 | 65.9 | 28000 | 14599.095 |  | 2
105 | 105 | 67 | 12.1996 | 779000 | 1385500 | 64 | 28000 | 14599.095 |  | 2
105 | 105 | 62 | 5.1542 | 732000 | 1348000 | 62.2 | 28000 | 14599.095 |  | 2
105 | 105 | 57 | -1.2082 | 734000 | 1165200 | 62.4 | 28000 | 14599.095 |  | 2
105 | 105 | 75 | 25.1345 | 891000 | 1191250 | 67.4 | 30000 | 17351.7933 |  | 2
105 | 105 | 72 | 20.0232 | 850000 | 1297500 | 66.1 | 30000 | 17351.7933 |  | 2
105 | 105 | 67 | 12.1996 | 784000 | 1454500 | 64.2 | 30000 | 17351.7933 |  | 2
105 | 105 | 62 | 5.1542 | 746000 | 1381250 | 62.8 | 30000 | 17351.7933 |  | 2
105 | 105 | 57 | -1.2082 | 746000 | 1183250 | 62.8 | 30000 | 17351.7933 |  | 2
115 | 115 | 75 | 15.3648 | 847000 | 1414320 | 75.8 | 28000 | 14599.095 |  | 2
115 | 115 | 72 | 11.5424 | 806000 | 1516100 | 74.5 | 28000 | 14599.095 |  | 2
115 | 115 | 67 | 5.6915 | 742000 | 1664100 | 72.8 | 28000 | 14599.095 |  | 2
115 | 115 | 62 | 0.42275 | 706000 | 1546840 | 70.6 | 28000 | 14599.095 |  | 2
115 | 115 | 57 | -4.3353 | 706000 | 1288120 | 70.7 | 28000 | 14599.095 |  | 2
115 | 115 | 75 | 15.3648 | 853000 | 1486150 | 76.1 | 30000 | 17351.7933 |  | 2
115 | 115 | 72 | 11.5424 | 812000 | 1606250 | 74.9 | 30000 | 17351.7933 |  | 2
115 | 115 | 67 | 5.6915 | 747000 | 1749700 | 72.9 | 30000 | 17351.7933 |  | 2
115 | 115 | 62 | 0.42275 | 718000 | 1572700 | 71 | 30000 | 17351.7933 |  | 2
115 | 115 | 57 | -4.3353 | 717000 | 1306050 | 71 | 30000 | 17351.7933 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 8
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 75 | 75 | 100 | 889000 | 316700 | 50.7 | 14000 | 4632.2849 |  | 1
75 | 75 | 72 | 86.8609 | 852000 | 361700 | 49.6 | 14000 | 4632.2849 |  | 1
75 | 75 | 67 | 66.7494 | 787000 | 422260 | 48.1 | 14000 | 4632.2849 |  | 1
75 | 75 | 62 | 48.6386 | 724000 | 505392 | 46.7 | 14000 | 4632.2849 |  | 1
75 | 75 | 57 | 32.2833 | 663000 | 570348 | 45.8 | 14000 | 4632.2849 |  | 1
75 | 75 | 75 | 100 | 933000 | 316625 | 51.8 | 17500 | 6013.8436 |  | 1
75 | 75 | 72 | 86.8609 | 893000 | 362850 | 50.7 | 17500 | 6013.8436 |  | 1
75 | 75 | 67 | 66.7494 | 826000 | 454075 | 49 | 17500 | 6013.8436 |  | 1
75 | 75 | 62 | 48.6386 | 763000 | 550630 | 47.7 | 17500 | 6013.8436 |  | 1
75 | 75 | 57 | 32.2833 | 705000 | 614850 | 46.5 | 17500 | 6013.8436 |  | 1
75 | 75 | 75 | 100 | 960000 | 321990 | 52.6 | 21000 | 8501.8994 |  | 1
75 | 75 | 72 | 86.8609 | 917000 | 373510 | 51.4 | 21000 | 8501.8994 |  | 1
75 | 75 | 67 | 66.7494 | 854000 | 483045 | 49.7 | 21000 | 8501.8994 |  | 1
75 | 75 | 62 | 48.6386 | 789000 | 589890 | 48.3 | 21000 | 8501.8994 |  | 1
75 | 75 | 57 | 32.2833 | 745000 | 658060 | 47.3 | 21000 | 8501.8994 |  | 1
75 | 75 | 75 | 100 | 981000 | 313180 | 53.3 | 24500 | 11717.2011 |  | 1
75 | 75 | 72 | 86.8609 | 937000 | 384095 | 52 | 24500 | 11717.2011 |  | 1
75 | 75 | 67 | 66.7494 | 874000 | 509400 | 50.3 | 24500 | 11717.2011 |  | 1
75 | 75 | 62 | 48.6386 | 809000 | 629400 | 48.8 | 24500 | 11717.2011 |  | 1
75 | 75 | 57 | 32.2833 | 780000 | 689350 | 48 | 24500 | 11717.2011 |  | 1
85 | 85 | 75 | 63.5688 | 869000 | 405300 | 55.8 | 14000 | 4632.2849 |  | 1
85 | 85 | 72 | 54.0993 | 831000 | 450300 | 54.9 | 14000 | 4632.2849 |  | 1
85 | 85 | 67 | 39.6049 | 766000 | 550740 | 53.4 | 14000 | 4632.2849 |  | 1
85 | 85 | 62 | 26.5524 | 703000 | 620608 | 52.1 | 14000 | 4632.2849 |  | 1
85 | 85 | 57 | 14.765 | 641000 | 685696 | 51.2 | 14000 | 4632.2849 |  | 1
85 | 85 | 75 | 63.5688 | 909000 | 432375 | 57 | 17500 | 6013.8436 |  | 1
85 | 85 | 72 | 54.0993 | 870000 | 516112.5 | 55.9 | 17500 | 6013.8436 |  | 1
85 | 85 | 67 | 39.6049 | 803000 | 615925 | 54.4 | 17500 | 6013.8436 |  | 1
85 | 85 | 62 | 26.5524 | 740000 | 703815 | 53.1 | 17500 | 6013.8436 |  | 1
85 | 85 | 57 | 14.765 | 686000 | 757225 | 52 | 17500 | 6013.8436 |  | 1
85 | 85 | 75 | 63.5688 | 935000 | 480940 | 57.7 | 21000 | 8501.8994 |  | 1
85 | 85 | 72 | 54.0993 | 892000 | 562645 | 56.5 | 21000 | 8501.8994 |  | 1
85 | 85 | 67 | 39.6049 | 829000 | 676955 | 55.1 | 21000 | 8501.8994 |  | 1
85 | 85 | 62 | 26.5524 | 765000 | 785110 | 53.8 | 21000 | 8501.8994 |  | 1
85 | 85 | 57 | 14.765 | 726000 | 810630 | 52.9 | 21000 | 8501.8994 |  | 1
85 | 85 | 75 | 63.5688 | 957000 | 522515 | 58.4 | 24500 | 11717.2011 |  | 1
85 | 85 | 72 | 54.0993 | 910000 | 606252.5 | 57.1 | 24500 | 11717.2011 |  | 1
85 | 85 | 67 | 39.6049 | 848000 | 734600 | 55.6 | 24500 | 11717.2011 |  | 1
85 | 85 | 62 | 26.5524 | 783000 | 850252.5 | 54.2 | 24500 | 11717.2011 |  | 1
85 | 85 | 57 | 14.765 | 760000 | 849302.5 | 53.5 | 24500 | 11717.2011 |  | 1
95 | 95 | 75 | 40.2091 | 844000 | 577000 | 62 | 14000 | 4632.2849 |  | 1
95 | 95 | 72 | 33.2947 | 803000 | 579110 | 60.8 | 14000 | 4632.2849 |  | 1
95 | 95 | 67 | 22.7111 | 740000 | 680210 | 59.8 | 14000 | 4632.2849 |  | 1
95 | 95 | 62 | 13.1803 | 679000 | 764140 | 58.3 | 14000 | 4632.2849 |  | 1
95 | 95 | 57 | 4.5734 | 615000 | 809900 | 58.6 | 14000 | 4632.2849 |  | 1
95 | 95 | 75 | 40.2091 | 880000 | 652750 | 63 | 17500 | 6013.8436 |  | 1
95 | 95 | 72 | 33.2947 | 841000 | 672325 | 62.1 | 17500 | 6013.8436 |  | 1
95 | 95 | 67 | 22.7111 | 775000 | 777875 | 60.7 | 17500 | 6013.8436 |  | 1
95 | 95 | 62 | 13.1803 | 711000 | 874650 | 59.5 | 17500 | 6013.8436 |  | 1
95 | 95 | 57 | 4.5734 | 662000 | 895887.5 | 58.9 | 17500 | 6013.8436 |  | 1
95 | 95 | 75 | 40.2091 | 906000 | 661200 | 63.9 | 21000 | 8501.8994 |  | 1
95 | 95 | 72 | 33.2947 | 864000 | 757920 | 62.7 | 21000 | 8501.8994 |  | 1
95 | 95 | 67 | 22.7111 | 799000 | 871385 | 61.4 | 21000 | 8501.8994 |  | 1
95 | 95 | 62 | 13.1803 | 735000 | 978850 | 60.2 | 21000 | 8501.8994 |  | 1
95 | 95 | 57 | 4.5734 | 704000 | 953480 | 59.1 | 21000 | 8501.8994 |  | 1
95 | 95 | 75 | 40.2091 | 925000 | 738527.5 | 64.6 | 24500 | 11717.2011 |  | 1
95 | 95 | 72 | 33.2947 | 884000 | 831697.5 | 63.5 | 24500 | 11717.2011 |  | 1
95 | 95 | 67 | 22.7111 | 817000 | 960740 | 61.9 | 24500 | 11717.2011 |  | 1
95 | 95 | 62 | 13.1803 | 752000 | 1067697.5 | 60.5 | 24500 | 11717.2011 |  | 1
95 | 95 | 57 | 4.5734 | 735000 | 993720 | 60.1 | 24500 | 11717.2011 |  | 1
105 | 105 | 75 | 25.1345 | 813000 | 716000 | 69.2 | 14000 | 4632.2849 |  | 1
105 | 105 | 72 | 20.0232 | 773000 | 703400 | 68.3 | 14000 | 4632.2849 |  | 1
105 | 105 | 67 | 12.1996 | 709000 | 811200 | 67.4 | 14000 | 4632.2849 |  | 1
105 | 105 | 62 | 5.1542 | 649000 | 893900 | 67.1 | 14000 | 4632.2849 |  | 1
105 | 105 | 57 | -1.2082 | 592000 | 916950 | 67.2 | 14000 | 4632.2849 |  | 1
105 | 105 | 75 | 25.1345 | 846000 | 834250 | 70.3 | 17500 | 6013.8436 |  | 1
105 | 105 | 72 | 20.0232 | 806000 | 835500 | 69.1 | 17500 | 6013.8436 |  | 1
105 | 105 | 67 | 12.1996 | 742000 | 941937.5 | 68.6 | 17500 | 6013.8436 |  | 1
105 | 105 | 62 | 5.1542 | 679000 | 1035750 | 68.7 | 17500 | 6013.8436 |  | 1
105 | 105 | 57 | -1.2082 | 637000 | 1012375 | 68.2 | 17500 | 6013.8436 |  | 1
105 | 105 | 75 | 25.1345 | 869000 | 851325 | 71.1 | 21000 | 8501.8994 |  | 1
105 | 105 | 72 | 20.0232 | 828000 | 953975 | 69.7 | 21000 | 8501.8994 |  | 1
105 | 105 | 67 | 12.1996 | 765000 | 1068750 | 69.1 | 21000 | 8501.8994 |  | 1
105 | 105 | 62 | 5.1542 | 701000 | 1163975 | 69.2 | 21000 | 8501.8994 |  | 1
105 | 105 | 57 | -1.2082 | 678000 | 1076475 | 68 | 21000 | 8501.8994 |  | 1
105 | 105 | 75 | 25.1345 | 886000 | 955950 | 71.8 | 24500 | 11717.2011 |  | 1
105 | 105 | 72 | 20.0232 | 846000 | 1053162.5 | 70.7 | 24500 | 11717.2011 |  | 1
105 | 105 | 67 | 12.1996 | 781000 | 1183900 | 69.6 | 24500 | 11717.2011 |  | 1
105 | 105 | 62 | 5.1542 | 717000 | 1265687.5 | 69.1 | 24500 | 11717.2011 |  | 1
105 | 105 | 57 | -1.2082 | 708000 | 1125725 | 68.7 | 24500 | 11717.2011 |  | 1
115 | 115 | 75 | 15.3648 | 779000 | 855000 | 78.2 | 14000 | 4632.2849 |  | 1
115 | 115 | 72 | 11.5424 | 739000 | 830540 | 78.6 | 14000 | 4632.2849 |  | 1
115 | 115 | 67 | 5.6915 | 676000 | 938880 | 77.5 | 14000 | 4632.2849 |  | 1
115 | 115 | 62 | 0.42275 | 616000 | 1022660 | 78 | 14000 | 4632.2849 |  | 1
115 | 115 | 57 | -4.3353 | 562000 | 1023540 | 79.9 | 14000 | 4632.2849 |  | 1
115 | 115 | 75 | 15.3648 | 808000 | 879000 | 79.3 | 17500 | 6013.8436 |  | 1
115 | 115 | 72 | 11.5424 | 770000 | 997637.5 | 78.4 | 17500 | 6013.8436 |  | 1
115 | 115 | 67 | 5.6915 | 706000 | 1102112.5 | 78.9 | 17500 | 6013.8436 |  | 1
115 | 115 | 62 | 0.42275 | 643000 | 1195850 | 79.8 | 17500 | 6013.8436 |  | 1
115 | 115 | 57 | -4.3353 | 610000 | 1115312.5 | 79.5 | 17500 | 6013.8436 |  | 1
115 | 115 | 75 | 15.3648 | 830000 | 1047225 | 80.3 | 21000 | 8501.8994 |  | 1
115 | 115 | 72 | 11.5424 | 791000 | 1146565 | 79.9 | 21000 | 8501.8994 |  | 1
115 | 115 | 67 | 5.6915 | 726000 | 1260650 | 79.3 | 21000 | 8501.8994 |  | 1
115 | 115 | 62 | 0.42275 | 664000 | 1350565 | 79.9 | 21000 | 8501.8994 |  | 1
115 | 115 | 57 | -4.3353 | 647000 | 1180610 | 79.4 | 21000 | 8501.8994 |  | 1
115 | 115 | 75 | 15.3648 | 845000 | 1178762.5 | 81 | 24500 | 11717.2011 |  | 1
115 | 115 | 72 | 11.5424 | 806000 | 1272627.5 | 80.3 | 24500 | 11717.2011 |  | 1
115 | 115 | 67 | 5.6915 | 742000 | 1404060 | 79.6 | 24500 | 11717.2011 |  | 1
115 | 115 | 62 | 0.42275 | 683000 | 1451897.5 | 78.5 | 24500 | 11717.2011 |  | 1
115 | 115 | 57 | -4.3353 | 677000 | 1233517.5 | 79.4 | 24500 | 11717.2011 |  | 1
75 | 75 | 75 | 100 | 1000000 | 313840 | 53.7 | 28000 | 15747.2682 |  | 1
75 | 75 | 72 | 86.8609 | 955000 | 395220 | 52.5 | 28000 | 15747.2682 |  | 1
75 | 75 | 67 | 66.7494 | 889000 | 535140 | 50.7 | 28000 | 15747.2682 |  | 1
75 | 75 | 62 | 48.6386 | 823000 | 662760 | 49.1 | 28000 | 15747.2682 |  | 1
75 | 75 | 57 | 32.2833 | 808000 | 713640 | 48.7 | 28000 | 15747.2682 |  | 1
75 | 75 | 75 | 100 | 1007000 | 313900 | 53.9 | 30000 | 18470.7933 |  | 1
75 | 75 | 72 | 86.8609 | 964000 | 399950 | 52.7 | 30000 | 18470.7933 |  | 1
75 | 75 | 67 | 66.7494 | 896000 | 549300 | 50.9 | 30000 | 18470.7933 |  | 1
75 | 75 | 62 | 48.6386 | 830000 | 676900 | 49.3 | 30000 | 18470.7933 |  | 1
75 | 75 | 57 | 32.2833 | 822000 | 725850 | 49.1 | 30000 | 18470.7933 |  | 1
85 | 85 | 75 | 63.5688 | 972000 | 556700 | 58.9 | 28000 | 15747.2682 |  | 1
85 | 85 | 72 | 54.0993 | 930000 | 647320 | 57.7 | 28000 | 15747.2682 |  | 1
85 | 85 | 67 | 39.6049 | 862000 | 790860 | 56 | 28000 | 15747.2682 |  | 1
85 | 85 | 62 | 26.5524 | 798000 | 899700 | 54.5 | 28000 | 15747.2682 |  | 1
85 | 85 | 57 | 14.765 | 787000 | 878280 | 54.2 | 28000 | 15747.2682 |  | 1
85 | 85 | 75 | 63.5688 | 979000 | 574750 | 59.1 | 30000 | 18470.7933 |  | 1
85 | 85 | 72 | 54.0993 | 937000 | 669050 | 57.9 | 30000 | 18470.7933 |  | 1
85 | 85 | 67 | 39.6049 | 869000 | 820700 | 56.2 | 30000 | 18470.7933 |  | 1
85 | 85 | 62 | 26.5524 | 804000 | 929450 | 54.6 | 30000 | 18470.7933 |  | 1
85 | 85 | 57 | 14.765 | 801000 | 893850 | 54.5 | 30000 | 18470.7933 |  | 1
95 | 95 | 75 | 40.2091 | 939000 | 808080 | 65 | 28000 | 15747.2682 |  | 1
95 | 95 | 72 | 33.2947 | 898000 | 902320 | 64 | 28000 | 15747.2682 |  | 1
95 | 95 | 67 | 22.7111 | 831000 | 1046940 | 62.3 | 28000 | 15747.2682 |  | 1
95 | 95 | 62 | 13.1803 | 766000 | 1140460 | 60.8 | 28000 | 15747.2682 |  | 1
95 | 95 | 57 | 4.5734 | 762000 | 1029960 | 60.6 | 28000 | 15747.2682 |  | 1
95 | 95 | 75 | 40.2091 | 946000 | 844800 | 65.2 | 30000 | 18470.7933 |  | 1
95 | 95 | 72 | 33.2947 | 904000 | 939750 | 64.2 | 30000 | 18470.7933 |  | 1
95 | 95 | 67 | 22.7111 | 837000 | 1092700 | 62.4 | 30000 | 18470.7933 |  | 1
95 | 95 | 62 | 13.1803 | 777000 | 1162050 | 61 | 30000 | 18470.7933 |  | 1
95 | 95 | 57 | 4.5734 | 775000 | 1052200 | 61 | 30000 | 18470.7933 |  | 1
105 | 105 | 75 | 25.1345 | 899000 | 1053800 | 72.2 | 28000 | 15747.2682 |  | 1
105 | 105 | 72 | 20.0232 | 859000 | 1153200 | 71.2 | 28000 | 15747.2682 |  | 1
105 | 105 | 67 | 12.1996 | 793000 | 1300900 | 69.9 | 28000 | 15747.2682 |  | 1
105 | 105 | 62 | 5.1542 | 736000 | 1333300 | 68.9 | 28000 | 15747.2682 |  | 1
105 | 105 | 57 | -1.2082 | 733000 | 1164200 | 69 | 28000 | 15747.2682 |  | 1
105 | 105 | 75 | 25.1345 | 905000 | 1109000 | 72.4 | 30000 | 18470.7933 |  | 1
105 | 105 | 72 | 20.0232 | 864000 | 1206250 | 71.4 | 30000 | 18470.7933 |  | 1
105 | 105 | 67 | 12.1996 | 800000 | 1370750 | 70.2 | 30000 | 18470.7933 |  | 1
105 | 105 | 62 | 5.1542 | 748000 | 1357750 | 69 | 30000 | 18470.7933 |  | 1
105 | 105 | 57 | -1.2082 | 746000 | 1183250 | 69.2 | 30000 | 18470.7933 |  | 1
115 | 115 | 75 | 15.3648 | 857000 | 1309300 | 81.3 | 28000 | 15747.2682 |  | 1
115 | 115 | 72 | 11.5424 | 818000 | 1404080 | 80.8 | 28000 | 15747.2682 |  | 1
115 | 115 | 67 | 5.6915 | 753000 | 1552860 | 80.2 | 28000 | 15747.2682 |  | 1
115 | 115 | 62 | 0.42275 | 705000 | 1500500 | 79.2 | 28000 | 15747.2682 |  | 1
115 | 115 | 57 | -4.3353 | 701000 | 1283120 | 79.5 | 28000 | 15747.2682 |  | 1
115 | 115 | 75 | 15.3648 | 863000 | 1384750 | 81.6 | 30000 | 18470.7933 |  | 1
115 | 115 | 72 | 11.5424 | 823000 | 1484300 | 81 | 30000 | 18470.7933 |  | 1
115 | 115 | 67 | 5.6915 | 759000 | 1641850 | 80.2 | 30000 | 18470.7933 |  | 1
115 | 115 | 62 | 0.42275 | 717000 | 1522050 | 79.3 | 30000 | 18470.7933 |  | 1
115 | 115 | 57 | -4.3353 | 713000 | 1302050 | 79.5 | 30000 | 18470.7933 |  | 1
75 | 75 | 75 | 100 | 912000 | 327700 | 51.6 | 14000 | 4632.2849 |  | 2
75 | 75 | 72 | 86.8609 | 868000 | 358304 | 50.4 | 14000 | 4632.2849 |  | 2
75 | 75 | 67 | 66.7494 | 796000 | 452612 | 48.4 | 14000 | 4632.2849 |  | 2
75 | 75 | 62 | 48.6386 | 732000 | 531612 | 46.7 | 14000 | 4632.2849 |  | 2
75 | 75 | 57 | 32.2833 | 674000 | 604612 | 45.3 | 14000 | 4632.2849 |  | 2
75 | 75 | 75 | 100 | 960000 | 339625 | 52.9 | 17500 | 6013.8436 |  | 2
75 | 75 | 72 | 86.8609 | 913000 | 385295 | 51.5 | 17500 | 6013.8436 |  | 2
75 | 75 | 67 | 66.7494 | 841000 | 491960 | 49.5 | 17500 | 6013.8436 |  | 2
75 | 75 | 62 | 48.6386 | 773000 | 592515 | 47.8 | 17500 | 6013.8436 |  | 2
75 | 75 | 57 | 32.2833 | 721000 | 637000 | 46.5 | 17500 | 6013.8436 |  | 2
75 | 75 | 75 | 100 | 992000 | 319890 | 53.8 | 21000 | 8501.8994 |  | 2
75 | 75 | 72 | 86.8609 | 944000 | 405220 | 52.4 | 21000 | 8501.8994 |  | 2
75 | 75 | 67 | 66.7494 | 871000 | 526286 | 50.3 | 21000 | 8501.8994 |  | 2
75 | 75 | 62 | 48.6386 | 803000 | 639286 | 48.5 | 21000 | 8501.8994 |  | 2
75 | 75 | 57 | 32.2833 | 767000 | 677750 | 47.7 | 21000 | 8501.8994 |  | 2
75 | 75 | 75 | 100 | 1016000 | 334436 | 54.4 | 24500 | 11717.2011 |  | 2
75 | 75 | 72 | 86.8609 | 967000 | 422590 | 53 | 24500 | 11717.2011 |  | 2
75 | 75 | 67 | 66.7494 | 892000 | 560167 | 50.9 | 24500 | 11717.2011 |  | 2
75 | 75 | 62 | 48.6386 | 823000 | 682590 | 49.1 | 24500 | 11717.2011 |  | 2
75 | 75 | 57 | 32.2833 | 805000 | 711655 | 48.7 | 24500 | 11717.2011 |  | 2
85 | 85 | 75 | 63.5688 | 885000 | 411300 | 56.5 | 14000 | 4632.2849 |  | 2
85 | 85 | 72 | 54.0993 | 837000 | 471520 | 55.2 | 14000 | 4632.2849 |  | 2
85 | 85 | 67 | 39.6049 | 776000 | 549432 | 53.3 | 14000 | 4632.2849 |  | 2
85 | 85 | 62 | 26.5524 | 714000 | 625344 | 51.7 | 14000 | 4632.2849 |  | 2
85 | 85 | 57 | 14.765 | 660000 | 703432 | 50.4 | 14000 | 4632.2849 |  | 2
85 | 85 | 75 | 63.5688 | 928000 | 471075 | 57.7 | 17500 | 6013.8436 |  | 2
85 | 85 | 72 | 54.0993 | 884000 | 522150 | 56.4 | 17500 | 6013.8436 |  | 2
85 | 85 | 67 | 39.6049 | 819000 | 618040 | 54.4 | 17500 | 6013.8436 |  | 2
85 | 85 | 62 | 26.5524 | 752000 | 714485 | 52.6 | 17500 | 6013.8436 |  | 2
85 | 85 | 57 | 14.765 | 708000 | 791037.5 | 51.6 | 17500 | 6013.8436 |  | 2
85 | 85 | 75 | 63.5688 | 958000 | 507978 | 58.6 | 21000 | 8501.8994 |  | 2
85 | 85 | 72 | 54.0993 | 913000 | 569780 | 57.2 | 21000 | 8501.8994 |  | 2
85 | 85 | 67 | 39.6049 | 847000 | 682648 | 55.3 | 21000 | 8501.8994 |  | 2
85 | 85 | 62 | 26.5524 | 786000 | 800714 | 53.6 | 21000 | 8501.8994 |  | 2
85 | 85 | 57 | 14.765 | 752000 | 840095 | 52.7 | 21000 | 8501.8994 |  | 2
85 | 85 | 75 | 63.5688 | 980000 | 540564 | 59.3 | 24500 | 11717.2011 |  | 2
85 | 85 | 72 | 54.0993 | 938000 | 616410 | 57.9 | 24500 | 11717.2011 |  | 2
85 | 85 | 67 | 39.6049 | 869000 | 748833 | 55.9 | 24500 | 11717.2011 |  | 2
85 | 85 | 62 | 26.5524 | 802000 | 879987 | 54.1 | 24500 | 11717.2011 |  | 2
85 | 85 | 57 | 14.765 | 787000 | 878997.5 | 53.7 | 24500 | 11717.2011 |  | 2
95 | 95 | 75 | 40.2091 | 858000 | 583000 | 62.2 | 14000 | 4632.2849 |  | 2
95 | 95 | 72 | 33.2947 | 809000 | 623760 | 60.8 | 14000 | 4632.2849 |  | 2
95 | 95 | 67 | 22.7111 | 759000 | 711070 | 59.3 | 14000 | 4632.2849 |  | 2
95 | 95 | 62 | 13.1803 | 698000 | 793380 | 57.7 | 14000 | 4632.2849 |  | 2
95 | 95 | 57 | 4.5734 | 643000 | 857760 | 56.5 | 14000 | 4632.2849 |  | 2
95 | 95 | 75 | 40.2091 | 901000 | 635987.5 | 63.5 | 17500 | 6013.8436 |  | 2
95 | 95 | 72 | 33.2947 | 861000 | 715312.5 | 62.3 | 17500 | 6013.8436 |  | 2
95 | 95 | 67 | 22.7111 | 793000 | 820087.5 | 60.3 | 17500 | 6013.8436 |  | 2
95 | 95 | 62 | 13.1803 | 735000 | 928862.5 | 58.8 | 17500 | 6013.8436 |  | 2
95 | 95 | 57 | 4.5734 | 693000 | 938437.5 | 57.7 | 17500 | 6013.8436 |  | 2
95 | 95 | 75 | 40.2091 | 931000 | 724245 | 64.5 | 21000 | 8501.8994 |  | 2
95 | 95 | 72 | 33.2947 | 889000 | 803175 | 63.2 | 21000 | 8501.8994 |  | 2
95 | 95 | 67 | 22.7111 | 825000 | 928105 | 61.3 | 21000 | 8501.8994 |  | 2
95 | 95 | 62 | 13.1803 | 763000 | 1037640 | 59.7 | 21000 | 8501.8994 |  | 2
95 | 95 | 57 | 4.5734 | 735000 | 994875 | 58.8 | 21000 | 8501.8994 |  | 2
95 | 95 | 75 | 40.2091 | 954000 | 798952.5 | 65.3 | 24500 | 11717.2011 |  | 2
95 | 95 | 72 | 33.2947 | 913000 | 889037.5 | 64 | 24500 | 11717.2011 |  | 2
95 | 95 | 67 | 22.7111 | 845000 | 1029080 | 62 | 24500 | 11717.2011 |  | 2
95 | 95 | 62 | 13.1803 | 777000 | 1139995 | 60 | 24500 | 11717.2011 |  | 2
95 | 95 | 57 | 4.5734 | 769000 | 1039847.5 | 59.8 | 24500 | 11717.2011 |  | 2
105 | 105 | 75 | 25.1345 | 835000 | 729000 | 69.2 | 14000 | 4632.2849 |  | 2
105 | 105 | 72 | 20.0232 | 795000 | 761750 | 68 | 14000 | 4632.2849 |  | 2
105 | 105 | 67 | 12.1996 | 730000 | 853300 | 66.1 | 14000 | 4632.2849 |  | 2
105 | 105 | 62 | 5.1542 | 676000 | 932300 | 65.2 | 14000 | 4632.2849 |  | 2
105 | 105 | 57 | -1.2082 | 623000 | 968200 | 63.6 | 14000 | 4632.2849 |  | 2
105 | 105 | 75 | 25.1345 | 875000 | 807937.5 | 70.7 | 17500 | 6013.8436 |  | 2
105 | 105 | 72 | 20.0232 | 834000 | 887187.5 | 69.5 | 17500 | 6013.8436 |  | 2
105 | 105 | 67 | 12.1996 | 767000 | 1000625 | 67.4 | 17500 | 6013.8436 |  | 2
105 | 105 | 62 | 5.1542 | 709000 | 1097625 | 66.2 | 17500 | 6013.8436 |  | 2
105 | 105 | 57 | -1.2082 | 673000 | 1072437.5 | 65 | 17500 | 6013.8436 |  | 2
105 | 105 | 75 | 25.1345 | 903000 | 929075 | 71.8 | 21000 | 8501.8994 |  | 2
105 | 105 | 72 | 20.0232 | 862000 | 1011625 | 70.6 | 21000 | 8501.8994 |  | 2
105 | 105 | 67 | 12.1996 | 796000 | 1140175 | 68.7 | 21000 | 8501.8994 |  | 2
105 | 105 | 62 | 5.1542 | 733000 | 1244400 | 67 | 21000 | 8501.8994 |  | 2
105 | 105 | 57 | -1.2082 | 714000 | 1135575 | 66.1 | 21000 | 8501.8994 |  | 2
105 | 105 | 75 | 25.1345 | 922000 | 1045325 | 72.6 | 24500 | 11717.2011 |  | 2
105 | 105 | 72 | 20.0232 | 881000 | 1133062.5 | 71.3 | 24500 | 11717.2011 |  | 2
105 | 105 | 67 | 12.1996 | 813000 | 1274800 | 69.3 | 24500 | 11717.2011 |  | 2
105 | 105 | 62 | 5.1542 | 751000 | 1370587.5 | 67.3 | 24500 | 11717.2011 |  | 2
105 | 105 | 57 | -1.2082 | 746000 | 1183937.5 | 67.1 | 24500 | 11717.2011 |  | 2
115 | 115 | 75 | 15.3648 | 804000 | 873000 | 77.7 | 14000 | 4632.2849 |  | 2
115 | 115 | 72 | 11.5424 | 766000 | 896050 | 76.8 | 14000 | 4632.2849 |  | 2
115 | 115 | 67 | 5.6915 | 701000 | 991220 | 74.5 | 14000 | 4632.2849 |  | 2
115 | 115 | 62 | 0.42275 | 645000 | 1068220 | 75.6 | 14000 | 4632.2849 |  | 2
115 | 115 | 57 | -4.3353 | 596000 | 1086490 | 74.1 | 14000 | 4632.2849 |  | 2
115 | 115 | 75 | 15.3648 | 840000 | 984587.5 | 79.5 | 17500 | 6013.8436 |  | 2
115 | 115 | 72 | 11.5424 | 799000 | 1064800 | 78.3 | 17500 | 6013.8436 |  | 2
115 | 115 | 67 | 5.6915 | 735000 | 1175275 | 76.4 | 17500 | 6013.8436 |  | 2
115 | 115 | 62 | 0.42275 | 677000 | 1271275 | 75.8 | 17500 | 6013.8436 |  | 2
115 | 115 | 57 | -4.3353 | 648000 | 1180262.5 | 74.9 | 17500 | 6013.8436 |  | 2
115 | 115 | 75 | 15.3648 | 865000 | 1138990 | 80.7 | 21000 | 8501.8994 |  | 2
115 | 115 | 72 | 11.5424 | 826000 | 1226160 | 79.8 | 21000 | 8501.8994 |  | 2
115 | 115 | 67 | 5.6915 | 760000 | 1349245 | 78.3 | 21000 | 8501.8994 |  | 2
115 | 115 | 62 | 0.42275 | 699000 | 1449160 | 76.7 | 21000 | 8501.8994 |  | 2
115 | 115 | 57 | -4.3353 | 687000 | 1252950 | 75.8 | 21000 | 8501.8994 |  | 2
115 | 115 | 75 | 15.3648 | 884000 | 1285655 | 82.1 | 24500 | 11717.2011 |  | 2
115 | 115 | 72 | 11.5424 | 843000 | 1376087.5 | 80.8 | 24500 | 11717.2011 |  | 2
115 | 115 | 67 | 5.6915 | 777000 | 1519520 | 79 | 24500 | 11717.2011 |  | 2
115 | 115 | 62 | 0.42275 | 719000 | 1539060 | 75.3 | 24500 | 11717.2011 |  | 2
115 | 115 | 57 | -4.3353 | 718000 | 1312247.5 | 76.5 | 24500 | 11717.2011 |  | 2
75 | 75 | 75 | 100 | 1034000 | 333696 | 54.9 | 28000 | 15747.2682 |  | 2
75 | 75 | 72 | 86.8609 | 985000 | 433872 | 53.5 | 28000 | 15747.2682 |  | 2
75 | 75 | 67 | 66.7494 | 909000 | 589960 | 51.4 | 28000 | 15747.2682 |  | 2
75 | 75 | 62 | 48.6386 | 839000 | 699608 | 49.6 | 28000 | 15747.2682 |  | 2
75 | 75 | 57 | 32.2833 | 836000 | 738560 | 49.5 | 28000 | 15747.2682 |  | 2
75 | 75 | 75 | 100 | 1042000 | 334460 | 55.2 | 30000 | 18470.7933 |  | 2
75 | 75 | 72 | 86.8609 | 993000 | 441220 | 53.8 | 30000 | 18470.7933 |  | 2
75 | 75 | 67 | 66.7494 | 916000 | 607600 | 51.6 | 30000 | 18470.7933 |  | 2
75 | 75 | 62 | 48.6386 | 853000 | 706650 | 50 | 30000 | 18470.7933 |  | 2
75 | 75 | 57 | 32.2833 | 851000 | 751550 | 49.9 | 30000 | 18470.7933 |  | 2
85 | 85 | 75 | 63.5688 | 1001000 | 577216 | 59.8 | 28000 | 15747.2682 |  | 2
85 | 85 | 72 | 54.0993 | 955000 | 665128 | 58.5 | 28000 | 15747.2682 |  | 2
85 | 85 | 67 | 39.6049 | 885000 | 815040 | 56.4 | 28000 | 15747.2682 |  | 2
85 | 85 | 62 | 26.5524 | 817000 | 954480 | 54.5 | 28000 | 15747.2682 |  | 2
85 | 85 | 57 | 14.765 | 816000 | 910360 | 54.5 | 28000 | 15747.2682 |  | 2
85 | 85 | 75 | 63.5688 | 1009000 | 601540 | 60.1 | 30000 | 18470.7933 |  | 2
85 | 85 | 72 | 54.0993 | 963000 | 690780 | 58.7 | 30000 | 18470.7933 |  | 2
85 | 85 | 67 | 39.6049 | 892000 | 849400 | 56.6 | 30000 | 18470.7933 |  | 2
85 | 85 | 62 | 26.5524 | 831000 | 955750 | 55 | 30000 | 18470.7933 |  | 2
85 | 85 | 57 | 14.765 | 829000 | 925150 | 54.9 | 30000 | 18470.7933 |  | 2
95 | 95 | 75 | 40.2091 | 973000 | 872660 | 65.9 | 28000 | 15747.2682 |  | 2
95 | 95 | 72 | 33.2947 | 929000 | 969280 | 64.6 | 28000 | 15747.2682 |  | 2
95 | 95 | 67 | 22.7111 | 859000 | 1125900 | 62.5 | 28000 | 15747.2682 |  | 2
95 | 95 | 62 | 13.1803 | 799000 | 1197940 | 60.6 | 28000 | 15747.2682 |  | 2
95 | 95 | 57 | 4.5734 | 797000 | 1078820 | 60.6 | 28000 | 15747.2682 |  | 2
95 | 95 | 75 | 40.2091 | 981000 | 913350 | 66.2 | 30000 | 18470.7933 |  | 2
95 | 95 | 72 | 33.2947 | 936000 | 1017300 | 64.8 | 30000 | 18470.7933 |  | 2
95 | 95 | 67 | 22.7111 | 867000 | 1183250 | 62.8 | 30000 | 18470.7933 |  | 2
95 | 95 | 62 | 13.1803 | 812000 | 1211900 | 61 | 30000 | 18470.7933 |  | 2
95 | 95 | 57 | 4.5734 | 810000 | 1097100 | 61 | 30000 | 18470.7933 |  | 2
105 | 105 | 75 | 25.1345 | 938000 | 1147100 | 73.3 | 28000 | 15747.2682 |  | 2
105 | 105 | 72 | 20.0232 | 895000 | 1254500 | 71.9 | 28000 | 15747.2682 |  | 2
105 | 105 | 67 | 12.1996 | 827000 | 1405500 | 69.9 | 28000 | 15747.2682 |  | 2
105 | 105 | 62 | 5.1542 | 772000 | 1413800 | 67.6 | 28000 | 15747.2682 |  | 2
105 | 105 | 57 | -1.2082 | 772000 | 1226300 | 67.9 | 28000 | 15747.2682 |  | 2
105 | 105 | 75 | 25.1345 | 945000 | 1209250 | 73.6 | 30000 | 18470.7933 |  | 2
105 | 105 | 72 | 20.0232 | 901000 | 1314500 | 72.2 | 30000 | 18470.7933 |  | 2
105 | 105 | 67 | 12.1996 | 833000 | 1482750 | 70.2 | 30000 | 18470.7933 |  | 2
105 | 105 | 62 | 5.1542 | 784000 | 1444000 | 68.1 | 30000 | 18470.7933 |  | 2
105 | 105 | 57 | -1.2082 | 785000 | 1247000 | 68.3 | 30000 | 18470.7933 |  | 2
115 | 115 | 75 | 15.3648 | 898000 | 1420540 | 83 | 28000 | 15747.2682 |  | 2
115 | 115 | 72 | 11.5424 | 856000 | 1534100 | 81.6 | 28000 | 15747.2682 |  | 2
115 | 115 | 67 | 5.6915 | 789000 | 1683100 | 80 | 28000 | 15747.2682 |  | 2
115 | 115 | 62 | 0.42275 | 742000 | 1625960 | 76.5 | 28000 | 15747.2682 |  | 2
115 | 115 | 57 | -4.3353 | 743000 | 1357460 | 77.3 | 28000 | 15747.2682 |  | 2
115 | 115 | 75 | 15.3648 | 905000 | 1503150 | 83.4 | 30000 | 18470.7933 |  | 2
115 | 115 | 72 | 11.5424 | 862000 | 1611700 | 82 | 30000 | 18470.7933 |  | 2
115 | 115 | 67 | 5.6915 | 794000 | 1781250 | 80 | 30000 | 18470.7933 |  | 2
115 | 115 | 62 | 0.42275 | 756000 | 1656900 | 77.6 | 30000 | 18470.7933 |  | 2
115 | 115 | 57 | -4.3353 | 755000 | 1378700 | 77.7 | 30000 | 18470.7933 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 9
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 75 | 75 | 100 | 1118000 | 397900 | 61.5 | 18000 | 5757.5363 |  | 1
75 | 75 | 72 | 86.8609 | 1070000 | 450900 | 60.5 | 18000 | 5757.5363 |  | 1
75 | 75 | 67 | 66.7494 | 985000 | 528590 | 59 | 18000 | 5757.5363 |  | 1
75 | 75 | 62 | 48.6386 | 903000 | 620620 | 57.8 | 18000 | 5757.5363 |  | 1
75 | 75 | 57 | 32.2833 | 822000 | 702610 | 56.7 | 18000 | 5757.5363 |  | 1
75 | 75 | 75 | 100 | 1173000 | 396375 | 62.6 | 22500 | 9252.067 |  | 1
75 | 75 | 72 | 86.8609 | 1118000 | 456137.5 | 61.5 | 22500 | 9252.067 |  | 1
75 | 75 | 67 | 66.7494 | 1032000 | 567237.5 | 59.9 | 22500 | 9252.067 |  | 1
75 | 75 | 62 | 48.6386 | 950000 | 680762.5 | 58.6 | 22500 | 9252.067 |  | 1
75 | 75 | 57 | 32.2833 | 884000 | 761137.5 | 57.4 | 22500 | 9252.067 |  | 1
75 | 75 | 75 | 100 | 1204000 | 407850 | 63.3 | 27000 | 14142.743 |  | 1
75 | 75 | 72 | 86.8609 | 1152000 | 469310 | 62.2 | 27000 | 14142.743 |  | 1
75 | 75 | 67 | 66.7494 | 1066000 | 602370 | 60.6 | 27000 | 14142.743 |  | 1
75 | 75 | 62 | 48.6386 | 981000 | 734885 | 59.2 | 27000 | 14142.743 |  | 1
75 | 75 | 57 | 32.2833 | 922000 | 811705 | 58.2 | 27000 | 14142.743 |  | 1
75 | 75 | 75 | 100 | 1231000 | 396322.5 | 63.9 | 31500 | 20679.6201 |  | 1
75 | 75 | 72 | 86.8609 | 1175000 | 481462.5 | 62.8 | 31500 | 20679.6201 |  | 1
75 | 75 | 67 | 66.7494 | 1090000 | 634997.5 | 61.1 | 31500 | 20679.6201 |  | 1
75 | 75 | 62 | 48.6386 | 1005000 | 781997.5 | 59.6 | 31500 | 20679.6201 |  | 1
75 | 75 | 57 | 32.2833 | 970000 | 856915 | 58.9 | 31500 | 20679.6201 |  | 1
85 | 85 | 75 | 63.5688 | 1086000 | 506100 | 68.1 | 18000 | 5757.5363 |  | 1
85 | 85 | 72 | 54.0993 | 1037000 | 563100 | 67.1 | 18000 | 5757.5363 |  | 1
85 | 85 | 67 | 39.6049 | 954000 | 685410 | 65.8 | 18000 | 5757.5363 |  | 1
85 | 85 | 62 | 26.5524 | 873000 | 782380 | 64.6 | 18000 | 5757.5363 |  | 1
85 | 85 | 57 | 14.765 | 791000 | 847380 | 63.3 | 18000 | 5757.5363 |  | 1
85 | 85 | 75 | 63.5688 | 1135000 | 538625 | 69.1 | 22500 | 9252.067 |  | 1
85 | 85 | 72 | 54.0993 | 1083000 | 639337.5 | 68.1 | 22500 | 9252.067 |  | 1
85 | 85 | 67 | 39.6049 | 998000 | 765762.5 | 66.6 | 22500 | 9252.067 |  | 1
85 | 85 | 62 | 26.5524 | 917000 | 884237.5 | 65.4 | 22500 | 9252.067 |  | 1
85 | 85 | 57 | 14.765 | 847000 | 946337.5 | 64.2 | 22500 | 9252.067 |  | 1
85 | 85 | 75 | 63.5688 | 1165000 | 591870 | 69.8 | 27000 | 14142.743 |  | 1
85 | 85 | 72 | 54.0993 | 1112000 | 699660 | 68.7 | 27000 | 14142.743 |  | 1
85 | 85 | 67 | 39.6049 | 1030000 | 840630 | 67.2 | 27000 | 14142.743 |  | 1
85 | 85 | 62 | 26.5524 | 947000 | 974115 | 66 | 27000 | 14142.743 |  | 1
85 | 85 | 57 | 14.765 | 899000 | 1004840 | 65.1 | 27000 | 14142.743 |  | 1
85 | 85 | 75 | 63.5688 | 1187000 | 645875 | 70.3 | 31500 | 20679.6201 |  | 1
85 | 85 | 72 | 54.0993 | 1137000 | 751537.5 | 69.3 | 31500 | 20679.6201 |  | 1
85 | 85 | 67 | 39.6049 | 1052000 | 912002.5 | 67.7 | 31500 | 20679.6201 |  | 1
85 | 85 | 62 | 26.5524 | 970000 | 1055270 | 66.4 | 31500 | 20679.6201 |  | 1
85 | 85 | 57 | 14.765 | 942000 | 1051620 | 65.8 | 31500 | 20679.6201 |  | 1
95 | 95 | 75 | 40.2091 | 1050000 | 727000 | 75.7 | 18000 | 5757.5363 |  | 1
95 | 95 | 72 | 33.2947 | 1001000 | 707780 | 74.7 | 18000 | 5757.5363 |  | 1
95 | 95 | 67 | 22.7111 | 920000 | 846360 | 73.6 | 18000 | 5757.5363 |  | 1
95 | 95 | 62 | 13.1803 | 841000 | 948270 | 72.3 | 18000 | 5757.5363 |  | 1
95 | 95 | 57 | 4.5734 | 763000 | 1009360 | 71.3 | 18000 | 5757.5363 |  | 1
95 | 95 | 75 | 40.2091 | 1093000 | 821250 | 76.7 | 22500 | 9252.067 |  | 1
95 | 95 | 72 | 33.2947 | 1044000 | 834137.5 | 75.8 | 22500 | 9252.067 |  | 1
95 | 95 | 67 | 22.7111 | 961000 | 970700 | 74.4 | 22500 | 9252.067 |  | 1
95 | 95 | 62 | 13.1803 | 882000 | 1088412.5 | 73.1 | 22500 | 9252.067 |  | 1
95 | 95 | 57 | 4.5734 | 827000 | 1088437.5 | 72.1 | 22500 | 9252.067 |  | 1
95 | 95 | 75 | 40.2091 | 1122000 | 813580 | 77.4 | 27000 | 14142.743 |  | 1
95 | 95 | 72 | 33.2947 | 1073000 | 935220 | 76.5 | 27000 | 14142.743 |  | 1
95 | 95 | 67 | 22.7111 | 990000 | 1086585 | 75 | 27000 | 14142.743 |  | 1
95 | 95 | 62 | 13.1803 | 909000 | 1215585 | 73.7 | 27000 | 14142.743 |  | 1
95 | 95 | 57 | 4.5734 | 873000 | 1184850 | 72.9 | 27000 | 14142.743 |  | 1
95 | 95 | 75 | 40.2091 | 1144000 | 908602.5 | 77.9 | 31500 | 20679.6201 |  | 1
95 | 95 | 72 | 33.2947 | 1093000 | 1030590 | 76.9 | 31500 | 20679.6201 |  | 1
95 | 95 | 67 | 22.7111 | 1011000 | 1191787.5 | 75.4 | 31500 | 20679.6201 |  | 1
95 | 95 | 62 | 13.1803 | 930000 | 1324590 | 74.1 | 31500 | 20679.6201 |  | 1
95 | 95 | 57 | 4.5734 | 910000 | 1232245 | 73.7 | 31500 | 20679.6201 |  | 1
105 | 105 | 75 | 25.1345 | 1010000 | 906000 | 84.5 | 18000 | 5757.5363 |  | 1
105 | 105 | 72 | 20.0232 | 961000 | 868000 | 83.7 | 18000 | 5757.5363 |  | 1
105 | 105 | 67 | 12.1996 | 881000 | 1008550 | 82.4 | 18000 | 5757.5363 |  | 1
105 | 105 | 62 | 5.1542 | 806000 | 1118400 | 81.3 | 18000 | 5757.5363 |  | 1
105 | 105 | 57 | -1.2082 | 734000 | 1154700 | 81.1 | 18000 | 5757.5363 |  | 1
105 | 105 | 75 | 25.1345 | 1048000 | 1054750 | 85.4 | 22500 | 9252.067 |  | 1
105 | 105 | 72 | 20.0232 | 1000000 | 1035937.5 | 84.6 | 22500 | 9252.067 |  | 1
105 | 105 | 67 | 12.1996 | 919000 | 1170500 | 83.2 | 22500 | 9252.067 |  | 1
105 | 105 | 62 | 5.1542 | 842000 | 1289687.5 | 82.2 | 22500 | 9252.067 |  | 1
105 | 105 | 57 | -1.2082 | 791000 | 1261250 | 81.8 | 22500 | 9252.067 |  | 1
105 | 105 | 75 | 25.1345 | 1075000 | 1046575 | 86.1 | 27000 | 14142.743 |  | 1
105 | 105 | 72 | 20.0232 | 1026000 | 1177125 | 85.1 | 27000 | 14142.743 |  | 1
105 | 105 | 67 | 12.1996 | 946000 | 1326975 | 83.8 | 27000 | 14142.743 |  | 1
105 | 105 | 62 | 5.1542 | 867000 | 1452975 | 82.8 | 27000 | 14142.743 |  | 1
105 | 105 | 57 | -1.2082 | 839000 | 1336475 | 82 | 27000 | 14142.743 |  | 1
105 | 105 | 75 | 25.1345 | 1095000 | 1183662.5 | 86.6 | 31500 | 20679.6201 |  | 1
105 | 105 | 72 | 20.0232 | 1046000 | 1305650 | 85.7 | 31500 | 20679.6201 |  | 1
105 | 105 | 67 | 12.1996 | 965000 | 1476975 | 84.2 | 31500 | 20679.6201 |  | 1
105 | 105 | 62 | 5.1542 | 886000 | 1569325 | 82.9 | 31500 | 20679.6201 |  | 1
105 | 105 | 57 | -1.2082 | 874000 | 1393750 | 82.6 | 31500 | 20679.6201 |  | 1
115 | 115 | 75 | 15.3648 | 963000 | 1084000 | 94.5 | 18000 | 5757.5363 |  | 1
115 | 115 | 72 | 11.5424 | 914000 | 1036120 | 93.7 | 18000 | 5757.5363 |  | 1
115 | 115 | 67 | 5.6915 | 838000 | 1173700 | 93.5 | 18000 | 5757.5363 |  | 1
115 | 115 | 62 | 0.42275 | 768000 | 1284560 | 92.2 | 18000 | 5757.5363 |  | 1
115 | 115 | 57 | -4.3353 | 713000 | 1247400 | 92.2 | 18000 | 5757.5363 |  | 1
115 | 115 | 75 | 15.3648 | 997000 | 1078350 | 95.3 | 22500 | 9252.067 |  | 1
115 | 115 | 72 | 11.5424 | 950000 | 1236975 | 94.5 | 22500 | 9252.067 |  | 1
115 | 115 | 67 | 5.6915 | 872000 | 1377962.5 | 93.9 | 22500 | 9252.067 |  | 1
115 | 115 | 62 | 0.42275 | 797000 | 1488962.5 | 94 | 22500 | 9252.067 |  | 1
115 | 115 | 57 | -4.3353 | 758000 | 1381700 | 93.5 | 22500 | 9252.067 |  | 1
115 | 115 | 75 | 15.3648 | 1021000 | 1295390 | 96 | 27000 | 14142.743 |  | 1
115 | 115 | 72 | 11.5424 | 974000 | 1420970 | 95.2 | 27000 | 14142.743 |  | 1
115 | 115 | 67 | 5.6915 | 896000 | 1565365 | 94.2 | 27000 | 14142.743 |  | 1
115 | 115 | 62 | 0.42275 | 821000 | 1677970 | 94.2 | 27000 | 14142.743 |  | 1
115 | 115 | 57 | -4.3353 | 802000 | 1467280 | 93.8 | 27000 | 14142.743 |  | 1
115 | 115 | 75 | 15.3648 | 1039000 | 1459455 | 96.5 | 31500 | 20679.6201 |  | 1
115 | 115 | 72 | 11.5424 | 992000 | 1590837.5 | 95.6 | 31500 | 20679.6201 |  | 1
115 | 115 | 67 | 5.6915 | 914000 | 1754965 | 94.5 | 31500 | 20679.6201 |  | 1
115 | 115 | 62 | 0.42275 | 839000 | 1815327.5 | 94.1 | 31500 | 20679.6201 |  | 1
115 | 115 | 57 | -4.3353 | 837000 | 1528267.5 | 94 | 31500 | 20679.6201 |  | 1
75 | 75 | 75 | 100 | 1251000 | 394000 | 64.3 | 36000 | 25095.1899 |  | 1
75 | 75 | 72 | 86.8609 | 1195000 | 493100 | 63.2 | 36000 | 25095.1899 |  | 1
75 | 75 | 67 | 66.7494 | 1109000 | 666120 | 61.4 | 36000 | 25095.1899 |  | 1
75 | 75 | 62 | 48.6386 | 1023000 | 822080 | 59.9 | 36000 | 25095.1899 |  | 1
75 | 75 | 57 | 32.2833 | 1004000 | 886640 | 59.6 | 36000 | 25095.1899 |  | 1
85 | 85 | 75 | 63.5688 | 1208000 | 688980 | 70.7 | 36000 | 25095.1899 |  | 1
85 | 85 | 72 | 54.0993 | 1153000 | 803900 | 69.6 | 36000 | 25095.1899 |  | 1
85 | 85 | 67 | 39.6049 | 1070000 | 980880 | 68.1 | 36000 | 25095.1899 |  | 1
85 | 85 | 62 | 26.5524 | 986000 | 1120940 | 66.7 | 36000 | 25095.1899 |  | 1
85 | 85 | 57 | 14.765 | 974000 | 1087400 | 66.4 | 36000 | 25095.1899 |  | 1
95 | 95 | 75 | 40.2091 | 1161000 | 994200 | 78.3 | 36000 | 25095.1899 |  | 1
95 | 95 | 72 | 33.2947 | 1110000 | 1119020 | 77.3 | 36000 | 25095.1899 |  | 1
95 | 95 | 67 | 22.7111 | 1027000 | 1298960 | 75.8 | 36000 | 25095.1899 |  | 1
95 | 95 | 62 | 13.1803 | 948000 | 1392320 | 74.4 | 36000 | 25095.1899 |  | 1
95 | 95 | 57 | 4.5734 | 942000 | 1274640 | 74.3 | 36000 | 25095.1899 |  | 1
105 | 105 | 75 | 25.1345 | 1110000 | 1304900 | 87 | 36000 | 25095.1899 |  | 1
105 | 105 | 72 | 20.0232 | 1061000 | 1430700 | 86.1 | 36000 | 25095.1899 |  | 1
105 | 105 | 67 | 12.1996 | 980000 | 1612600 | 84.6 | 36000 | 25095.1899 |  | 1
105 | 105 | 62 | 5.1542 | 908000 | 1651400 | 83.2 | 36000 | 25095.1899 |  | 1
105 | 105 | 57 | -1.2082 | 905000 | 1439600 | 83.2 | 36000 | 25095.1899 |  | 1
115 | 115 | 75 | 15.3648 | 1052000 | 1621520 | 96.8 | 36000 | 25095.1899 |  | 1
115 | 115 | 72 | 11.5424 | 1005000 | 1739380 | 96 | 36000 | 25095.1899 |  | 1
115 | 115 | 67 | 5.6915 | 927000 | 1926240 | 94.8 | 36000 | 25095.1899 |  | 1
115 | 115 | 62 | 0.42275 | 867000 | 1871780 | 94.2 | 36000 | 25095.1899 |  | 1
115 | 115 | 57 | -4.3353 | 864000 | 1584720 | 94.3 | 36000 | 25095.1899 |  | 1
75 | 75 | 75 | 100 | 1177000 | 423900 | 63.2 | 18000 | 5757.5363 |  | 2
75 | 75 | 72 | 86.8609 | 1117000 | 460590 | 62 | 18000 | 5757.5363 |  | 2
75 | 75 | 67 | 66.7494 | 1025000 | 575388 | 60 | 18000 | 5757.5363 |  | 2
75 | 75 | 62 | 48.6386 | 946000 | 680016 | 58.4 | 18000 | 5757.5363 |  | 2
75 | 75 | 57 | 32.2833 | 870000 | 770388 | 57 | 18000 | 5757.5363 |  | 2
75 | 75 | 75 | 100 | 1238000 | 434375 | 64.6 | 22500 | 9252.067 |  | 2
75 | 75 | 72 | 86.8609 | 1176000 | 487095 | 63.2 | 22500 | 9252.067 |  | 2
75 | 75 | 67 | 66.7494 | 1081000 | 626235 | 61.2 | 22500 | 9252.067 |  | 2
75 | 75 | 62 | 48.6386 | 999000 | 752235 | 59.5 | 22500 | 9252.067 |  | 2
75 | 75 | 57 | 32.2833 | 929000 | 814237.5 | 58.1 | 22500 | 9252.067 |  | 2
75 | 75 | 75 | 100 | 1279000 | 413885 | 65.4 | 27000 | 14142.743 |  | 2
75 | 75 | 72 | 86.8609 | 1214000 | 516198 | 64.1 | 27000 | 14142.743 |  | 2
75 | 75 | 67 | 66.7494 | 1119000 | 668140 | 62 | 27000 | 14142.743 |  | 2
75 | 75 | 62 | 48.6386 | 1036000 | 814140 | 60.2 | 27000 | 14142.743 |  | 2
75 | 75 | 57 | 32.2833 | 984000 | 869250 | 59.2 | 27000 | 14142.743 |  | 2
75 | 75 | 75 | 100 | 1309000 | 414335 | 66.1 | 31500 | 20679.6201 |  | 2
75 | 75 | 72 | 86.8609 | 1246000 | 531132 | 64.7 | 31500 | 20679.6201 |  | 2
75 | 75 | 67 | 66.7494 | 1147000 | 705731 | 62.6 | 31500 | 20679.6201 |  | 2
75 | 75 | 62 | 48.6386 | 1061000 | 863132 | 60.8 | 31500 | 20679.6201 |  | 2
75 | 75 | 57 | 32.2833 | 1031000 | 910985 | 60.2 | 31500 | 20679.6201 |  | 2
85 | 85 | 75 | 63.5688 | 1138000 | 527100 | 69.7 | 18000 | 5757.5363 |  | 2
85 | 85 | 72 | 54.0993 | 1081000 | 619380 | 68.4 | 18000 | 5757.5363 |  | 2
85 | 85 | 67 | 39.6049 | 1000000 | 708612 | 66.6 | 18000 | 5757.5363 |  | 2
85 | 85 | 62 | 26.5524 | 922000 | 807984 | 65.1 | 18000 | 5757.5363 |  | 2
85 | 85 | 57 | 14.765 | 846000 | 900612 | 63.8 | 18000 | 5757.5363 |  | 2
85 | 85 | 75 | 63.5688 | 1191000 | 573625 | 70.9 | 22500 | 9252.067 |  | 2
85 | 85 | 72 | 54.0993 | 1133000 | 675620 | 69.6 | 22500 | 9252.067 |  | 2
85 | 85 | 67 | 39.6049 | 1051000 | 794765 | 67.8 | 22500 | 9252.067 |  | 2
85 | 85 | 62 | 26.5524 | 971000 | 917480 | 66.2 | 22500 | 9252.067 |  | 2
85 | 85 | 57 | 14.765 | 908000 | 1014762.5 | 64.9 | 22500 | 9252.067 |  | 2
85 | 85 | 75 | 63.5688 | 1228000 | 656085 | 71.7 | 27000 | 14142.743 |  | 2
85 | 85 | 72 | 54.0993 | 1167000 | 732802 | 70.4 | 27000 | 14142.743 |  | 2
85 | 85 | 67 | 39.6049 | 1087000 | 880860 | 68.6 | 27000 | 14142.743 |  | 2
85 | 85 | 62 | 26.5524 | 1005000 | 1024860 | 66.9 | 27000 | 14142.743 |  | 2
85 | 85 | 57 | 14.765 | 962000 | 1073780 | 65.9 | 27000 | 14142.743 |  | 2
85 | 85 | 75 | 63.5688 | 1255000 | 701066 | 72.3 | 31500 | 20679.6201 |  | 2
85 | 85 | 72 | 54.0993 | 1198000 | 795868 | 71 | 31500 | 20679.6201 |  | 2
85 | 85 | 67 | 39.6049 | 1113000 | 965269 | 69.2 | 31500 | 20679.6201 |  | 2
85 | 85 | 62 | 26.5524 | 1028000 | 1126868 | 67.4 | 31500 | 20679.6201 |  | 2
85 | 85 | 57 | 14.765 | 1006000 | 1124282.5 | 66.9 | 31500 | 20679.6201 |  | 2
95 | 95 | 75 | 40.2091 | 1100000 | 747000 | 77.1 | 18000 | 5757.5363 |  | 2
95 | 95 | 72 | 33.2947 | 1050000 | 791240 | 76 | 18000 | 5757.5363 |  | 2
95 | 95 | 67 | 22.7111 | 971000 | 908120 | 74.4 | 18000 | 5757.5363 |  | 2
95 | 95 | 62 | 13.1803 | 894000 | 1011090 | 73.1 | 18000 | 5757.5363 |  | 2
95 | 95 | 57 | 4.5734 | 819000 | 1092150 | 71.5 | 18000 | 5757.5363 |  | 2
95 | 95 | 75 | 40.2091 | 1151000 | 791137.5 | 78.3 | 22500 | 9252.067 |  | 2
95 | 95 | 72 | 33.2947 | 1092000 | 908975 | 77 | 22500 | 9252.067 |  | 2
95 | 95 | 67 | 22.7111 | 1018000 | 1046400 | 75.5 | 22500 | 9252.067 |  | 2
95 | 95 | 62 | 13.1803 | 940000 | 1174112.5 | 74.1 | 22500 | 9252.067 |  | 2
95 | 95 | 57 | 4.5734 | 883000 | 1194850 | 72.7 | 22500 | 9252.067 |  | 2
95 | 95 | 75 | 40.2091 | 1185000 | 910950 | 79.2 | 27000 | 14142.743 |  | 2
95 | 95 | 72 | 33.2947 | 1134000 | 1020770 | 78 | 27000 | 14142.743 |  | 2
95 | 95 | 67 | 22.7111 | 1051000 | 1177225 | 76.3 | 27000 | 14142.743 |  | 2
95 | 95 | 62 | 13.1803 | 971000 | 1318225 | 74.8 | 27000 | 14142.743 |  | 2
95 | 95 | 57 | 4.5734 | 936000 | 1265670 | 73.8 | 27000 | 14142.743 |  | 2
95 | 95 | 75 | 40.2091 | 1208000 | 1007972.5 | 79.8 | 31500 | 20679.6201 |  | 2
95 | 95 | 72 | 33.2947 | 1153000 | 1128565 | 78.5 | 31500 | 20679.6201 |  | 2
95 | 95 | 67 | 22.7111 | 1075000 | 1306762.5 | 76.9 | 31500 | 20679.6201 |  | 2
95 | 95 | 62 | 13.1803 | 994000 | 1446170 | 75.2 | 31500 | 20679.6201 |  | 2
95 | 95 | 57 | 4.5734 | 979000 | 1327232.5 | 74.8 | 31500 | 20679.6201 |  | 2
105 | 105 | 75 | 25.1345 | 1064000 | 929000 | 85.9 | 18000 | 5757.5363 |  | 2
105 | 105 | 72 | 20.0232 | 1014000 | 964350 | 84.9 | 18000 | 5757.5363 |  | 2
105 | 105 | 67 | 12.1996 | 936000 | 1082200 | 83.5 | 18000 | 5757.5363 |  | 2
105 | 105 | 62 | 5.1542 | 858000 | 1191100 | 82.3 | 18000 | 5757.5363 |  | 2
105 | 105 | 57 | -1.2082 | 792000 | 1230450 | 80.5 | 18000 | 5757.5363 |  | 2
105 | 105 | 75 | 25.1345 | 1110000 | 1007312.5 | 87.2 | 22500 | 9252.067 |  | 2
105 | 105 | 72 | 20.0232 | 1060000 | 1128625 | 86.1 | 22500 | 9252.067 |  | 2
105 | 105 | 67 | 12.1996 | 980000 | 1268000 | 84.6 | 22500 | 9252.067 |  | 2
105 | 105 | 62 | 5.1542 | 900000 | 1388000 | 83.3 | 22500 | 9252.067 |  | 2
105 | 105 | 57 | -1.2082 | 854000 | 1355187.5 | 82 | 22500 | 9252.067 |  | 2
105 | 105 | 75 | 25.1345 | 1140000 | 1170675 | 88 | 27000 | 14142.743 |  | 2
105 | 105 | 72 | 20.0232 | 1091000 | 1283950 | 86.9 | 27000 | 14142.743 |  | 2
105 | 105 | 67 | 12.1996 | 1009000 | 1441375 | 85.4 | 27000 | 14142.743 |  | 2
105 | 105 | 62 | 5.1542 | 930000 | 1580375 | 83.9 | 27000 | 14142.743 |  | 2
105 | 105 | 57 | -1.2082 | 905000 | 1439600 | 83.1 | 27000 | 14142.743 |  | 2
105 | 105 | 75 | 25.1345 | 1161000 | 1316950 | 88.5 | 31500 | 20679.6201 |  | 2
105 | 105 | 72 | 20.0232 | 1104000 | 1437275 | 87.1 | 31500 | 20679.6201 |  | 2
105 | 105 | 67 | 12.1996 | 1031000 | 1619937.5 | 86 | 31500 | 20679.6201 |  | 2
105 | 105 | 62 | 5.1542 | 952000 | 1729287.5 | 84.2 | 31500 | 20679.6201 |  | 2
105 | 105 | 57 | -1.2082 | 946000 | 1500400 | 83.9 | 31500 | 20679.6201 |  | 2
115 | 115 | 75 | 15.3648 | 1019000 | 1115000 | 96.1 | 18000 | 5757.5363 |  | 2
115 | 115 | 72 | 11.5424 | 967000 | 1144350 | 94.7 | 18000 | 5757.5363 |  | 2
115 | 115 | 67 | 5.6915 | 893000 | 1260210 | 94.2 | 18000 | 5757.5363 |  | 2
115 | 115 | 62 | 0.42275 | 816000 | 1357210 | 94.4 | 18000 | 5757.5363 |  | 2
115 | 115 | 57 | -4.3353 | 756000 | 1379700 | 92.7 | 18000 | 5757.5363 |  | 2
115 | 115 | 75 | 15.3648 | 1061000 | 1231625 | 97.4 | 22500 | 9252.067 |  | 2
115 | 115 | 72 | 11.5424 | 1012000 | 1342275 | 96.4 | 22500 | 9252.067 |  | 2
115 | 115 | 67 | 5.6915 | 932000 | 1485600 | 95.3 | 22500 | 9252.067 |  | 2
115 | 115 | 62 | 0.42275 | 855000 | 1604600 | 95.2 | 22500 | 9252.067 |  | 2
115 | 115 | 57 | -4.3353 | 820000 | 1495675 | 93.4 | 22500 | 9252.067 |  | 2
115 | 115 | 75 | 15.3648 | 1087000 | 1433340 | 98.2 | 27000 | 14142.743 |  | 2
115 | 115 | 72 | 11.5424 | 1039000 | 1545130 | 97.2 | 27000 | 14142.743 |  | 2
115 | 115 | 67 | 5.6915 | 960000 | 1703525 | 96.1 | 27000 | 14142.743 |  | 2
115 | 115 | 62 | 0.42275 | 882000 | 1829130 | 94.4 | 27000 | 14142.743 |  | 2
115 | 115 | 57 | -4.3353 | 868000 | 1585255 | 94.2 | 27000 | 14142.743 |  | 2
115 | 115 | 75 | 15.3648 | 1108000 | 1617730 | 98.8 | 31500 | 20679.6201 |  | 2
115 | 115 | 72 | 11.5424 | 1059000 | 1744985 | 97.8 | 31500 | 20679.6201 |  | 2
115 | 115 | 67 | 5.6915 | 979000 | 1928112.5 | 96.7 | 31500 | 20679.6201 |  | 2
115 | 115 | 62 | 0.42275 | 910000 | 1954092.5 | 95 | 31500 | 20679.6201 |  | 2
115 | 115 | 57 | -4.3353 | 906000 | 1657905 | 94.8 | 31500 | 20679.6201 |  | 2
75 | 75 | 75 | 100 | 1331000 | 416240 | 66.6 | 36000 | 25095.1899 |  | 2
75 | 75 | 72 | 86.8609 | 1267000 | 550008 | 65.2 | 36000 | 25095.1899 |  | 2
75 | 75 | 67 | 66.7494 | 1169000 | 747264 | 63 | 36000 | 25095.1899 |  | 2
75 | 75 | 62 | 48.6386 | 1081000 | 889240 | 61.2 | 36000 | 25095.1899 |  | 2
75 | 75 | 57 | 32.2833 | 1069000 | 943720 | 61.1 | 36000 | 25095.1899 |  | 2
85 | 85 | 75 | 63.5688 | 1276000 | 746504 | 72.8 | 36000 | 25095.1899 |  | 2
85 | 85 | 72 | 54.0993 | 1218000 | 852992 | 71.5 | 36000 | 25095.1899 |  | 2
85 | 85 | 67 | 39.6049 | 1133000 | 1044736 | 69.6 | 36000 | 25095.1899 |  | 2
85 | 85 | 62 | 26.5524 | 1048000 | 1216780 | 67.8 | 36000 | 25095.1899 |  | 2
85 | 85 | 57 | 14.765 | 1043000 | 1164320 | 67.7 | 36000 | 25095.1899 |  | 2
95 | 95 | 75 | 40.2091 | 1231000 | 1100540 | 80.3 | 36000 | 25095.1899 |  | 2
95 | 95 | 72 | 33.2947 | 1177000 | 1230420 | 79.1 | 36000 | 25095.1899 |  | 2
95 | 95 | 67 | 22.7111 | 1093000 | 1431360 | 77.4 | 36000 | 25095.1899 |  | 2
95 | 95 | 62 | 13.1803 | 1017000 | 1511900 | 75.6 | 36000 | 25095.1899 |  | 2
95 | 95 | 57 | 4.5734 | 1014000 | 1370400 | 75.6 | 36000 | 25095.1899 |  | 2
105 | 105 | 75 | 25.1345 | 1182000 | 1444900 | 89.1 | 36000 | 25095.1899 |  | 2
105 | 105 | 72 | 20.0232 | 1129000 | 1581700 | 88 | 36000 | 25095.1899 |  | 2
105 | 105 | 67 | 12.1996 | 1047000 | 1785600 | 86.4 | 36000 | 25095.1899 |  | 2
105 | 105 | 62 | 5.1542 | 983000 | 1779800 | 84.8 | 36000 | 25095.1899 |  | 2
105 | 105 | 57 | -1.2082 | 979000 | 1553200 | 84.7 | 36000 | 25095.1899 |  | 2
115 | 115 | 75 | 15.3648 | 1126000 | 1801120 | 99.5 | 36000 | 25095.1899 |  | 2
115 | 115 | 72 | 11.5424 | 1073000 | 1930980 | 98.3 | 36000 | 25095.1899 |  | 2
115 | 115 | 67 | 5.6915 | 993000 | 2134840 | 97.4 | 36000 | 25095.1899 |  | 2
115 | 115 | 62 | 0.42275 | 938000 | 2046800 | 95.3 | 36000 | 25095.1899 |  | 2
115 | 115 | 57 | -4.3353 | 937000 | 1713160 | 95.3 | 36000 | 25095.1899 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 10
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
75 | 75 | 75 | 100 | 1198000 | 420000 | 68.6 | 20000 | 7141.1788 |  | 1
75 | 75 | 72 | 86.8609 | 1147000 | 480000 | 67.4 | 20000 | 7141.1788 |  | 1
75 | 75 | 67 | 66.7494 | 1057000 | 569200 | 65.6 | 20000 | 7141.1788 |  | 1
75 | 75 | 62 | 48.6386 | 970000 | 670900 | 64.1 | 20000 | 7141.1788 |  | 1
75 | 75 | 57 | 32.2833 | 883000 | 759100 | 62.7 | 20000 | 7141.1788 |  | 1
75 | 75 | 75 | 100 | 1251000 | 422750 | 69.9 | 25000 | 11785.9665 |  | 1
75 | 75 | 72 | 86.8609 | 1194000 | 488125 | 68.5 | 25000 | 11785.9665 |  | 1
75 | 75 | 67 | 66.7494 | 1104000 | 609750 | 66.6 | 25000 | 11785.9665 |  | 1
75 | 75 | 62 | 48.6386 | 1017000 | 736000 | 65 | 25000 | 11785.9665 |  | 1
75 | 75 | 57 | 32.2833 | 944000 | 821750 | 63.7 | 25000 | 11785.9665 |  | 1
75 | 75 | 75 | 100 | 1285000 | 391000 | 70.8 | 30000 | 18262.4134 |  | 1
75 | 75 | 72 | 86.8609 | 1228000 | 499550 | 69.3 | 30000 | 18262.4134 |  | 1
75 | 75 | 67 | 66.7494 | 1138000 | 646950 | 67.4 | 30000 | 18262.4134 |  | 1
75 | 75 | 62 | 48.6386 | 1050000 | 794300 | 65.7 | 30000 | 18262.4134 |  | 1
75 | 75 | 57 | 32.2833 | 991000 | 873400 | 64.7 | 30000 | 18262.4134 |  | 1
85 | 85 | 75 | 63.5688 | 1161000 | 544000 | 75.7 | 20000 | 7141.1788 |  | 1
85 | 85 | 72 | 54.0993 | 1111000 | 634200 | 74.6 | 20000 | 7141.1788 |  | 1
85 | 85 | 67 | 39.6049 | 1023000 | 741800 | 72.9 | 20000 | 7141.1788 |  | 1
85 | 85 | 62 | 26.5524 | 938000 | 850200 | 71.5 | 20000 | 7141.1788 |  | 1
85 | 85 | 57 | 14.765 | 855000 | 926800 | 70.2 | 20000 | 7141.1788 |  | 1
85 | 85 | 75 | 63.5688 | 1209000 | 576250 | 77 | 25000 | 11785.9665 |  | 1
85 | 85 | 72 | 54.0993 | 1155000 | 688000 | 75.7 | 25000 | 11785.9665 |  | 1
85 | 85 | 67 | 39.6049 | 1068000 | 828250 | 73.9 | 25000 | 11785.9665 |  | 1
85 | 85 | 62 | 26.5524 | 982000 | 960000 | 72.4 | 25000 | 11785.9665 |  | 1
85 | 85 | 57 | 14.765 | 923000 | 991375 | 71.2 | 25000 | 11785.9665 |  | 1
85 | 85 | 75 | 63.5688 | 1238000 | 668300 | 77.8 | 30000 | 18262.4134 |  | 1
85 | 85 | 72 | 54.0993 | 1186000 | 751100 | 76.5 | 30000 | 18262.4134 |  | 1
85 | 85 | 67 | 39.6049 | 1099000 | 910050 | 74.6 | 30000 | 18262.4134 |  | 1
85 | 85 | 62 | 26.5524 | 1012000 | 1057700 | 73 | 30000 | 18262.4134 |  | 1
85 | 85 | 57 | 14.765 | 975000 | 1053050 | 72.2 | 30000 | 18262.4134 |  | 1
95 | 95 | 75 | 40.2091 | 1121000 | 787000 | 84.1 | 20000 | 7141.1788 |  | 1
95 | 95 | 72 | 33.2947 | 1071000 | 825600 | 83 | 20000 | 7141.1788 |  | 1
95 | 95 | 67 | 22.7111 | 985000 | 919100 | 81.4 | 20000 | 7141.1788 |  | 1
95 | 95 | 62 | 13.1803 | 902000 | 1032000 | 80 | 20000 | 7141.1788 |  | 1
95 | 95 | 57 | 4.5734 | 825000 | 1091500 | 79.3 | 20000 | 7141.1788 |  | 1
95 | 95 | 75 | 40.2091 | 1164000 | 834750 | 85.2 | 25000 | 11785.9665 |  | 1
95 | 95 | 72 | 33.2947 | 1113000 | 902250 | 84.1 | 25000 | 11785.9665 |  | 1
95 | 95 | 67 | 22.7111 | 1027000 | 1053875 | 82.4 | 25000 | 11785.9665 |  | 1
95 | 95 | 62 | 13.1803 | 942000 | 1184000 | 80.8 | 25000 | 11785.9665 |  | 1
95 | 95 | 57 | 4.5734 | 893000 | 1167000 | 79.7 | 25000 | 11785.9665 |  | 1
95 | 95 | 75 | 40.2091 | 1191000 | 862400 | 86 | 30000 | 18262.4134 |  | 1
95 | 95 | 72 | 33.2947 | 1141000 | 1012850 | 84.8 | 30000 | 18262.4134 |  | 1
95 | 95 | 67 | 22.7111 | 1056000 | 1179700 | 83.1 | 30000 | 18262.4134 |  | 1
95 | 95 | 62 | 13.1803 | 970000 | 1321700 | 81.5 | 30000 | 18262.4134 |  | 1
95 | 95 | 57 | 4.5734 | 933000 | 1264650 | 80.8 | 30000 | 18262.4134 |  | 1
105 | 105 | 75 | 25.1345 | 1077000 | 986000 | 93.7 | 20000 | 7141.1788 |  | 1
105 | 105 | 72 | 20.0232 | 1026000 | 1017500 | 92.7 | 20000 | 7141.1788 |  | 1
105 | 105 | 67 | 12.1996 | 942000 | 1097000 | 91.4 | 20000 | 7141.1788 |  | 1
105 | 105 | 62 | 5.1542 | 861000 | 1211000 | 90.5 | 20000 | 7141.1788 |  | 1
105 | 105 | 57 | -1.2082 | 796000 | 1215000 | 89.8 | 20000 | 7141.1788 |  | 1
105 | 105 | 75 | 25.1345 | 1113000 | 1082750 | 94.7 | 25000 | 11785.9665 |  | 1
105 | 105 | 72 | 20.0232 | 1064000 | 1117625 | 93.7 | 25000 | 11785.9665 |  | 1
105 | 105 | 67 | 12.1996 | 981000 | 1274125 | 92.1 | 25000 | 11785.9665 |  | 1
105 | 105 | 62 | 5.1542 | 899000 | 1405000 | 91.3 | 25000 | 11785.9665 |  | 1
105 | 105 | 57 | -1.2082 | 849000 | 1349875 | 90.9 | 25000 | 11785.9665 |  | 1
105 | 105 | 75 | 25.1345 | 1139000 | 1125250 | 95.4 | 30000 | 18262.4134 |  | 1
105 | 105 | 72 | 20.0232 | 1090000 | 1278000 | 94.3 | 30000 | 18262.4134 |  | 1
105 | 105 | 67 | 12.1996 | 1007000 | 1444500 | 92.7 | 30000 | 18262.4134 |  | 1
105 | 105 | 62 | 5.1542 | 924000 | 1573250 | 91.9 | 30000 | 18262.4134 |  | 1
105 | 105 | 57 | -1.2082 | 897000 | 1425000 | 91.4 | 30000 | 18262.4134 |  | 1
115 | 115 | 75 | 15.3648 | 1025000 | 1187000 | 104.6 | 20000 | 7141.1788 |  | 1
115 | 115 | 72 | 11.5424 | 976000 | 1118400 | 103.9 | 20000 | 7141.1788 |  | 1
115 | 115 | 67 | 5.6915 | 895000 | 1278300 | 103.4 | 20000 | 7141.1788 |  | 1
115 | 115 | 62 | 0.42275 | 817000 | 1395700 | 103.4 | 20000 | 7141.1788 |  | 1
115 | 115 | 57 | -4.3353 | 759000 | 1355300 | 103.1 | 20000 | 7141.1788 |  | 1
115 | 115 | 75 | 15.3648 | 1057000 | 1332500 | 105.4 | 25000 | 11785.9665 |  | 1
115 | 115 | 72 | 11.5424 | 1010000 | 1346125 | 104.6 | 25000 | 11785.9665 |  | 1
115 | 115 | 67 | 5.6915 | 930000 | 1503000 | 103.9 | 25000 | 11785.9665 |  | 1
115 | 115 | 62 | 0.42275 | 851000 | 1625000 | 103.9 | 25000 | 11785.9665 |  | 1
115 | 115 | 57 | -4.3353 | 812000 | 1485750 | 103.8 | 25000 | 11785.9665 |  | 1
115 | 115 | 75 | 15.3648 | 1080000 | 1395000 | 106.1 | 30000 | 18262.4134 |  | 1
115 | 115 | 72 | 11.5424 | 1034000 | 1535200 | 105.3 | 30000 | 18262.4134 |  | 1
115 | 115 | 67 | 5.6915 | 954000 | 1708300 | 104.3 | 30000 | 18262.4134 |  | 1
115 | 115 | 62 | 0.42275 | 875000 | 1799650 | 104.1 | 30000 | 18262.4134 |  | 1
115 | 115 | 57 | -4.3353 | 858000 | 1562550 | 104 | 30000 | 18262.4134 |  | 1
75 | 75 | 75 | 100 | 1310000 | 421875 | 71.4 | 35000 | 27101.8883 |  | 1
75 | 75 | 72 | 86.8609 | 1252000 | 514475 | 70 | 35000 | 27101.8883 |  | 1
75 | 75 | 67 | 66.7494 | 1162000 | 682700 | 68 | 35000 | 27101.8883 |  | 1
75 | 75 | 62 | 48.6386 | 1073000 | 846625 | 66.2 | 35000 | 27101.8883 |  | 1
75 | 75 | 57 | 32.2833 | 1038000 | 916200 | 65.5 | 35000 | 27101.8883 |  | 1
75 | 75 | 75 | 100 | 1329000 | 418400 | 71.9 | 40000 | 38473.1788 |  | 1
75 | 75 | 72 | 86.8609 | 1273000 | 528400 | 70.5 | 40000 | 38473.1788 |  | 1
75 | 75 | 67 | 66.7494 | 1181000 | 717000 | 68.4 | 40000 | 38473.1788 |  | 1
75 | 75 | 62 | 48.6386 | 1092000 | 886800 | 66.6 | 40000 | 38473.1788 |  | 1
75 | 75 | 57 | 32.2833 | 1074000 | 948000 | 66.2 | 40000 | 38473.1788 |  | 1
85 | 85 | 75 | 63.5688 | 1260000 | 687975 | 78.4 | 35000 | 27101.8883 |  | 1
85 | 85 | 72 | 54.0993 | 1206000 | 810450 | 77.1 | 35000 | 27101.8883 |  | 1
85 | 85 | 67 | 39.6049 | 1121000 | 988300 | 75.2 | 35000 | 27101.8883 |  | 1
85 | 85 | 62 | 26.5524 | 1034000 | 1136450 | 73.5 | 35000 | 27101.8883 |  | 1
85 | 85 | 57 | 14.765 | 1007000 | 1124950 | 72.9 | 35000 | 27101.8883 |  | 1
85 | 85 | 75 | 63.5688 | 1278000 | 735800 | 78.9 | 40000 | 38473.1788 |  | 1
85 | 85 | 72 | 54.0993 | 1224000 | 866800 | 77.5 | 40000 | 38473.1788 |  | 1
85 | 85 | 67 | 39.6049 | 1139000 | 1063000 | 75.6 | 40000 | 38473.1788 |  | 1
85 | 85 | 62 | 26.5524 | 1054000 | 1202000 | 73.9 | 40000 | 38473.1788 |  | 1
85 | 85 | 57 | 14.765 | 1044000 | 1165600 | 73.6 | 40000 | 38473.1788 |  | 1
95 | 95 | 75 | 40.2091 | 1212000 | 974675 | 86.6 | 35000 | 27101.8883 |  | 1
95 | 95 | 72 | 33.2947 | 1160000 | 1117325 | 85.3 | 35000 | 27101.8883 |  | 1
95 | 95 | 67 | 22.7111 | 1077000 | 1295100 | 83.6 | 35000 | 27101.8883 |  | 1
95 | 95 | 62 | 13.1803 | 992000 | 1418775 | 81.9 | 35000 | 27101.8883 |  | 1
95 | 95 | 57 | 4.5734 | 973000 | 1319500 | 81.5 | 35000 | 27101.8883 |  | 1
95 | 95 | 75 | 40.2091 | 1228000 | 1067800 | 87 | 40000 | 38473.1788 |  | 1
95 | 95 | 72 | 33.2947 | 1177000 | 1212200 | 85.8 | 40000 | 38473.1788 |  | 1
95 | 95 | 67 | 22.7111 | 1093000 | 1412800 | 84 | 40000 | 38473.1788 |  | 1
95 | 95 | 62 | 13.1803 | 1014000 | 1487000 | 82.3 | 40000 | 38473.1788 |  | 1
95 | 95 | 57 | 4.5734 | 1006000 | 1362400 | 82.2 | 40000 | 38473.1788 |  | 1
105 | 105 | 75 | 25.1345 | 1158000 | 1273375 | 95.9 | 35000 | 27101.8883 |  | 1
105 | 105 | 72 | 20.0232 | 1108000 | 1418875 | 94.8 | 35000 | 27101.8883 |  | 1
105 | 105 | 67 | 12.1996 | 1026000 | 1609125 | 93.2 | 35000 | 27101.8883 |  | 1
105 | 105 | 62 | 5.1542 | 947000 | 1696000 | 92.2 | 35000 | 27101.8883 |  | 1
105 | 105 | 57 | -1.2082 | 937000 | 1485625 | 91.7 | 35000 | 27101.8883 |  | 1
105 | 105 | 75 | 25.1345 | 1173000 | 1405000 | 96.4 | 40000 | 38473.1788 |  | 1
105 | 105 | 72 | 20.0232 | 1123000 | 1555000 | 95.3 | 40000 | 38473.1788 |  | 1
105 | 105 | 67 | 12.1996 | 1041000 | 1758000 | 93.6 | 40000 | 38473.1788 |  | 1
105 | 105 | 62 | 5.1542 | 970000 | 1763000 | 92.5 | 40000 | 38473.1788 |  | 1
105 | 105 | 57 | -1.2082 | 967000 | 1539000 | 92.4 | 40000 | 38473.1788 |  | 1
115 | 115 | 75 | 15.3648 | 1098000 | 1586475 | 106.6 | 35000 | 27101.8883 |  | 1
115 | 115 | 72 | 11.5424 | 1050000 | 1731900 | 105.7 | 35000 | 27101.8883 |  | 1
115 | 115 | 67 | 5.6915 | 972000 | 1915375 | 104.7 | 35000 | 27101.8883 |  | 1
115 | 115 | 62 | 0.42275 | 901000 | 1906100 | 104 | 35000 | 27101.8883 |  | 1
115 | 115 | 57 | -4.3353 | 894000 | 1635125 | 104.2 | 35000 | 27101.8883 |  | 1
115 | 115 | 75 | 15.3648 | 1110000 | 1749000 | 107 | 40000 | 38473.1788 |  | 1
115 | 115 | 72 | 11.5424 | 1063000 | 1911200 | 106.1 | 40000 | 38473.1788 |  | 1
115 | 115 | 67 | 5.6915 | 985000 | 2102200 | 104.9 | 40000 | 38473.1788 |  | 1
115 | 115 | 62 | 0.42275 | 923000 | 2016400 | 104.4 | 40000 | 38473.1788 |  | 1
115 | 115 | 57 | -4.3353 | 922000 | 1676600 | 104.5 | 40000 | 38473.1788 |  | 1
75 | 75 | 75 | 100 | 1269000 | 455000 | 71.2 | 20000 | 7141.1788 |  | 2
75 | 75 | 72 | 86.8609 | 1208000 | 507400 | 69.7 | 20000 | 7141.1788 |  | 2
75 | 75 | 67 | 66.7494 | 1114000 | 623400 | 67.3 | 20000 | 7141.1788 |  | 2
75 | 75 | 62 | 48.6386 | 1026000 | 742240 | 65.4 | 20000 | 7141.1788 |  | 2
75 | 75 | 57 | 32.2833 | 941000 | 823480 | 63.7 | 20000 | 7141.1788 |  | 2
75 | 75 | 75 | 100 | 1332000 | 429250 | 72.9 | 25000 | 11785.9665 |  | 2
75 | 75 | 72 | 86.8609 | 1267000 | 524550 | 71.1 | 25000 | 11785.9665 |  | 2
75 | 75 | 67 | 66.7494 | 1171000 | 677500 | 68.7 | 25000 | 11785.9665 |  | 2
75 | 75 | 62 | 48.6386 | 1081000 | 819150 | 66.6 | 25000 | 11785.9665 |  | 2
75 | 75 | 57 | 32.2833 | 1010000 | 886125 | 65 | 25000 | 11785.9665 |  | 2
75 | 75 | 75 | 100 | 1373000 | 444300 | 73.9 | 30000 | 18262.4134 |  | 2
75 | 75 | 72 | 86.8609 | 1308000 | 546460 | 72.2 | 30000 | 18262.4134 |  | 2
75 | 75 | 67 | 66.7494 | 1210000 | 722220 | 69.7 | 30000 | 18262.4134 |  | 2
75 | 75 | 62 | 48.6386 | 1118000 | 880220 | 67.5 | 30000 | 18262.4134 |  | 2
75 | 75 | 57 | 32.2833 | 1069000 | 944800 | 66.4 | 30000 | 18262.4134 |  | 2
85 | 85 | 75 | 63.5688 | 1231000 | 574000 | 78.3 | 20000 | 7141.1788 |  | 2
85 | 85 | 72 | 54.0993 | 1172000 | 674100 | 76.7 | 20000 | 7141.1788 |  | 2
85 | 85 | 67 | 39.6049 | 1084000 | 777600 | 74.6 | 20000 | 7141.1788 |  | 2
85 | 85 | 62 | 26.5524 | 998000 | 882760 | 72.8 | 20000 | 7141.1788 |  | 2
85 | 85 | 57 | 14.765 | 916000 | 980440 | 71.1 | 20000 | 7141.1788 |  | 2
85 | 85 | 75 | 63.5688 | 1285000 | 648800 | 79.7 | 25000 | 11785.9665 |  | 2
85 | 85 | 72 | 54.0993 | 1227000 | 737800 | 78.3 | 25000 | 11785.9665 |  | 2
85 | 85 | 67 | 39.6049 | 1136000 | 871500 | 75.9 | 25000 | 11785.9665 |  | 2
85 | 85 | 62 | 26.5524 | 1048000 | 1004850 | 74.1 | 25000 | 11785.9665 |  | 2
85 | 85 | 57 | 14.765 | 987000 | 1090125 | 72.5 | 25000 | 11785.9665 |  | 2
85 | 85 | 75 | 63.5688 | 1324000 | 712000 | 80.8 | 30000 | 18262.4134 |  | 2
85 | 85 | 72 | 54.0993 | 1265000 | 804160 | 79.2 | 30000 | 18262.4134 |  | 2
85 | 85 | 67 | 39.6049 | 1173000 | 961400 | 76.9 | 30000 | 18262.4134 |  | 2
85 | 85 | 62 | 26.5524 | 1083000 | 1122780 | 74.9 | 30000 | 18262.4134 |  | 2
85 | 85 | 57 | 14.765 | 1043000 | 1165550 | 73.8 | 30000 | 18262.4134 |  | 2
95 | 95 | 75 | 40.2091 | 1189000 | 818000 | 86.5 | 20000 | 7141.1788 |  | 2
95 | 95 | 72 | 33.2947 | 1136000 | 860000 | 85.1 | 20000 | 7141.1788 |  | 2
95 | 95 | 67 | 22.7111 | 1049000 | 994800 | 83.2 | 20000 | 7141.1788 |  | 2
95 | 95 | 62 | 13.1803 | 963000 | 1108100 | 81.5 | 20000 | 7141.1788 |  | 2
95 | 95 | 57 | 4.5734 | 887000 | 1174600 | 80.1 | 20000 | 7141.1788 |  | 2
95 | 95 | 75 | 40.2091 | 1241000 | 909750 | 88 | 25000 | 11785.9665 |  | 2
95 | 95 | 72 | 33.2947 | 1183000 | 992625 | 86.5 | 25000 | 11785.9665 |  | 2
95 | 95 | 67 | 22.7111 | 1097000 | 1142875 | 84.5 | 25000 | 11785.9665 |  | 2
95 | 95 | 62 | 13.1803 | 1010000 | 1281000 | 82.7 | 25000 | 11785.9665 |  | 2
95 | 95 | 57 | 4.5734 | 955000 | 1293250 | 81.3 | 25000 | 11785.9665 |  | 2
95 | 95 | 75 | 40.2091 | 1275000 | 997500 | 89 | 30000 | 18262.4134 |  | 2
95 | 95 | 72 | 33.2947 | 1221000 | 1113350 | 87.6 | 30000 | 18262.4134 |  | 2
95 | 95 | 67 | 22.7111 | 1131000 | 1289250 | 85.5 | 30000 | 18262.4134 |  | 2
95 | 95 | 62 | 13.1803 | 1041000 | 1436300 | 83.4 | 30000 | 18262.4134 |  | 2
95 | 95 | 57 | 4.5734 | 1012000 | 1368400 | 82.5 | 30000 | 18262.4134 |  | 2
105 | 105 | 75 | 25.1345 | 1147000 | 1023000 | 96.1 | 20000 | 7141.1788 |  | 2
105 | 105 | 72 | 20.0232 | 1090000 | 1056500 | 94.7 | 20000 | 7141.1788 |  | 2
105 | 105 | 67 | 12.1996 | 1007000 | 1187000 | 93.3 | 20000 | 7141.1788 |  | 2
105 | 105 | 62 | 5.1542 | 923000 | 1301500 | 92.4 | 20000 | 7141.1788 |  | 2
105 | 105 | 57 | -1.2082 | 853000 | 1349500 | 90.6 | 20000 | 7141.1788 |  | 2
105 | 105 | 75 | 25.1345 | 1193000 | 1104125 | 97.6 | 25000 | 11785.9665 |  | 2
105 | 105 | 72 | 20.0232 | 1139000 | 1231375 | 96.3 | 25000 | 11785.9665 |  | 2
105 | 105 | 67 | 12.1996 | 1051000 | 1391000 | 94.6 | 25000 | 11785.9665 |  | 2
105 | 105 | 62 | 5.1542 | 965000 | 1523000 | 93.4 | 25000 | 11785.9665 |  | 2
105 | 105 | 57 | -1.2082 | 921000 | 1464125 | 92.2 | 25000 | 11785.9665 |  | 2
105 | 105 | 75 | 25.1345 | 1224000 | 1285750 | 98.6 | 30000 | 18262.4134 |  | 2
105 | 105 | 72 | 20.0232 | 1170000 | 1402250 | 97.3 | 30000 | 18262.4134 |  | 2
105 | 105 | 67 | 12.1996 | 1082000 | 1583750 | 95.5 | 30000 | 18262.4134 |  | 2
105 | 105 | 62 | 5.1542 | 995000 | 1712250 | 94 | 30000 | 18262.4134 |  | 2
105 | 105 | 57 | -1.2082 | 975000 | 1552500 | 93 | 30000 | 18262.4134 |  | 2
115 | 115 | 75 | 15.3648 | 1095000 | 1163400 | 107.2 | 20000 | 7141.1788 |  | 2
115 | 115 | 72 | 11.5424 | 1043000 | 1242100 | 106.4 | 20000 | 7141.1788 |  | 2
115 | 115 | 67 | 5.6915 | 959000 | 1377200 | 105.6 | 20000 | 7141.1788 |  | 2
115 | 115 | 62 | 0.42275 | 877000 | 1492900 | 105.4 | 20000 | 7141.1788 |  | 2
115 | 115 | 57 | -4.3353 | 817000 | 1493600 | 104 | 20000 | 7141.1788 |  | 2
115 | 115 | 75 | 15.3648 | 1137000 | 1353250 | 108.8 | 25000 | 11785.9665 |  | 2
115 | 115 | 72 | 11.5424 | 1085000 | 1476750 | 107.9 | 25000 | 11785.9665 |  | 2
115 | 115 | 67 | 5.6915 | 999000 | 1634000 | 106.7 | 25000 | 11785.9665 |  | 2
115 | 115 | 62 | 0.42275 | 915000 | 1753375 | 106.4 | 25000 | 11785.9665 |  | 2
115 | 115 | 57 | -4.3353 | 883000 | 1614500 | 104.6 | 25000 | 11785.9665 |  | 2
115 | 115 | 75 | 15.3648 | 1166000 | 1578600 | 109.9 | 30000 | 18262.4134 |  | 2
115 | 115 | 72 | 11.5424 | 1113000 | 1699700 | 108.8 | 30000 | 18262.4134 |  | 2
115 | 115 | 67 | 5.6915 | 1027000 | 1875250 | 107.6 | 30000 | 18262.4134 |  | 2
115 | 115 | 62 | 0.42275 | 945000 | 1963050 | 106.5 | 30000 | 18262.4134 |  | 2
115 | 115 | 57 | -4.3353 | 933000 | 1706850 | 105.5 | 30000 | 18262.4134 |  | 2
75 | 75 | 75 | 100 | 1402000 | 443075 | 74.7 | 35000 | 27101.8883 |  | 2
75 | 75 | 72 | 86.8609 | 1337000 | 572480 | 73 | 35000 | 27101.8883 |  | 2
75 | 75 | 67 | 66.7494 | 1239000 | 767590 | 70.4 | 35000 | 27101.8883 |  | 2
75 | 75 | 62 | 48.6386 | 1144000 | 919260 | 68.2 | 35000 | 27101.8883 |  | 2
75 | 75 | 57 | 32.2833 | 1118000 | 986575 | 67.6 | 35000 | 27101.8883 |  | 2
75 | 75 | 75 | 100 | 1426000 | 443600 | 75.3 | 40000 | 38473.1788 |  | 2
75 | 75 | 72 | 86.8609 | 1360000 | 584280 | 73.6 | 40000 | 38473.1788 |  | 2
75 | 75 | 67 | 66.7494 | 1260000 | 805120 | 71 | 40000 | 38473.1788 |  | 2
75 | 75 | 62 | 48.6386 | 1170000 | 959200 | 68.8 | 40000 | 38473.1788 |  | 2
75 | 75 | 57 | 32.2833 | 1159000 | 1024200 | 68.6 | 40000 | 38473.1788 |  | 2
85 | 85 | 75 | 63.5688 | 1351000 | 767850 | 81.6 | 35000 | 27101.8883 |  | 2
85 | 85 | 72 | 54.0993 | 1292000 | 873630 | 80 | 35000 | 27101.8883 |  | 2
85 | 85 | 67 | 39.6049 | 1199000 | 1054410 | 77.6 | 35000 | 27101.8883 |  | 2
85 | 85 | 62 | 26.5524 | 1107000 | 1230740 | 75.5 | 35000 | 27101.8883 |  | 2
85 | 85 | 57 | 14.765 | 1090000 | 1217575 | 74.9 | 35000 | 27101.8883 |  | 2
85 | 85 | 75 | 63.5688 | 1373000 | 819400 | 82.2 | 40000 | 38473.1788 |  | 2
85 | 85 | 72 | 54.0993 | 1313000 | 937720 | 80.6 | 40000 | 38473.1788 |  | 2
85 | 85 | 67 | 39.6049 | 1219000 | 1145880 | 78.2 | 40000 | 38473.1788 |  | 2
85 | 85 | 62 | 26.5524 | 1135000 | 1306400 | 76.1 | 40000 | 38473.1788 |  | 2
85 | 85 | 57 | 14.765 | 1128000 | 1258400 | 75.9 | 40000 | 38473.1788 |  | 2
95 | 95 | 75 | 40.2091 | 1302000 | 1105525 | 89.8 | 35000 | 27101.8883 |  | 2
95 | 95 | 72 | 33.2947 | 1246000 | 1232075 | 88.3 | 35000 | 27101.8883 |  | 2
95 | 95 | 67 | 22.7111 | 1155000 | 1428850 | 86.2 | 35000 | 27101.8883 |  | 2
95 | 95 | 62 | 13.1803 | 1069000 | 1551975 | 84.1 | 35000 | 27101.8883 |  | 2
95 | 95 | 57 | 4.5734 | 1057000 | 1432375 | 83.7 | 35000 | 27101.8883 |  | 2
95 | 95 | 75 | 40.2091 | 1322000 | 1206600 | 90.4 | 40000 | 38473.1788 |  | 2
95 | 95 | 72 | 33.2947 | 1264000 | 1343200 | 88.9 | 40000 | 38473.1788 |  | 2
95 | 95 | 67 | 22.7111 | 1173000 | 1562800 | 86.8 | 40000 | 38473.1788 |  | 2
95 | 95 | 62 | 13.1803 | 1097000 | 1624200 | 84.7 | 40000 | 38473.1788 |  | 2
95 | 95 | 57 | 4.5734 | 1093000 | 1482400 | 84.6 | 40000 | 38473.1788 |  | 2
105 | 105 | 75 | 25.1345 | 1249000 | 1437875 | 99.4 | 35000 | 27101.8883 |  | 2
105 | 105 | 72 | 20.0232 | 1192000 | 1572125 | 98 | 35000 | 27101.8883 |  | 2
105 | 105 | 67 | 12.1996 | 1104000 | 1769750 | 96.2 | 35000 | 27101.8883 |  | 2
105 | 105 | 62 | 5.1542 | 1026000 | 1841375 | 94.4 | 35000 | 27101.8883 |  | 2
105 | 105 | 57 | -1.2082 | 1018000 | 1614750 | 94 | 35000 | 27101.8883 |  | 2
105 | 105 | 75 | 25.1345 | 1266000 | 1589000 | 100 | 40000 | 38473.1788 |  | 2
105 | 105 | 72 | 20.0232 | 1209000 | 1729000 | 98.6 | 40000 | 38473.1788 |  | 2
105 | 105 | 67 | 12.1996 | 1120000 | 1951000 | 96.8 | 40000 | 38473.1788 |  | 2
105 | 105 | 62 | 5.1542 | 1054000 | 1928000 | 94.6 | 40000 | 38473.1788 |  | 2
105 | 105 | 57 | -1.2082 | 1052000 | 1668000 | 94.7 | 40000 | 38473.1788 |  | 2
115 | 115 | 75 | 15.3648 | 1187000 | 1781700 | 110.6 | 35000 | 27101.8883 |  | 2
115 | 115 | 72 | 11.5424 | 1133000 | 1909175 | 109.5 | 35000 | 27101.8883 |  | 2
115 | 115 | 67 | 5.6915 | 1046000 | 2108650 | 108.3 | 35000 | 27101.8883 |  | 2
115 | 115 | 62 | 0.42275 | 976000 | 2116375 | 105.9 | 35000 | 27101.8883 |  | 2
115 | 115 | 57 | -4.3353 | 973000 | 1781500 | 106.2 | 35000 | 27101.8883 |  | 2
115 | 115 | 75 | 15.3648 | 1204000 | 1969400 | 111.5 | 40000 | 38473.1788 |  | 2
115 | 115 | 72 | 11.5424 | 1149000 | 2128200 | 110.2 | 40000 | 38473.1788 |  | 2
115 | 115 | 67 | 5.6915 | 1061000 | 2336200 | 108.6 | 40000 | 38473.1788 |  | 2
115 | 115 | 62 | 0.42275 | 1009000 | 2169400 | 106.8 | 40000 | 38473.1788 |  | 2
115 | 115 | 57 | -4.3353 | 1006000 | 1837600 | 106.9 | 40000 | 38473.1788 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 11
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 12
Degradation Coefficient (C_d)
IEER or SEER
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions