## Table 1
Degradation Coefficient (C_d)
IEER or SEER | 23.3
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 75 | 63 | 52.1129 | 70900 | 48212 | 3.24 | 1500 | 308.5056 |  | 1
65 | 80 | 63 | 39.1676 | 70900 | 56720 | 3.24 | 1500 | 308.5056 |  | 1
65 | 85 | 63 | 29.0563 | 70900 | 63810 | 3.24 | 1500 | 308.5056 |  | 1
65 | 75 | 63 | 52.1129 | 73700 | 51590 | 3.25 | 1750 | 415.4851 |  | 1
65 | 80 | 63 | 39.1676 | 73700 | 61171 | 3.25 | 1750 | 415.4851 |  | 1
65 | 85 | 63 | 29.0563 | 73700 | 70015 | 3.25 | 1750 | 415.4851 |  | 1
65 | 75 | 63 | 52.1129 | 76300 | 56462 | 3.25 | 2050 | 557.4497 |  | 1
65 | 80 | 63 | 39.1676 | 76300 | 67144 | 3.25 | 2050 | 557.4497 |  | 1
65 | 85 | 63 | 29.0563 | 76300 | 76300 | 3.25 | 2050 | 557.4497 |  | 1
65 | 75 | 63 | 52.1129 | 78300 | 60291 | 3.25 | 2300 | 837.6202 |  | 1
65 | 80 | 63 | 39.1676 | 78300 | 72036 | 3.25 | 2300 | 837.6202 |  | 1
65 | 85 | 63 | 29.0563 | 78300 | 78300 | 3.25 | 2300 | 837.6202 |  | 1
65 | 75 | 67 | 66.7494 | 65100 | 34503 | 3.22 | 950 | 183.889 |  | 1
65 | 80 | 67 | 51.5724 | 65100 | 39711 | 3.22 | 950 | 183.889 |  | 1
65 | 85 | 67 | 39.6049 | 65100 | 44919 | 3.22 | 950 | 183.889 |  | 1
65 | 75 | 67 | 66.7494 | 70400 | 38016 | 3.24 | 1200 | 183.889 |  | 1
65 | 80 | 67 | 51.5724 | 70400 | 44352 | 3.24 | 1200 | 183.889 |  | 1
65 | 85 | 67 | 39.6049 | 70400 | 50688 | 3.24 | 1200 | 183.889 |  | 1
65 | 75 | 67 | 66.7494 | 75200 | 41360 | 3.25 | 1500 | 308.5056 |  | 1
65 | 80 | 67 | 51.5724 | 75200 | 49632 | 3.25 | 1500 | 308.5056 |  | 1
65 | 85 | 67 | 39.6049 | 75200 | 57152 | 3.25 | 1500 | 308.5056 |  | 1
65 | 75 | 67 | 66.7494 | 78100 | 43736 | 3.25 | 1750 | 415.4851 |  | 1
65 | 80 | 67 | 51.5724 | 78100 | 53108 | 3.25 | 1750 | 415.4851 |  | 1
65 | 85 | 67 | 39.6049 | 78100 | 62480 | 3.25 | 1750 | 415.4851 |  | 1
65 | 75 | 67 | 66.7494 | 80900 | 46922 | 3.25 | 2050 | 557.4497 |  | 1
65 | 80 | 67 | 51.5724 | 80900 | 58248 | 3.25 | 2050 | 557.4497 |  | 1
65 | 85 | 67 | 39.6049 | 80900 | 67956 | 3.25 | 2050 | 557.4497 |  | 1
65 | 75 | 67 | 66.7494 | 82800 | 49680 | 3.25 | 2300 | 837.6202 |  | 1
65 | 80 | 67 | 51.5724 | 82800 | 61272 | 3.25 | 2300 | 837.6202 |  | 1
65 | 85 | 67 | 39.6049 | 82800 | 72864 | 3.25 | 2300 | 837.6202 |  | 1
65 | 75 | 71 | 82.6659 | 69100 | 29713 | 3.23 | 950 | 183.889 |  | 1
65 | 80 | 71 | 65.0618 | 69100 | 35241 | 3.23 | 950 | 183.889 |  | 1
65 | 85 | 71 | 51.076 | 69100 | 40078 | 3.23 | 950 | 183.889 |  | 1
65 | 75 | 71 | 82.6659 | 74800 | 32164 | 3.25 | 1200 | 195.7435 |  | 1
65 | 80 | 71 | 65.0618 | 74800 | 38896 | 3.25 | 1200 | 195.7435 |  | 1
65 | 85 | 71 | 51.076 | 74800 | 44880 | 3.25 | 1200 | 195.7435 |  | 1
65 | 75 | 71 | 82.6659 | 79600 | 34228 | 3.25 | 1500 | 308.5056 |  | 1
65 | 80 | 71 | 65.0618 | 79600 | 42188 | 3.25 | 1500 | 308.5056 |  | 1
65 | 85 | 71 | 51.076 | 79600 | 50148 | 3.25 | 1500 | 308.5056 |  | 1
65 | 75 | 71 | 82.6659 | 82700 | 36388 | 3.25 | 1750 | 415.4851 |  | 1
65 | 80 | 71 | 65.0618 | 82700 | 45485 | 3.25 | 1750 | 415.4851 |  | 1
65 | 85 | 71 | 51.076 | 82700 | 53755 | 3.25 | 1750 | 415.4851 |  | 1
65 | 75 | 71 | 82.6659 | 85500 | 37620 | 3.25 | 2050 | 557.4497 |  | 1
65 | 80 | 71 | 65.0618 | 85500 | 48735 | 3.25 | 2050 | 557.4497 |  | 1
65 | 85 | 71 | 51.076 | 85500 | 58995 | 3.25 | 2050 | 557.4497 |  | 1
65 | 75 | 71 | 82.6659 | 87700 | 39465 | 3.25 | 2300 | 837.6202 |  | 1
65 | 80 | 71 | 65.0618 | 87700 | 51743 | 3.25 | 2300 | 837.6202 |  | 1
65 | 85 | 71 | 51.076 | 87700 | 63144 | 3.25 | 2300 | 837.6202 |  | 1
75 | 75 | 63 | 52.1129 | 68600 | 47334 | 3.66 | 1500 | 292.6033 |  | 1
75 | 80 | 63 | 39.1676 | 68600 | 54880 | 3.66 | 1500 | 292.6033 |  | 1
75 | 85 | 63 | 29.0563 | 68600 | 63112 | 3.66 | 1500 | 292.6033 |  | 1
75 | 75 | 63 | 52.1129 | 71500 | 51480 | 3.67 | 1750 | 415.4851 |  | 1
75 | 80 | 63 | 39.1676 | 71500 | 60775 | 3.67 | 1750 | 415.4851 |  | 1
75 | 85 | 63 | 29.0563 | 71500 | 69355 | 3.67 | 1750 | 415.4851 |  | 1
75 | 75 | 63 | 52.1129 | 74000 | 54760 | 3.68 | 2050 | 557.4497 |  | 1
75 | 80 | 63 | 39.1676 | 74000 | 65860 | 3.68 | 2050 | 557.4497 |  | 1
75 | 85 | 63 | 29.0563 | 74000 | 74000 | 3.68 | 2050 | 557.4497 |  | 1
75 | 75 | 63 | 52.1129 | 75800 | 59124 | 3.69 | 2300 | 837.6202 |  | 1
75 | 80 | 63 | 39.1676 | 75800 | 70494 | 3.69 | 2300 | 837.6202 |  | 1
75 | 85 | 63 | 29.0563 | 75800 | 75800 | 3.69 | 2300 | 837.6202 |  | 1
75 | 75 | 67 | 66.7494 | 63400 | 33602 | 3.63 | 950 | 183.889 |  | 1
75 | 80 | 67 | 51.5724 | 63400 | 38674 | 3.63 | 950 | 183.889 |  | 1
75 | 85 | 67 | 39.6049 | 63400 | 43746 | 3.63 | 950 | 183.889 |  | 1
75 | 75 | 67 | 66.7494 | 68500 | 36990 | 3.66 | 1200 | 183.889 |  | 1
75 | 80 | 67 | 51.5724 | 68500 | 43155 | 3.66 | 1200 | 183.889 |  | 1
75 | 85 | 67 | 39.6049 | 68500 | 50005 | 3.66 | 1200 | 183.889 |  | 1
75 | 75 | 67 | 66.7494 | 72900 | 40824 | 3.68 | 1500 | 308.5056 |  | 1
75 | 80 | 67 | 51.5724 | 72900 | 48114 | 3.68 | 1500 | 308.5056 |  | 1
75 | 85 | 67 | 39.6049 | 72900 | 56133 | 3.68 | 1500 | 308.5056 |  | 1
75 | 75 | 67 | 66.7494 | 75700 | 43149 | 3.69 | 1750 | 415.4851 |  | 1
75 | 80 | 67 | 51.5724 | 75700 | 52233 | 3.69 | 1750 | 415.4851 |  | 1
75 | 85 | 67 | 39.6049 | 75700 | 61317 | 3.69 | 1750 | 415.4851 |  | 1
75 | 75 | 67 | 66.7494 | 78200 | 45356 | 3.7 | 2050 | 557.4497 |  | 1
75 | 80 | 67 | 51.5724 | 78200 | 57086 | 3.7 | 2050 | 557.4497 |  | 1
75 | 85 | 67 | 39.6049 | 78200 | 67252 | 3.7 | 2050 | 557.4497 |  | 1
75 | 75 | 67 | 66.7494 | 80100 | 48861 | 3.7 | 2300 | 837.6202 |  | 1
75 | 80 | 67 | 51.5724 | 80100 | 60876 | 3.7 | 2300 | 837.6202 |  | 1
75 | 85 | 67 | 39.6049 | 80100 | 72090 | 3.7 | 2300 | 837.6202 |  | 1
75 | 75 | 71 | 82.6659 | 67300 | 28939 | 3.65 | 950 | 183.889 |  | 1
75 | 80 | 71 | 65.0618 | 67300 | 34323 | 3.65 | 950 | 183.889 |  | 1
75 | 85 | 71 | 51.076 | 67300 | 39034 | 3.65 | 950 | 183.889 |  | 1
75 | 75 | 71 | 82.6659 | 72600 | 31218 | 3.68 | 1200 | 195.7435 |  | 1
75 | 80 | 71 | 65.0618 | 72600 | 37752 | 3.68 | 1200 | 195.7435 |  | 1
75 | 85 | 71 | 51.076 | 72600 | 44286 | 3.68 | 1200 | 195.7435 |  | 1
75 | 75 | 71 | 82.6659 | 77200 | 33196 | 3.7 | 1500 | 308.5056 |  | 1
75 | 80 | 71 | 65.0618 | 77200 | 41688 | 3.7 | 1500 | 308.5056 |  | 1
75 | 85 | 71 | 51.076 | 77200 | 49408 | 3.7 | 1500 | 308.5056 |  | 1
75 | 75 | 71 | 82.6659 | 80200 | 35288 | 3.7 | 1750 | 415.4851 |  | 1
75 | 80 | 71 | 65.0618 | 80200 | 44110 | 3.7 | 1750 | 415.4851 |  | 1
75 | 85 | 71 | 51.076 | 80200 | 52932 | 3.7 | 1750 | 415.4851 |  | 1
75 | 75 | 71 | 82.6659 | 82900 | 36476 | 3.71 | 2050 | 557.4497 |  | 1
75 | 80 | 71 | 65.0618 | 82900 | 47253 | 3.71 | 2050 | 557.4497 |  | 1
75 | 85 | 71 | 51.076 | 82900 | 58030 | 3.71 | 2050 | 557.4497 |  | 1
75 | 75 | 71 | 82.6659 | 85000 | 38250 | 3.71 | 2300 | 837.6202 |  | 1
75 | 80 | 71 | 65.0618 | 85000 | 51000 | 3.71 | 2300 | 837.6202 |  | 1
75 | 85 | 71 | 51.076 | 85000 | 62050 | 3.71 | 2300 | 837.6202 |  | 1
85 | 75 | 63 | 52.1129 | 66600 | 46620 | 4.17 | 1500 | 292.6033 |  | 1
85 | 80 | 63 | 39.1676 | 66600 | 54612 | 4.17 | 1500 | 292.6033 |  | 1
85 | 85 | 63 | 29.0563 | 66600 | 61938 | 4.17 | 1500 | 292.6033 |  | 1
85 | 75 | 63 | 52.1129 | 68800 | 50224 | 4.19 | 1750 | 400.161 |  | 1
85 | 80 | 63 | 39.1676 | 68800 | 59168 | 4.19 | 1750 | 400.161 |  | 1
85 | 85 | 63 | 29.0563 | 68800 | 68112 | 4.19 | 1750 | 400.161 |  | 1
85 | 75 | 63 | 52.1129 | 71300 | 54188 | 4.21 | 2050 | 557.4497 |  | 1
85 | 80 | 63 | 39.1676 | 71300 | 64883 | 4.21 | 2050 | 557.4497 |  | 1
85 | 85 | 63 | 29.0563 | 71300 | 71300 | 4.21 | 2050 | 557.4497 |  | 1
85 | 75 | 63 | 52.1129 | 72900 | 57591 | 4.22 | 2300 | 837.6202 |  | 1
85 | 80 | 63 | 39.1676 | 72900 | 69255 | 4.22 | 2300 | 837.6202 |  | 1
85 | 85 | 63 | 29.0563 | 72900 | 72900 | 4.22 | 2300 | 837.6202 |  | 1
85 | 75 | 67 | 66.7494 | 61400 | 32542 | 4.13 | 950 | 183.889 |  | 1
85 | 80 | 67 | 51.5724 | 61400 | 38068 | 4.13 | 950 | 183.889 |  | 1
85 | 85 | 67 | 39.6049 | 61400 | 42980 | 4.13 | 950 | 183.889 |  | 1
85 | 75 | 67 | 66.7494 | 66300 | 35802 | 4.17 | 1200 | 183.889 |  | 1
85 | 80 | 67 | 51.5724 | 66300 | 42432 | 4.17 | 1200 | 183.889 |  | 1
85 | 85 | 67 | 39.6049 | 66300 | 49062 | 4.17 | 1200 | 183.889 |  | 1
85 | 75 | 67 | 66.7494 | 70300 | 39368 | 4.2 | 1500 | 292.6033 |  | 1
85 | 80 | 67 | 51.5724 | 70300 | 47101 | 4.2 | 1500 | 292.6033 |  | 1
85 | 85 | 67 | 39.6049 | 70300 | 54834 | 4.2 | 1500 | 292.6033 |  | 1
85 | 75 | 67 | 66.7494 | 72900 | 42282 | 4.22 | 1750 | 415.4851 |  | 1
85 | 80 | 67 | 51.5724 | 72900 | 51030 | 4.22 | 1750 | 415.4851 |  | 1
85 | 85 | 67 | 39.6049 | 72900 | 60507 | 4.22 | 1750 | 415.4851 |  | 1
85 | 75 | 67 | 66.7494 | 75300 | 45180 | 4.23 | 2050 | 557.4497 |  | 1
85 | 80 | 67 | 51.5724 | 75300 | 55722 | 4.23 | 2050 | 557.4497 |  | 1
85 | 85 | 67 | 39.6049 | 75300 | 65511 | 4.23 | 2050 | 557.4497 |  | 1
85 | 75 | 67 | 66.7494 | 77200 | 47092 | 4.24 | 2300 | 837.6202 |  | 1
85 | 80 | 67 | 51.5724 | 77200 | 59444 | 4.24 | 2300 | 837.6202 |  | 1
85 | 85 | 67 | 39.6049 | 77200 | 71024 | 4.24 | 2300 | 837.6202 |  | 1
85 | 75 | 71 | 82.6659 | 65100 | 27993 | 4.17 | 950 | 183.889 |  | 1
85 | 80 | 71 | 65.0618 | 65100 | 33201 | 4.17 | 950 | 183.889 |  | 1
85 | 85 | 71 | 51.076 | 65100 | 38409 | 4.17 | 950 | 183.889 |  | 1
85 | 75 | 71 | 82.6659 | 70200 | 30186 | 4.2 | 1200 | 183.889 |  | 1
85 | 80 | 71 | 65.0618 | 70200 | 36504 | 4.2 | 1200 | 183.889 |  | 1
85 | 85 | 71 | 51.076 | 70200 | 43524 | 4.2 | 1200 | 183.889 |  | 1
85 | 75 | 71 | 82.6659 | 74500 | 32035 | 4.23 | 1500 | 308.5056 |  | 1
85 | 80 | 71 | 65.0618 | 74500 | 40230 | 4.23 | 1500 | 308.5056 |  | 1
85 | 85 | 71 | 51.076 | 74500 | 48425 | 4.23 | 1500 | 308.5056 |  | 1
85 | 75 | 71 | 82.6659 | 77300 | 34012 | 4.24 | 1750 | 415.4851 |  | 1
85 | 80 | 71 | 65.0618 | 77300 | 43288 | 4.24 | 1750 | 415.4851 |  | 1
85 | 85 | 71 | 51.076 | 77300 | 52564 | 4.24 | 1750 | 415.4851 |  | 1
85 | 75 | 71 | 82.6659 | 79900 | 35955 | 4.26 | 2050 | 557.4497 |  | 1
85 | 80 | 71 | 65.0618 | 79900 | 46342 | 4.26 | 2050 | 557.4497 |  | 1
85 | 85 | 71 | 51.076 | 79900 | 56729 | 4.26 | 2050 | 557.4497 |  | 1
85 | 75 | 71 | 82.6659 | 81600 | 36720 | 4.27 | 2300 | 837.6202 |  | 1
85 | 80 | 71 | 65.0618 | 81600 | 48960 | 4.27 | 2300 | 837.6202 |  | 1
85 | 85 | 71 | 51.076 | 81600 | 60384 | 4.27 | 2300 | 837.6202 |  | 1
95 | 75 | 63 | 52.1129 | 63700 | 45227 | 4.76 | 1500 | 292.6033 |  | 1
95 | 80 | 63 | 39.1676 | 63700 | 52871 | 4.76 | 1500 | 292.6033 |  | 1
95 | 85 | 63 | 29.0563 | 63700 | 60515 | 4.76 | 1500 | 292.6033 |  | 1
95 | 75 | 63 | 52.1129 | 65900 | 48107 | 4.77 | 1750 | 400.161 |  | 1
95 | 80 | 63 | 39.1676 | 65900 | 57992 | 4.77 | 1750 | 400.161 |  | 1
95 | 85 | 63 | 29.0563 | 65900 | 65900 | 4.77 | 1750 | 400.161 |  | 1
95 | 75 | 63 | 52.1129 | 68300 | 52591 | 4.8 | 2050 | 538.9452 |  | 1
95 | 80 | 63 | 39.1676 | 68300 | 63519 | 4.8 | 2050 | 538.9452 |  | 1
95 | 85 | 63 | 29.0563 | 68300 | 68300 | 4.8 | 2050 | 538.9452 |  | 1
95 | 75 | 63 | 52.1129 | 69800 | 56538 | 4.81 | 2300 | 817.67 |  | 1
95 | 80 | 63 | 39.1676 | 69800 | 67706 | 4.81 | 2300 | 817.67 |  | 1
95 | 85 | 63 | 29.0563 | 69800 | 69800 | 4.81 | 2300 | 817.67 |  | 1
95 | 75 | 67 | 66.7494 | 59100 | 31323 | 4.71 | 950 | 183.889 |  | 1
95 | 80 | 67 | 51.5724 | 59100 | 36642 | 4.71 | 950 | 183.889 |  | 1
95 | 85 | 67 | 39.6049 | 59100 | 41961 | 4.71 | 950 | 183.889 |  | 1
95 | 75 | 67 | 66.7494 | 63700 | 35035 | 4.75 | 1200 | 183.889 |  | 1
95 | 80 | 67 | 51.5724 | 63700 | 41405 | 4.75 | 1200 | 183.889 |  | 1
95 | 85 | 67 | 39.6049 | 63700 | 47775 | 4.75 | 1200 | 183.889 |  | 1
95 | 75 | 67 | 66.7494 | 67600 | 37856 | 4.79 | 1500 | 292.6033 |  | 1
95 | 80 | 67 | 51.5724 | 67600 | 45968 | 4.79 | 1500 | 292.6033 |  | 1
95 | 85 | 67 | 39.6049 | 67600 | 54080 | 4.79 | 1500 | 292.6033 |  | 1
95 | 75 | 67 | 66.7494 | 70000 | 40600 | 4.81 | 1750 | 400.161 |  | 1
95 | 80 | 67 | 51.5724 | 70000 | 49700 | 4.81 | 1750 | 400.161 |  | 1
95 | 85 | 67 | 39.6049 | 70000 | 58800 | 4.81 | 1750 | 400.161 |  | 1
95 | 75 | 67 | 66.7494 | 72100 | 43981 | 4.83 | 2050 | 557.4497 |  | 1
95 | 80 | 67 | 51.5724 | 72100 | 53354 | 4.83 | 2050 | 557.4497 |  | 1
95 | 85 | 67 | 39.6049 | 72100 | 64890 | 4.83 | 2050 | 557.4497 |  | 1
95 | 75 | 67 | 66.7494 | 73800 | 45756 | 4.84 | 2300 | 837.6202 |  | 1
95 | 80 | 67 | 51.5724 | 73800 | 58302 | 4.84 | 2300 | 837.6202 |  | 1
95 | 85 | 67 | 39.6049 | 73800 | 69372 | 4.84 | 2300 | 837.6202 |  | 1
95 | 75 | 71 | 82.6659 | 62800 | 27004 | 4.74 | 950 | 183.889 |  | 1
95 | 80 | 71 | 65.0618 | 62800 | 32028 | 4.74 | 950 | 183.889 |  | 1
95 | 85 | 71 | 51.076 | 62800 | 37052 | 4.74 | 950 | 183.889 |  | 1
95 | 75 | 71 | 82.6659 | 67500 | 29025 | 4.79 | 1200 | 183.889 |  | 1
95 | 80 | 71 | 65.0618 | 67500 | 35775 | 4.79 | 1200 | 183.889 |  | 1
95 | 85 | 71 | 51.076 | 67500 | 41850 | 4.79 | 1200 | 183.889 |  | 1
95 | 75 | 71 | 82.6659 | 71600 | 30788 | 4.82 | 1500 | 308.5056 |  | 1
95 | 80 | 71 | 65.0618 | 71600 | 39380 | 4.82 | 1500 | 308.5056 |  | 1
95 | 85 | 71 | 51.076 | 71600 | 46540 | 4.82 | 1500 | 308.5056 |  | 1
95 | 75 | 71 | 82.6659 | 74200 | 32648 | 4.84 | 1750 | 415.4851 |  | 1
95 | 80 | 71 | 65.0618 | 74200 | 42294 | 4.84 | 1750 | 415.4851 |  | 1
95 | 85 | 71 | 51.076 | 74200 | 51198 | 4.84 | 1750 | 415.4851 |  | 1
95 | 75 | 71 | 82.6659 | 76600 | 34470 | 4.86 | 2050 | 557.4497 |  | 1
95 | 80 | 71 | 65.0618 | 76600 | 45194 | 4.86 | 2050 | 557.4497 |  | 1
95 | 85 | 71 | 51.076 | 76600 | 55152 | 4.86 | 2050 | 557.4497 |  | 1
95 | 75 | 71 | 82.6659 | 78200 | 35972 | 4.88 | 2300 | 837.6202 |  | 1
95 | 80 | 71 | 65.0618 | 78200 | 48484 | 4.88 | 2300 | 837.6202 |  | 1
95 | 85 | 71 | 51.076 | 78200 | 59432 | 4.88 | 2300 | 837.6202 |  | 1
105 | 75 | 63 | 52.1129 | 57200 | 38896 | 5.34 | 1200 | 183.889 |  | 1
105 | 80 | 63 | 39.1676 | 57200 | 45188 | 5.34 | 1200 | 183.889 |  | 1
105 | 85 | 63 | 29.0563 | 57200 | 51480 | 5.34 | 1200 | 183.889 |  | 1
105 | 75 | 63 | 52.1129 | 60800 | 43776 | 5.38 | 1500 | 292.6033 |  | 1
105 | 80 | 63 | 39.1676 | 60800 | 51680 | 5.38 | 1500 | 292.6033 |  | 1
105 | 85 | 63 | 29.0563 | 60800 | 59584 | 5.38 | 1500 | 292.6033 |  | 1
105 | 75 | 63 | 52.1129 | 63000 | 47250 | 5.4 | 1750 | 400.161 |  | 1
105 | 80 | 63 | 39.1676 | 63000 | 56700 | 5.4 | 1750 | 400.161 |  | 1
105 | 85 | 63 | 29.0563 | 63000 | 63000 | 5.4 | 1750 | 400.161 |  | 1
105 | 75 | 63 | 52.1129 | 65000 | 51350 | 5.42 | 2050 | 538.9452 |  | 1
105 | 80 | 63 | 39.1676 | 65000 | 62400 | 5.42 | 2050 | 538.9452 |  | 1
105 | 85 | 63 | 29.0563 | 65000 | 65000 | 5.42 | 2050 | 538.9452 |  | 1
105 | 75 | 63 | 52.1129 | 66600 | 55278 | 5.44 | 2300 | 817.67 |  | 1
105 | 80 | 63 | 39.1676 | 66600 | 65934 | 5.44 | 2300 | 817.67 |  | 1
105 | 85 | 63 | 29.0563 | 66600 | 66600 | 5.44 | 2300 | 817.67 |  | 1
105 | 75 | 67 | 66.7494 | 56800 | 30672 | 5.33 | 950 | 183.889 |  | 1
105 | 80 | 67 | 51.5724 | 56800 | 35784 | 5.33 | 950 | 183.889 |  | 1
105 | 85 | 67 | 39.6049 | 56800 | 40896 | 5.33 | 950 | 183.889 |  | 1
105 | 75 | 67 | 66.7494 | 61000 | 33550 | 5.38 | 1200 | 183.889 |  | 1
105 | 80 | 67 | 51.5724 | 61000 | 40260 | 5.38 | 1200 | 183.889 |  | 1
105 | 85 | 67 | 39.6049 | 61000 | 46360 | 5.38 | 1200 | 183.889 |  | 1
105 | 75 | 67 | 66.7494 | 64500 | 36765 | 5.41 | 1500 | 292.6033 |  | 1
105 | 80 | 67 | 51.5724 | 64500 | 44505 | 5.41 | 1500 | 292.6033 |  | 1
105 | 85 | 67 | 39.6049 | 64500 | 52890 | 5.41 | 1500 | 292.6033 |  | 1
105 | 75 | 67 | 66.7494 | 66800 | 39412 | 5.44 | 1750 | 400.161 |  | 1
105 | 80 | 67 | 51.5724 | 66800 | 48764 | 5.44 | 1750 | 400.161 |  | 1
105 | 85 | 67 | 39.6049 | 66800 | 57448 | 5.44 | 1750 | 400.161 |  | 1
105 | 75 | 67 | 66.7494 | 69000 | 42780 | 5.46 | 2050 | 538.9452 |  | 1
105 | 80 | 67 | 51.5724 | 69000 | 53130 | 5.46 | 2050 | 538.9452 |  | 1
105 | 85 | 67 | 39.6049 | 69000 | 63480 | 5.46 | 2050 | 538.9452 |  | 1
105 | 75 | 67 | 66.7494 | 70500 | 45120 | 5.47 | 2300 | 817.67 |  | 1
105 | 80 | 67 | 51.5724 | 70500 | 57105 | 5.47 | 2300 | 817.67 |  | 1
105 | 85 | 67 | 39.6049 | 70500 | 68385 | 5.47 | 2300 | 817.67 |  | 1
105 | 75 | 71 | 82.6659 | 60200 | 25886 | 5.36 | 950 | 183.889 |  | 1
105 | 80 | 71 | 65.0618 | 60200 | 30702 | 5.36 | 950 | 183.889 |  | 1
105 | 85 | 71 | 51.076 | 60200 | 36120 | 5.36 | 950 | 183.889 |  | 1
105 | 75 | 71 | 82.6659 | 64700 | 27821 | 5.42 | 1200 | 183.889 |  | 1
105 | 80 | 71 | 65.0618 | 64700 | 34291 | 5.42 | 1200 | 183.889 |  | 1
105 | 85 | 71 | 51.076 | 64700 | 40761 | 5.42 | 1200 | 183.889 |  | 1
105 | 75 | 71 | 82.6659 | 68400 | 30096 | 5.45 | 1500 | 292.6033 |  | 1
105 | 80 | 71 | 65.0618 | 68400 | 37620 | 5.45 | 1500 | 292.6033 |  | 1
105 | 85 | 71 | 51.076 | 68400 | 45828 | 5.45 | 1500 | 292.6033 |  | 1
105 | 75 | 71 | 82.6659 | 70700 | 31815 | 5.48 | 1750 | 415.4851 |  | 1
105 | 80 | 71 | 65.0618 | 70700 | 40299 | 5.48 | 1750 | 415.4851 |  | 1
105 | 85 | 71 | 51.076 | 70700 | 49490 | 5.48 | 1750 | 415.4851 |  | 1
105 | 75 | 71 | 82.6659 | 73000 | 33580 | 5.5 | 2050 | 557.4497 |  | 1
105 | 80 | 71 | 65.0618 | 73000 | 43800 | 5.5 | 2050 | 557.4497 |  | 1
105 | 85 | 71 | 51.076 | 73000 | 54020 | 5.5 | 2050 | 557.4497 |  | 1
105 | 75 | 71 | 82.6659 | 74600 | 35062 | 5.51 | 2300 | 837.6202 |  | 1
105 | 80 | 71 | 65.0618 | 74600 | 46998 | 5.51 | 2300 | 837.6202 |  | 1
105 | 85 | 71 | 51.076 | 74600 | 58188 | 5.51 | 2300 | 837.6202 |  | 1
115 | 75 | 63 | 52.1129 | 54500 | 37605 | 5.96 | 1200 | 183.889 |  | 1
115 | 80 | 63 | 39.1676 | 54500 | 44145 | 5.96 | 1200 | 183.889 |  | 1
115 | 85 | 63 | 29.0563 | 54500 | 50140 | 5.96 | 1200 | 183.889 |  | 1
115 | 75 | 63 | 52.1129 | 57700 | 42121 | 6.01 | 1500 | 292.6033 |  | 1
115 | 80 | 63 | 39.1676 | 57700 | 50199 | 6.01 | 1500 | 292.6033 |  | 1
115 | 85 | 63 | 29.0563 | 57700 | 57700 | 6.01 | 1500 | 292.6033 |  | 1
115 | 75 | 63 | 52.1129 | 59700 | 45372 | 6.03 | 1750 | 400.161 |  | 1
115 | 80 | 63 | 39.1676 | 59700 | 54924 | 6.03 | 1750 | 400.161 |  | 1
115 | 85 | 63 | 29.0563 | 59700 | 59700 | 6.03 | 1750 | 400.161 |  | 1
115 | 75 | 63 | 52.1129 | 61900 | 50139 | 6.06 | 2050 | 538.9452 |  | 1
115 | 80 | 63 | 39.1676 | 61900 | 60662 | 6.06 | 2050 | 538.9452 |  | 1
115 | 85 | 63 | 29.0563 | 61900 | 61900 | 6.06 | 2050 | 538.9452 |  | 1
115 | 75 | 63 | 52.1129 | 63300 | 53805 | 6.07 | 2300 | 817.67 |  | 1
115 | 80 | 63 | 39.1676 | 63300 | 63300 | 6.07 | 2300 | 817.67 |  | 1
115 | 85 | 63 | 29.0563 | 63300 | 63300 | 6.07 | 2300 | 817.67 |  | 1
115 | 75 | 67 | 66.7494 | 54300 | 29322 | 5.97 | 950 | 183.889 |  | 1
115 | 80 | 67 | 51.5724 | 54300 | 34752 | 5.97 | 950 | 183.889 |  | 1
115 | 85 | 67 | 39.6049 | 54300 | 39639 | 5.97 | 950 | 183.889 |  | 1
115 | 75 | 67 | 66.7494 | 58000 | 32480 | 6.01 | 1200 | 183.889 |  | 1
115 | 80 | 67 | 51.5724 | 58000 | 38860 | 6.01 | 1200 | 183.889 |  | 1
115 | 85 | 67 | 39.6049 | 58000 | 44660 | 6.01 | 1200 | 183.889 |  | 1
115 | 75 | 67 | 66.7494 | 61300 | 35554 | 6.05 | 1500 | 292.6033 |  | 1
115 | 80 | 67 | 51.5724 | 61300 | 43523 | 6.05 | 1500 | 292.6033 |  | 1
115 | 85 | 67 | 39.6049 | 61300 | 51492 | 6.05 | 1500 | 292.6033 |  | 1
115 | 75 | 67 | 66.7494 | 63300 | 37980 | 6.08 | 1750 | 400.161 |  | 1
115 | 80 | 67 | 51.5724 | 63300 | 46842 | 6.08 | 1750 | 400.161 |  | 1
115 | 85 | 67 | 39.6049 | 63300 | 56337 | 6.08 | 1750 | 400.161 |  | 1
115 | 75 | 67 | 66.7494 | 65400 | 41202 | 6.11 | 2050 | 538.9452 |  | 1
115 | 80 | 67 | 51.5724 | 65400 | 51666 | 6.11 | 2050 | 538.9452 |  | 1
115 | 85 | 67 | 39.6049 | 65400 | 62130 | 6.11 | 2050 | 538.9452 |  | 1
115 | 75 | 67 | 66.7494 | 66600 | 43290 | 6.12 | 2300 | 817.67 |  | 1
115 | 80 | 67 | 51.5724 | 66600 | 55278 | 6.12 | 2300 | 817.67 |  | 1
115 | 85 | 67 | 39.6049 | 66600 | 65934 | 6.12 | 2300 | 817.67 |  | 1
115 | 75 | 71 | 82.6659 | 57700 | 24811 | 6.01 | 950 | 183.889 |  | 1
115 | 80 | 71 | 65.0618 | 57700 | 30004 | 6.01 | 950 | 183.889 |  | 1
115 | 85 | 71 | 51.076 | 57700 | 35197 | 6.01 | 950 | 183.889 |  | 1
115 | 75 | 71 | 82.6659 | 61600 | 26488 | 6.06 | 1200 | 183.889 |  | 1
115 | 80 | 71 | 65.0618 | 61600 | 33264 | 6.06 | 1200 | 183.889 |  | 1
115 | 85 | 71 | 51.076 | 61600 | 39424 | 6.06 | 1200 | 183.889 |  | 1
115 | 75 | 71 | 82.6659 | 65100 | 28644 | 6.1 | 1500 | 292.6033 |  | 1
115 | 80 | 71 | 65.0618 | 65100 | 36456 | 6.1 | 1500 | 292.6033 |  | 1
115 | 85 | 71 | 51.076 | 65100 | 44268 | 6.1 | 1500 | 292.6033 |  | 1
115 | 75 | 71 | 82.6659 | 67200 | 30240 | 6.12 | 1750 | 400.161 |  | 1
115 | 80 | 71 | 65.0618 | 67200 | 39648 | 6.12 | 1750 | 400.161 |  | 1
115 | 85 | 71 | 51.076 | 67200 | 48384 | 6.12 | 1750 | 400.161 |  | 1
115 | 75 | 71 | 82.6659 | 69300 | 31878 | 6.15 | 2050 | 538.9452 |  | 1
115 | 80 | 71 | 65.0618 | 69300 | 42966 | 6.15 | 2050 | 538.9452 |  | 1
115 | 85 | 71 | 51.076 | 69300 | 53361 | 6.15 | 2050 | 538.9452 |  | 1
115 | 75 | 71 | 82.6659 | 70400 | 33088 | 6.16 | 2300 | 817.67 |  | 1
115 | 80 | 71 | 65.0618 | 70400 | 45056 | 6.16 | 2300 | 817.67 |  | 1
115 | 85 | 71 | 51.076 | 70400 | 57024 | 6.16 | 2300 | 817.67 |  | 1
95 | 75 | 63 | 52.1129 | 63700 | 45227 | 4.76 | 1500 | 292.6033 |  | 1
95 | 80 | 63 | 39.1676 | 63700 | 52871 | 4.76 | 1500 | 292.6033 |  | 1
95 | 85 | 63 | 29.0563 | 63700 | 60515 | 4.76 | 1500 | 292.6033 |  | 1
95 | 75 | 63 | 52.1129 | 65900 | 48107 | 4.77 | 1750 | 400.161 |  | 1
95 | 80 | 63 | 39.1676 | 65900 | 57992 | 4.77 | 1750 | 400.161 |  | 1
95 | 85 | 63 | 29.0563 | 65900 | 65900 | 4.77 | 1750 | 400.161 |  | 1
95 | 75 | 63 | 52.1129 | 68300 | 52591 | 4.8 | 2050 | 538.9452 |  | 1
95 | 80 | 63 | 39.1676 | 68300 | 63519 | 4.8 | 2050 | 538.9452 |  | 1
95 | 85 | 63 | 29.0563 | 68300 | 68300 | 4.8 | 2050 | 538.9452 |  | 1
95 | 75 | 63 | 52.1129 | 69800 | 56538 | 4.81 | 2300 | 817.67 |  | 1
95 | 80 | 63 | 39.1676 | 69800 | 67706 | 4.81 | 2300 | 817.67 |  | 1
95 | 85 | 63 | 29.0563 | 69800 | 69800 | 4.81 | 2300 | 817.67 |  | 1
95 | 75 | 67 | 66.7494 | 59100 | 31323 | 4.71 | 950 | 183.889 |  | 1
95 | 80 | 67 | 51.5724 | 59100 | 36642 | 4.71 | 950 | 183.889 |  | 1
95 | 85 | 67 | 39.6049 | 59100 | 41961 | 4.71 | 950 | 183.889 |  | 1
95 | 75 | 67 | 66.7494 | 63700 | 35035 | 4.75 | 1200 | 183.889 |  | 1
95 | 80 | 67 | 51.5724 | 63700 | 41405 | 4.75 | 1200 | 183.889 |  | 1
95 | 85 | 67 | 39.6049 | 63700 | 47775 | 4.75 | 1200 | 183.889 |  | 1
95 | 75 | 67 | 66.7494 | 67600 | 37856 | 4.79 | 1500 | 292.6033 |  | 1
95 | 80 | 67 | 51.5724 | 67600 | 45968 | 4.79 | 1500 | 292.6033 |  | 1
95 | 85 | 67 | 39.6049 | 67600 | 54080 | 4.79 | 1500 | 292.6033 |  | 1
95 | 75 | 67 | 66.7494 | 70000 | 40600 | 4.81 | 1750 | 400.161 |  | 1
95 | 80 | 67 | 51.5724 | 70000 | 49700 | 4.81 | 1750 | 400.161 |  | 1
95 | 85 | 67 | 39.6049 | 70000 | 58800 | 4.81 | 1750 | 400.161 |  | 1
95 | 75 | 67 | 66.7494 | 72100 | 43981 | 4.83 | 2050 | 557.4497 |  | 1
95 | 80 | 67 | 51.5724 | 72100 | 53354 | 4.83 | 2050 | 557.4497 |  | 1
95 | 85 | 67 | 39.6049 | 72100 | 64890 | 4.83 | 2050 | 557.4497 |  | 1
95 | 75 | 67 | 66.7494 | 73800 | 45756 | 4.84 | 2300 | 837.6202 |  | 1
95 | 80 | 67 | 51.5724 | 73800 | 58302 | 4.84 | 2300 | 837.6202 |  | 1
95 | 85 | 67 | 39.6049 | 73800 | 69372 | 4.84 | 2300 | 837.6202 |  | 1
95 | 75 | 71 | 82.6659 | 62800 | 27004 | 4.74 | 950 | 183.889 |  | 1
95 | 80 | 71 | 65.0618 | 62800 | 32028 | 4.74 | 950 | 183.889 |  | 1
95 | 85 | 71 | 51.076 | 62800 | 37052 | 4.74 | 950 | 183.889 |  | 1
95 | 75 | 71 | 82.6659 | 67500 | 29025 | 4.79 | 1200 | 183.889 |  | 1
95 | 80 | 71 | 65.0618 | 67500 | 35775 | 4.79 | 1200 | 183.889 |  | 1
95 | 85 | 71 | 51.076 | 67500 | 41850 | 4.79 | 1200 | 183.889 |  | 1
95 | 75 | 71 | 82.6659 | 71600 | 30788 | 4.82 | 1500 | 308.5056 |  | 1
95 | 80 | 71 | 65.0618 | 71600 | 39380 | 4.82 | 1500 | 308.5056 |  | 1
95 | 85 | 71 | 51.076 | 71600 | 46540 | 4.82 | 1500 | 308.5056 |  | 1
95 | 75 | 71 | 82.6659 | 74200 | 32648 | 4.84 | 1750 | 415.4851 |  | 1
95 | 80 | 71 | 65.0618 | 74200 | 42294 | 4.84 | 1750 | 415.4851 |  | 1
95 | 85 | 71 | 51.076 | 74200 | 51198 | 4.84 | 1750 | 415.4851 |  | 1
95 | 75 | 71 | 82.6659 | 76600 | 34470 | 4.86 | 2050 | 557.4497 |  | 1
95 | 80 | 71 | 65.0618 | 76600 | 45194 | 4.86 | 2050 | 557.4497 |  | 1
95 | 85 | 71 | 51.076 | 76600 | 55152 | 4.86 | 2050 | 557.4497 |  | 1
95 | 75 | 71 | 82.6659 | 78200 | 35972 | 4.88 | 2300 | 837.6202 |  | 1
95 | 80 | 71 | 65.0618 | 78200 | 48484 | 4.88 | 2300 | 837.6202 |  | 1
95 | 85 | 71 | 51.076 | 78200 | 59432 | 4.88 | 2300 | 837.6202 |  | 1
105 | 75 | 63 | 52.1129 | 57200 | 38896 | 5.34 | 1200 | 183.889 |  | 1
105 | 80 | 63 | 39.1676 | 57200 | 45188 | 5.34 | 1200 | 183.889 |  | 1
105 | 85 | 63 | 29.0563 | 57200 | 51480 | 5.34 | 1200 | 183.889 |  | 1
105 | 75 | 63 | 52.1129 | 60800 | 43776 | 5.38 | 1500 | 292.6033 |  | 1
105 | 80 | 63 | 39.1676 | 60800 | 51680 | 5.38 | 1500 | 292.6033 |  | 1
105 | 85 | 63 | 29.0563 | 60800 | 59584 | 5.38 | 1500 | 292.6033 |  | 1
105 | 75 | 63 | 52.1129 | 63000 | 47250 | 5.4 | 1750 | 400.161 |  | 1
105 | 80 | 63 | 39.1676 | 63000 | 56700 | 5.4 | 1750 | 400.161 |  | 1
105 | 85 | 63 | 29.0563 | 63000 | 63000 | 5.4 | 1750 | 400.161 |  | 1
105 | 75 | 63 | 52.1129 | 65000 | 51350 | 5.42 | 2050 | 538.9452 |  | 1
105 | 80 | 63 | 39.1676 | 65000 | 62400 | 5.42 | 2050 | 538.9452 |  | 1
105 | 85 | 63 | 29.0563 | 65000 | 65000 | 5.42 | 2050 | 538.9452 |  | 1
105 | 75 | 63 | 52.1129 | 66600 | 55278 | 5.44 | 2300 | 817.67 |  | 1
105 | 80 | 63 | 39.1676 | 66600 | 65934 | 5.44 | 2300 | 817.67 |  | 1
105 | 85 | 63 | 29.0563 | 66600 | 66600 | 5.44 | 2300 | 817.67 |  | 1
105 | 75 | 67 | 66.7494 | 56800 | 30672 | 5.33 | 950 | 183.889 |  | 1
105 | 80 | 67 | 51.5724 | 56800 | 35784 | 5.33 | 950 | 183.889 |  | 1
105 | 85 | 67 | 39.6049 | 56800 | 40896 | 5.33 | 950 | 183.889 |  | 1
105 | 75 | 67 | 66.7494 | 61000 | 33550 | 5.38 | 1200 | 183.889 |  | 1
105 | 80 | 67 | 51.5724 | 61000 | 40260 | 5.38 | 1200 | 183.889 |  | 1
105 | 85 | 67 | 39.6049 | 61000 | 46360 | 5.38 | 1200 | 183.889 |  | 1
105 | 75 | 67 | 66.7494 | 64500 | 36765 | 5.41 | 1500 | 292.6033 |  | 1
105 | 80 | 67 | 51.5724 | 64500 | 44505 | 5.41 | 1500 | 292.6033 |  | 1
105 | 85 | 67 | 39.6049 | 64500 | 52890 | 5.41 | 1500 | 292.6033 |  | 1
105 | 75 | 67 | 66.7494 | 66800 | 39412 | 5.44 | 1750 | 400.161 |  | 1
105 | 80 | 67 | 51.5724 | 66800 | 48764 | 5.44 | 1750 | 400.161 |  | 1
105 | 85 | 67 | 39.6049 | 66800 | 57448 | 5.44 | 1750 | 400.161 |  | 1
105 | 75 | 67 | 66.7494 | 69000 | 42780 | 5.46 | 2050 | 538.9452 |  | 1
105 | 80 | 67 | 51.5724 | 69000 | 53130 | 5.46 | 2050 | 538.9452 |  | 1
105 | 85 | 67 | 39.6049 | 69000 | 63480 | 5.46 | 2050 | 538.9452 |  | 1
105 | 75 | 67 | 66.7494 | 70500 | 45120 | 5.47 | 2300 | 817.67 |  | 1
105 | 80 | 67 | 51.5724 | 70500 | 57105 | 5.47 | 2300 | 817.67 |  | 1
105 | 85 | 67 | 39.6049 | 70500 | 68385 | 5.47 | 2300 | 817.67 |  | 1
105 | 75 | 71 | 82.6659 | 60200 | 25886 | 5.36 | 950 | 183.889 |  | 1
105 | 80 | 71 | 65.0618 | 60200 | 30702 | 5.36 | 950 | 183.889 |  | 1
105 | 85 | 71 | 51.076 | 60200 | 36120 | 5.36 | 950 | 183.889 |  | 1
105 | 75 | 71 | 82.6659 | 64700 | 27821 | 5.42 | 1200 | 183.889 |  | 1
105 | 80 | 71 | 65.0618 | 64700 | 34291 | 5.42 | 1200 | 183.889 |  | 1
105 | 85 | 71 | 51.076 | 64700 | 40761 | 5.42 | 1200 | 183.889 |  | 1
105 | 75 | 71 | 82.6659 | 68400 | 30096 | 5.45 | 1500 | 292.6033 |  | 1
105 | 80 | 71 | 65.0618 | 68400 | 37620 | 5.45 | 1500 | 292.6033 |  | 1
105 | 85 | 71 | 51.076 | 68400 | 45828 | 5.45 | 1500 | 292.6033 |  | 1
105 | 75 | 71 | 82.6659 | 70700 | 31815 | 5.48 | 1750 | 415.4851 |  | 1
105 | 80 | 71 | 65.0618 | 70700 | 40299 | 5.48 | 1750 | 415.4851 |  | 1
105 | 85 | 71 | 51.076 | 70700 | 49490 | 5.48 | 1750 | 415.4851 |  | 1
105 | 75 | 71 | 82.6659 | 73000 | 33580 | 5.5 | 2050 | 557.4497 |  | 1
105 | 80 | 71 | 65.0618 | 73000 | 43800 | 5.5 | 2050 | 557.4497 |  | 1
105 | 85 | 71 | 51.076 | 73000 | 54020 | 5.5 | 2050 | 557.4497 |  | 1
105 | 75 | 71 | 82.6659 | 74600 | 35062 | 5.51 | 2300 | 837.6202 |  | 1
105 | 80 | 71 | 65.0618 | 74600 | 46998 | 5.51 | 2300 | 837.6202 |  | 1
105 | 85 | 71 | 51.076 | 74600 | 58188 | 5.51 | 2300 | 837.6202 |  | 1
115 | 75 | 63 | 52.1129 | 54500 | 37605 | 5.96 | 1200 | 183.889 |  | 1
115 | 80 | 63 | 39.1676 | 54500 | 44145 | 5.96 | 1200 | 183.889 |  | 1
115 | 85 | 63 | 29.0563 | 54500 | 50140 | 5.96 | 1200 | 183.889 |  | 1
115 | 75 | 63 | 52.1129 | 57700 | 42121 | 6.01 | 1500 | 292.6033 |  | 1
115 | 80 | 63 | 39.1676 | 57700 | 50199 | 6.01 | 1500 | 292.6033 |  | 1
115 | 85 | 63 | 29.0563 | 57700 | 57700 | 6.01 | 1500 | 292.6033 |  | 1
115 | 75 | 63 | 52.1129 | 59700 | 45372 | 6.03 | 1750 | 400.161 |  | 1
115 | 80 | 63 | 39.1676 | 59700 | 54924 | 6.03 | 1750 | 400.161 |  | 1
115 | 85 | 63 | 29.0563 | 59700 | 59700 | 6.03 | 1750 | 400.161 |  | 1
115 | 75 | 63 | 52.1129 | 61900 | 50139 | 6.06 | 2050 | 538.9452 |  | 1
115 | 80 | 63 | 39.1676 | 61900 | 60662 | 6.06 | 2050 | 538.9452 |  | 1
115 | 85 | 63 | 29.0563 | 61900 | 61900 | 6.06 | 2050 | 538.9452 |  | 1
115 | 75 | 63 | 52.1129 | 63300 | 53805 | 6.07 | 2300 | 817.67 |  | 1
115 | 80 | 63 | 39.1676 | 63300 | 63300 | 6.07 | 2300 | 817.67 |  | 1
115 | 85 | 63 | 29.0563 | 63300 | 63300 | 6.07 | 2300 | 817.67 |  | 1
115 | 75 | 67 | 66.7494 | 54300 | 29322 | 5.97 | 950 | 183.889 |  | 1
115 | 80 | 67 | 51.5724 | 54300 | 34752 | 5.97 | 950 | 183.889 |  | 1
115 | 85 | 67 | 39.6049 | 54300 | 39639 | 5.97 | 950 | 183.889 |  | 1
115 | 75 | 67 | 66.7494 | 58000 | 32480 | 6.01 | 1200 | 183.889 |  | 1
115 | 80 | 67 | 51.5724 | 58000 | 38860 | 6.01 | 1200 | 183.889 |  | 1
115 | 85 | 67 | 39.6049 | 58000 | 44660 | 6.01 | 1200 | 183.889 |  | 1
115 | 75 | 67 | 66.7494 | 61300 | 35554 | 6.05 | 1500 | 292.6033 |  | 1
115 | 80 | 67 | 51.5724 | 61300 | 43523 | 6.05 | 1500 | 292.6033 |  | 1
115 | 85 | 67 | 39.6049 | 61300 | 51492 | 6.05 | 1500 | 292.6033 |  | 1
115 | 75 | 67 | 66.7494 | 63300 | 37980 | 6.08 | 1750 | 400.161 |  | 1
115 | 80 | 67 | 51.5724 | 63300 | 46842 | 6.08 | 1750 | 400.161 |  | 1
115 | 85 | 67 | 39.6049 | 63300 | 56337 | 6.08 | 1750 | 400.161 |  | 1
115 | 75 | 67 | 66.7494 | 65400 | 41202 | 6.11 | 2050 | 538.9452 |  | 1
115 | 80 | 67 | 51.5724 | 65400 | 51666 | 6.11 | 2050 | 538.9452 |  | 1
115 | 85 | 67 | 39.6049 | 65400 | 62130 | 6.11 | 2050 | 538.9452 |  | 1
115 | 75 | 67 | 66.7494 | 66600 | 43290 | 6.12 | 2300 | 817.67 |  | 1
115 | 80 | 67 | 51.5724 | 66600 | 55278 | 6.12 | 2300 | 817.67 |  | 1
115 | 85 | 67 | 39.6049 | 66600 | 65934 | 6.12 | 2300 | 817.67 |  | 1
115 | 75 | 71 | 82.6659 | 57700 | 24811 | 6.01 | 950 | 183.889 |  | 1
115 | 80 | 71 | 65.0618 | 57700 | 30004 | 6.01 | 950 | 183.889 |  | 1
115 | 85 | 71 | 51.076 | 57700 | 35197 | 6.01 | 950 | 183.889 |  | 1
115 | 75 | 71 | 82.6659 | 61600 | 26488 | 6.06 | 1200 | 183.889 |  | 1
115 | 80 | 71 | 65.0618 | 61600 | 33264 | 6.06 | 1200 | 183.889 |  | 1
115 | 85 | 71 | 51.076 | 61600 | 39424 | 6.06 | 1200 | 183.889 |  | 1
115 | 75 | 71 | 82.6659 | 65100 | 28644 | 6.1 | 1500 | 292.6033 |  | 1
115 | 80 | 71 | 65.0618 | 65100 | 36456 | 6.1 | 1500 | 292.6033 |  | 1
115 | 85 | 71 | 51.076 | 65100 | 44268 | 6.1 | 1500 | 292.6033 |  | 1
115 | 75 | 71 | 82.6659 | 67200 | 30240 | 6.12 | 1750 | 400.161 |  | 1
115 | 80 | 71 | 65.0618 | 67200 | 39648 | 6.12 | 1750 | 400.161 |  | 1
115 | 85 | 71 | 51.076 | 67200 | 48384 | 6.12 | 1750 | 400.161 |  | 1
115 | 75 | 71 | 82.6659 | 69300 | 31878 | 6.15 | 2050 | 538.9452 |  | 1
115 | 80 | 71 | 65.0618 | 69300 | 42966 | 6.15 | 2050 | 538.9452 |  | 1
115 | 85 | 71 | 51.076 | 69300 | 53361 | 6.15 | 2050 | 538.9452 |  | 1
115 | 75 | 71 | 82.6659 | 70400 | 33088 | 6.16 | 2300 | 817.67 |  | 1
115 | 80 | 71 | 65.0618 | 70400 | 45056 | 6.16 | 2300 | 817.67 |  | 1
115 | 85 | 71 | 51.076 | 70400 | 57024 | 6.16 | 2300 | 817.67 |  | 1
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 2
Degradation Coefficient (C_d)
IEER or SEER | 18.5
Standby Power (W)
Crankcase Heater Power (W)
Net
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 75 | 63 | 52.1129 | 33600 | 27888 | 0.91 | 1200 | 208.3799 |  | 1
65 | 80 | 63 | 39.1676 | 33600 | 32592 | 0.91 | 1200 | 208.3799 |  | 1
65 | 85 | 63 | 29.0563 | 33600 | 33600 | 0.91 | 1200 | 208.3799 |  | 1
65 | 75 | 63 | 52.1129 | 35200 | 31328 | 0.91 | 1500 | 208.3799 |  | 1
65 | 80 | 63 | 39.1676 | 35200 | 34848 | 0.91 | 1500 | 208.3799 |  | 1
65 | 85 | 63 | 29.0563 | 35200 | 35200 | 0.91 | 1500 | 208.3799 |  | 1
65 | 75 | 63 | 52.1129 | 36700 | 34131 | 0.9 | 1800 | 208.3799 |  | 1
65 | 80 | 63 | 39.1676 | 36700 | 36700 | 0.9 | 1800 | 208.3799 |  | 1
65 | 85 | 63 | 29.0563 | 36700 | 36700 | 0.9 | 1800 | 208.3799 |  | 1
65 | 75 | 67 | 66.7494 | 35100 | 18603 | 0.91 | 1200 | 208.3799 |  | 1
65 | 80 | 67 | 51.5724 | 35100 | 27027 | 0.91 | 1200 | 208.3799 |  | 1
65 | 85 | 67 | 39.6049 | 35100 | 33345 | 0.91 | 1200 | 208.3799 |  | 1
65 | 75 | 67 | 66.7494 | 36600 | 20862 | 0.9 | 1500 | 208.3799 |  | 1
65 | 80 | 67 | 51.5724 | 36600 | 30744 | 0.9 | 1500 | 208.3799 |  | 1
65 | 85 | 67 | 39.6049 | 36600 | 35868 | 0.9 | 1500 | 208.3799 |  | 1
65 | 75 | 67 | 66.7494 | 37700 | 22620 | 0.9 | 1800 | 208.3799 |  | 1
65 | 80 | 67 | 51.5724 | 37700 | 34307 | 0.9 | 1800 | 208.3799 |  | 1
65 | 85 | 67 | 39.6049 | 37700 | 37700 | 0.9 | 1800 | 208.3799 |  | 1
65 | 75 | 71 | 82.6659 | 36800 | 8832 | 0.9 | 1200 | 208.3799 |  | 1
65 | 80 | 71 | 65.0618 | 36800 | 17664 | 0.9 | 1200 | 208.3799 |  | 1
65 | 85 | 71 | 51.076 | 36800 | 26496 | 0.9 | 1200 | 208.3799 |  | 1
65 | 75 | 71 | 82.6659 | 38200 | 8786 | 0.9 | 1500 | 208.3799 |  | 1
65 | 80 | 71 | 65.0618 | 38200 | 19864 | 0.9 | 1500 | 208.3799 |  | 1
65 | 85 | 71 | 51.076 | 38200 | 30178 | 0.9 | 1500 | 208.3799 |  | 1
65 | 75 | 71 | 82.6659 | 39400 | 9456 | 0.89 | 1800 | 208.3799 |  | 1
65 | 80 | 71 | 65.0618 | 39400 | 22458 | 0.89 | 1800 | 208.3799 |  | 1
65 | 85 | 71 | 51.076 | 39400 | 33884 | 0.89 | 1800 | 208.3799 |  | 1
75 | 75 | 63 | 52.1129 | 32300 | 27455 | 1.09 | 1200 | 208.3799 |  | 1
75 | 80 | 63 | 39.1676 | 32300 | 31654 | 1.09 | 1200 | 208.3799 |  | 1
75 | 85 | 63 | 29.0563 | 32300 | 32300 | 1.09 | 1200 | 208.3799 |  | 1
75 | 75 | 63 | 52.1129 | 34000 | 30940 | 1.08 | 1500 | 208.3799 |  | 1
75 | 80 | 63 | 39.1676 | 34000 | 34000 | 1.08 | 1500 | 208.3799 |  | 1
75 | 85 | 63 | 29.0563 | 34000 | 34000 | 1.08 | 1500 | 208.3799 |  | 1
75 | 75 | 63 | 52.1129 | 35400 | 33276 | 1.08 | 1800 | 208.3799 |  | 1
75 | 80 | 63 | 39.1676 | 35400 | 35400 | 1.08 | 1800 | 208.3799 |  | 1
75 | 85 | 63 | 29.0563 | 35400 | 35400 | 1.08 | 1800 | 208.3799 |  | 1
75 | 75 | 67 | 66.7494 | 33800 | 18252 | 1.08 | 1200 | 208.3799 |  | 1
75 | 80 | 67 | 51.5724 | 33800 | 26702 | 1.08 | 1200 | 208.3799 |  | 1
75 | 85 | 67 | 39.6049 | 33800 | 32448 | 1.08 | 1200 | 208.3799 |  | 1
75 | 75 | 67 | 66.7494 | 35200 | 20416 | 1.08 | 1500 | 208.3799 |  | 1
75 | 80 | 67 | 51.5724 | 35200 | 30624 | 1.08 | 1500 | 208.3799 |  | 1
75 | 85 | 67 | 39.6049 | 35200 | 34848 | 1.08 | 1500 | 208.3799 |  | 1
75 | 75 | 67 | 66.7494 | 36200 | 22082 | 1.08 | 1800 | 208.3799 |  | 1
75 | 80 | 67 | 51.5724 | 36200 | 33666 | 1.08 | 1800 | 208.3799 |  | 1
75 | 85 | 67 | 39.6049 | 36200 | 36200 | 1.08 | 1800 | 208.3799 |  | 1
75 | 75 | 71 | 82.6659 | 35400 | 8142 | 1.08 | 1200 | 208.3799 |  | 1
75 | 80 | 71 | 65.0618 | 35400 | 17346 | 1.08 | 1200 | 208.3799 |  | 1
75 | 85 | 71 | 51.076 | 35400 | 26196 | 1.08 | 1200 | 208.3799 |  | 1
75 | 75 | 71 | 82.6659 | 36700 | 8441 | 1.08 | 1500 | 208.3799 |  | 1
75 | 80 | 71 | 65.0618 | 36700 | 19818 | 1.08 | 1500 | 208.3799 |  | 1
75 | 85 | 71 | 51.076 | 36700 | 30094 | 1.08 | 1500 | 208.3799 |  | 1
75 | 75 | 71 | 82.6659 | 37800 | 9072 | 1.08 | 1800 | 208.3799 |  | 1
75 | 80 | 71 | 65.0618 | 37800 | 21924 | 1.08 | 1800 | 208.3799 |  | 1
75 | 85 | 71 | 51.076 | 37800 | 33642 | 1.08 | 1800 | 208.3799 |  | 1
85 | 75 | 63 | 52.1129 | 31100 | 27057 | 1.28 | 1200 | 208.3799 |  | 1
85 | 80 | 63 | 39.1676 | 31100 | 30478 | 1.28 | 1200 | 208.3799 |  | 1
85 | 85 | 63 | 29.0563 | 31100 | 31100 | 1.28 | 1200 | 208.3799 |  | 1
85 | 75 | 63 | 52.1129 | 32700 | 30411 | 1.28 | 1500 | 208.3799 |  | 1
85 | 80 | 63 | 39.1676 | 32700 | 32700 | 1.28 | 1500 | 208.3799 |  | 1
85 | 85 | 63 | 29.0563 | 32700 | 32700 | 1.28 | 1500 | 208.3799 |  | 1
85 | 75 | 63 | 52.1129 | 34100 | 32395 | 1.29 | 1800 | 208.3799 |  | 1
85 | 80 | 63 | 39.1676 | 34100 | 34100 | 1.29 | 1800 | 208.3799 |  | 1
85 | 85 | 63 | 29.0563 | 34100 | 34100 | 1.29 | 1800 | 208.3799 |  | 1
85 | 75 | 67 | 66.7494 | 32500 | 17875 | 1.28 | 1200 | 208.3799 |  | 1
85 | 80 | 67 | 51.5724 | 32500 | 26650 | 1.28 | 1200 | 208.3799 |  | 1
85 | 85 | 67 | 39.6049 | 32500 | 31525 | 1.28 | 1200 | 208.3799 |  | 1
85 | 75 | 67 | 66.7494 | 33800 | 19942 | 1.28 | 1500 | 208.3799 |  | 1
85 | 80 | 67 | 51.5724 | 33800 | 30082 | 1.28 | 1500 | 208.3799 |  | 1
85 | 85 | 67 | 39.6049 | 33800 | 33462 | 1.28 | 1500 | 208.3799 |  | 1
85 | 75 | 67 | 66.7494 | 34800 | 21924 | 1.29 | 1800 | 208.3799 |  | 1
85 | 80 | 67 | 51.5724 | 34800 | 32712 | 1.29 | 1800 | 208.3799 |  | 1
85 | 85 | 67 | 39.6049 | 34800 | 34800 | 1.29 | 1800 | 208.3799 |  | 1
85 | 75 | 71 | 82.6659 | 34000 | 7820 | 1.29 | 1200 | 208.3799 |  | 1
85 | 80 | 71 | 65.0618 | 34000 | 17340 | 1.29 | 1200 | 208.3799 |  | 1
85 | 85 | 71 | 51.076 | 34000 | 25840 | 1.29 | 1200 | 208.3799 |  | 1
85 | 75 | 71 | 82.6659 | 35400 | 8496 | 1.29 | 1500 | 208.3799 |  | 1
85 | 80 | 71 | 65.0618 | 35400 | 19470 | 1.29 | 1500 | 208.3799 |  | 1
85 | 85 | 71 | 51.076 | 35400 | 29736 | 1.29 | 1500 | 208.3799 |  | 1
85 | 75 | 71 | 82.6659 | 36300 | 9075 | 1.29 | 1800 | 208.3799 |  | 1
85 | 80 | 71 | 65.0618 | 36300 | 21780 | 1.29 | 1800 | 208.3799 |  | 1
85 | 85 | 71 | 51.076 | 36300 | 33396 | 1.29 | 1800 | 208.3799 |  | 1
95 | 75 | 63 | 52.1129 | 30000 | 26400 | 1.51 | 1200 | 208.3799 |  | 1
95 | 80 | 63 | 39.1676 | 30000 | 29700 | 1.51 | 1200 | 208.3799 |  | 1
95 | 85 | 63 | 29.0563 | 30000 | 30000 | 1.51 | 1200 | 208.3799 |  | 1
95 | 75 | 63 | 52.1129 | 31500 | 29610 | 1.51 | 1500 | 208.3799 |  | 1
95 | 80 | 63 | 39.1676 | 31500 | 31500 | 1.51 | 1500 | 208.3799 |  | 1
95 | 85 | 63 | 29.0563 | 31500 | 31500 | 1.51 | 1500 | 208.3799 |  | 1
95 | 75 | 63 | 52.1129 | 32900 | 31584 | 1.52 | 1800 | 208.3799 |  | 1
95 | 80 | 63 | 39.1676 | 32900 | 32900 | 1.52 | 1800 | 208.3799 |  | 1
95 | 85 | 63 | 29.0563 | 32900 | 32900 | 1.52 | 1800 | 208.3799 |  | 1
95 | 75 | 67 | 66.7494 | 31200 | 17472 | 1.51 | 1200 | 208.3799 |  | 1
95 | 80 | 67 | 51.5724 | 31200 | 26208 | 1.51 | 1200 | 208.3799 |  | 1
95 | 85 | 67 | 39.6049 | 31200 | 30576 | 1.51 | 1200 | 208.3799 |  | 1
95 | 75 | 67 | 66.7494 | 32500 | 19825 | 1.52 | 1500 | 208.3799 |  | 1
95 | 80 | 67 | 51.5724 | 32500 | 29900 | 1.52 | 1500 | 208.3799 |  | 1
95 | 85 | 67 | 39.6049 | 32500 | 32500 | 1.52 | 1500 | 208.3799 |  | 1
95 | 75 | 67 | 66.7494 | 33400 | 21710 | 1.52 | 1800 | 208.3799 |  | 1
95 | 80 | 67 | 51.5724 | 33400 | 31730 | 1.52 | 1800 | 208.3799 |  | 1
95 | 85 | 67 | 39.6049 | 33400 | 33400 | 1.52 | 1800 | 208.3799 |  | 1
95 | 75 | 71 | 82.6659 | 32700 | 7848 | 1.52 | 1200 | 208.3799 |  | 1
95 | 80 | 71 | 65.0618 | 32700 | 17004 | 1.52 | 1200 | 208.3799 |  | 1
95 | 85 | 71 | 51.076 | 32700 | 25833 | 1.52 | 1200 | 208.3799 |  | 1
95 | 75 | 71 | 82.6659 | 33900 | 8136 | 1.52 | 1500 | 208.3799 |  | 1
95 | 80 | 71 | 65.0618 | 33900 | 19323 | 1.52 | 1500 | 208.3799 |  | 1
95 | 85 | 71 | 51.076 | 33900 | 29832 | 1.52 | 1500 | 208.3799 |  | 1
95 | 75 | 71 | 82.6659 | 34900 | 9074 | 1.52 | 1800 | 208.3799 |  | 1
95 | 80 | 71 | 65.0618 | 34900 | 21638 | 1.52 | 1800 | 208.3799 |  | 1
95 | 85 | 71 | 51.076 | 34900 | 32457 | 1.52 | 1800 | 208.3799 |  | 1
65 | 75 | 63 | 52.1129 | 113800 | 81936 | 5.18 | 3120 | 375.0838 |  | 2
65 | 80 | 63 | 39.1676 | 113800 | 95592 | 5.18 | 3120 | 375.0838 |  | 2
65 | 85 | 63 | 29.0563 | 113800 | 109248 | 5.18 | 3120 | 375.0838 |  | 2
65 | 75 | 63 | 52.1129 | 119200 | 90592 | 5.18 | 3900 | 583.4637 |  | 2
65 | 80 | 63 | 39.1676 | 119200 | 107280 | 5.18 | 3900 | 583.4637 |  | 2
65 | 85 | 63 | 29.0563 | 119200 | 118008 | 5.18 | 3900 | 583.4637 |  | 2
65 | 75 | 63 | 52.1129 | 124200 | 99360 | 5.19 | 4680 | 771.0056 |  | 2
65 | 80 | 63 | 39.1676 | 124200 | 117990 | 5.19 | 4680 | 771.0056 |  | 2
65 | 85 | 63 | 29.0563 | 124200 | 124200 | 5.19 | 4680 | 771.0056 |  | 2
65 | 75 | 67 | 66.7494 | 119800 | 69484 | 5.18 | 3120 | 375.0838 |  | 2
65 | 80 | 67 | 51.5724 | 119800 | 83860 | 5.18 | 3120 | 375.0838 |  | 2
65 | 85 | 67 | 39.6049 | 119800 | 97038 | 5.18 | 3120 | 375.0838 |  | 2
65 | 75 | 67 | 66.7494 | 126500 | 75900 | 5.18 | 3900 | 583.4637 |  | 2
65 | 80 | 67 | 51.5724 | 126500 | 93610 | 5.18 | 3900 | 583.4637 |  | 2
65 | 85 | 67 | 39.6049 | 126500 | 110055 | 5.18 | 3900 | 583.4637 |  | 2
65 | 75 | 67 | 66.7494 | 130100 | 80662 | 5.19 | 4680 | 771.0056 |  | 2
65 | 80 | 67 | 51.5724 | 130100 | 100177 | 5.19 | 4680 | 771.0056 |  | 2
65 | 85 | 67 | 39.6049 | 130100 | 119692 | 5.19 | 4680 | 771.0056 |  | 2
65 | 75 | 71 | 82.6659 | 124900 | 54956 | 5.19 | 3120 | 375.0838 |  | 2
65 | 80 | 71 | 65.0618 | 124900 | 69944 | 5.19 | 3120 | 375.0838 |  | 2
65 | 85 | 71 | 51.076 | 124900 | 84932 | 5.19 | 3120 | 375.0838 |  | 2
65 | 75 | 71 | 82.6659 | 132100 | 58124 | 5.19 | 3900 | 583.4637 |  | 2
65 | 80 | 71 | 65.0618 | 132100 | 77939 | 5.19 | 3900 | 583.4637 |  | 2
65 | 85 | 71 | 51.076 | 132100 | 93791 | 5.19 | 3900 | 583.4637 |  | 2
65 | 75 | 71 | 82.6659 | 137500 | 63250 | 5.19 | 4680 | 843.9385 |  | 2
65 | 80 | 71 | 65.0618 | 137500 | 83875 | 5.19 | 4680 | 843.9385 |  | 2
65 | 85 | 71 | 51.076 | 137500 | 103125 | 5.19 | 4680 | 843.9385 |  | 2
75 | 75 | 63 | 52.1129 | 110400 | 80592 | 5.76 | 3120 | 375.0838 |  | 2
75 | 80 | 63 | 39.1676 | 110400 | 94944 | 5.76 | 3120 | 375.0838 |  | 2
75 | 85 | 63 | 29.0563 | 110400 | 107088 | 5.76 | 3120 | 375.0838 |  | 2
75 | 75 | 63 | 52.1129 | 115600 | 89012 | 5.78 | 3900 | 583.4637 |  | 2
75 | 80 | 63 | 39.1676 | 115600 | 106352 | 5.78 | 3900 | 583.4637 |  | 2
75 | 85 | 63 | 29.0563 | 115600 | 115600 | 5.78 | 3900 | 583.4637 |  | 2
75 | 75 | 63 | 52.1129 | 120600 | 97686 | 5.79 | 4680 | 771.0056 |  | 2
75 | 80 | 63 | 39.1676 | 120600 | 116982 | 5.79 | 4680 | 771.0056 |  | 2
75 | 85 | 63 | 29.0563 | 120600 | 120600 | 5.79 | 4680 | 771.0056 |  | 2
75 | 75 | 67 | 66.7494 | 116300 | 67454 | 5.78 | 3120 | 375.0838 |  | 2
75 | 80 | 67 | 51.5724 | 116300 | 82573 | 5.78 | 3120 | 375.0838 |  | 2
75 | 85 | 67 | 39.6049 | 116300 | 95366 | 5.78 | 3120 | 375.0838 |  | 2
75 | 75 | 67 | 66.7494 | 122500 | 74725 | 5.8 | 3900 | 583.4637 |  | 2
75 | 80 | 67 | 51.5724 | 122500 | 91875 | 5.8 | 3900 | 583.4637 |  | 2
75 | 85 | 67 | 39.6049 | 122500 | 109025 | 5.8 | 3900 | 583.4637 |  | 2
75 | 75 | 67 | 66.7494 | 126900 | 79947 | 5.81 | 4680 | 771.0056 |  | 2
75 | 80 | 67 | 51.5724 | 126900 | 100251 | 5.81 | 4680 | 771.0056 |  | 2
75 | 85 | 67 | 39.6049 | 126900 | 119286 | 5.81 | 4680 | 771.0056 |  | 2
75 | 75 | 71 | 82.6659 | 120800 | 54360 | 5.85 | 3120 | 375.0838 |  | 2
75 | 80 | 71 | 65.0618 | 120800 | 68856 | 5.85 | 3120 | 375.0838 |  | 2
75 | 85 | 71 | 51.076 | 120800 | 82144 | 5.85 | 3120 | 375.0838 |  | 2
75 | 75 | 71 | 82.6659 | 127500 | 57375 | 5.87 | 3900 | 583.4637 |  | 2
75 | 80 | 71 | 65.0618 | 127500 | 75225 | 5.87 | 3900 | 583.4637 |  | 2
75 | 85 | 71 | 51.076 | 127500 | 93075 | 5.87 | 3900 | 583.4637 |  | 2
75 | 75 | 71 | 82.6659 | 132400 | 60904 | 5.88 | 4680 | 771.0056 |  | 2
75 | 80 | 71 | 65.0618 | 132400 | 82088 | 5.88 | 4680 | 771.0056 |  | 2
75 | 85 | 71 | 51.076 | 132400 | 100624 | 5.88 | 4680 | 771.0056 |  | 2
85 | 75 | 63 | 52.1129 | 105400 | 77996 | 6.6 | 3120 | 333.4078 |  | 2
85 | 80 | 63 | 39.1676 | 105400 | 92752 | 6.6 | 3120 | 333.4078 |  | 2
85 | 85 | 63 | 29.0563 | 105400 | 103292 | 6.6 | 3120 | 333.4078 |  | 2
85 | 75 | 63 | 52.1129 | 110600 | 87374 | 6.62 | 3900 | 583.4637 |  | 2
85 | 80 | 63 | 39.1676 | 110600 | 103964 | 6.62 | 3900 | 583.4637 |  | 2
85 | 85 | 63 | 29.0563 | 110600 | 110600 | 6.62 | 3900 | 583.4637 |  | 2
85 | 75 | 63 | 52.1129 | 115300 | 95699 | 6.64 | 4680 | 771.0056 |  | 2
85 | 80 | 63 | 39.1676 | 115300 | 112994 | 6.64 | 4680 | 771.0056 |  | 2
85 | 85 | 63 | 29.0563 | 115300 | 115300 | 6.64 | 4680 | 771.0056 |  | 2
85 | 75 | 67 | 66.7494 | 111000 | 65490 | 6.63 | 3120 | 375.0838 |  | 2
85 | 80 | 67 | 51.5724 | 111000 | 79920 | 6.63 | 3120 | 375.0838 |  | 2
85 | 85 | 67 | 39.6049 | 111000 | 93240 | 6.63 | 3120 | 375.0838 |  | 2
85 | 75 | 67 | 66.7494 | 116700 | 72354 | 6.66 | 3900 | 583.4637 |  | 2
85 | 80 | 67 | 51.5724 | 116700 | 89859 | 6.66 | 3900 | 583.4637 |  | 2
85 | 85 | 67 | 39.6049 | 116700 | 106197 | 6.66 | 3900 | 583.4637 |  | 2
85 | 75 | 67 | 66.7494 | 120900 | 77376 | 6.66 | 4680 | 771.0056 |  | 2
85 | 80 | 67 | 51.5724 | 120900 | 97929 | 6.66 | 4680 | 771.0056 |  | 2
85 | 85 | 67 | 39.6049 | 120900 | 116064 | 6.66 | 4680 | 771.0056 |  | 2
85 | 75 | 71 | 82.6659 | 116100 | 52245 | 6.66 | 3120 | 375.0838 |  | 2
85 | 80 | 71 | 65.0618 | 116100 | 67338 | 6.66 | 3120 | 375.0838 |  | 2
85 | 85 | 71 | 51.076 | 116100 | 81270 | 6.66 | 3120 | 375.0838 |  | 2
85 | 75 | 71 | 82.6659 | 122200 | 54990 | 6.68 | 3900 | 583.4637 |  | 2
85 | 80 | 71 | 65.0618 | 122200 | 74542 | 6.68 | 3900 | 583.4637 |  | 2
85 | 85 | 71 | 51.076 | 122200 | 90428 | 6.68 | 3900 | 583.4637 |  | 2
85 | 75 | 71 | 82.6659 | 126700 | 59549 | 6.7 | 4680 | 771.0056 |  | 2
85 | 80 | 71 | 65.0618 | 126700 | 79821 | 6.7 | 4680 | 771.0056 |  | 2
85 | 85 | 71 | 51.076 | 126700 | 100093 | 6.7 | 4680 | 771.0056 |  | 2
95 | 75 | 63 | 52.1129 | 100000 | 76000 | 7.51 | 3120 | 333.4078 |  | 2
95 | 80 | 63 | 39.1676 | 100000 | 90000 | 7.51 | 3120 | 333.4078 |  | 2
95 | 85 | 63 | 29.0563 | 100000 | 99000 | 7.51 | 3120 | 333.4078 |  | 2
95 | 75 | 63 | 52.1129 | 105800 | 84640 | 7.51 | 3900 | 583.4637 |  | 2
95 | 80 | 63 | 39.1676 | 105800 | 100510 | 7.51 | 3900 | 583.4637 |  | 2
95 | 85 | 63 | 29.0563 | 105800 | 105800 | 7.51 | 3900 | 583.4637 |  | 2
95 | 75 | 63 | 52.1129 | 110500 | 93925 | 7.53 | 4680 | 771.0056 |  | 2
95 | 80 | 63 | 39.1676 | 110500 | 109395 | 7.53 | 4680 | 771.0056 |  | 2
95 | 85 | 63 | 29.0563 | 110500 | 110500 | 7.53 | 4680 | 771.0056 |  | 2
95 | 75 | 67 | 66.7494 | 106000 | 63600 | 7.55 | 3120 | 375.0838 |  | 2
95 | 80 | 67 | 51.5724 | 106000 | 78440 | 7.55 | 3120 | 375.0838 |  | 2
95 | 85 | 67 | 39.6049 | 106000 | 91160 | 7.55 | 3120 | 375.0838 |  | 2
95 | 75 | 67 | 66.7494 | 110800 | 69804 | 7.08 | 3900 | 583.4637 |  | 2
95 | 80 | 67 | 51.5724 | 110800 | 86424 | 7.08 | 3900 | 583.4637 |  | 2
95 | 85 | 67 | 39.6049 | 110800 | 103044 | 7.08 | 3900 | 583.4637 |  | 2
95 | 75 | 67 | 66.7494 | 114700 | 75702 | 7.6 | 4680 | 771.0056 |  | 2
95 | 80 | 67 | 51.5724 | 114700 | 95201 | 7.6 | 4680 | 771.0056 |  | 2
95 | 85 | 67 | 39.6049 | 114700 | 111259 | 7.6 | 4680 | 771.0056 |  | 2
95 | 75 | 71 | 82.6659 | 110900 | 49905 | 7.58 | 3120 | 375.0838 |  | 2
95 | 80 | 71 | 65.0618 | 110900 | 65431 | 7.58 | 3120 | 375.0838 |  | 2
95 | 85 | 71 | 51.076 | 110900 | 78739 | 7.58 | 3120 | 375.0838 |  | 2
95 | 75 | 71 | 82.6659 | 116600 | 53636 | 7.61 | 3900 | 583.4637 |  | 2
95 | 80 | 71 | 65.0618 | 116600 | 72292 | 7.61 | 3900 | 583.4637 |  | 2
95 | 85 | 71 | 51.076 | 116600 | 88616 | 7.61 | 3900 | 583.4637 |  | 2
95 | 75 | 71 | 82.6659 | 120700 | 55522 | 7.62 | 4680 | 771.0056 |  | 2
95 | 80 | 71 | 65.0618 | 120700 | 78455 | 7.62 | 4680 | 771.0056 |  | 2
95 | 85 | 71 | 51.076 | 120700 | 97767 | 7.62 | 4680 | 771.0056 |  | 2
65 | 75 | 63 | 52.1129 | 155200 | 111744 | 8.72 | 4160 | 687.6536 |  | 3
65 | 80 | 63 | 39.1676 | 155200 | 130368 | 8.72 | 4160 | 687.6536 |  | 3
65 | 85 | 63 | 29.0563 | 155200 | 147440 | 8.72 | 4160 | 687.6536 |  | 3
65 | 75 | 63 | 52.1129 | 164500 | 126665 | 8.75 | 5200 | 1041.8994 |  | 3
65 | 80 | 63 | 39.1676 | 164500 | 148050 | 8.75 | 5200 | 1041.8994 |  | 3
65 | 85 | 63 | 29.0563 | 164500 | 164500 | 8.75 | 5200 | 1041.8994 |  | 3
65 | 75 | 63 | 52.1129 | 171300 | 138753 | 8.77 | 6240 | 1479.4972 |  | 3
65 | 80 | 63 | 39.1676 | 171300 | 164448 | 8.77 | 6240 | 1479.4972 |  | 3
65 | 85 | 63 | 29.0563 | 171300 | 171300 | 8.77 | 6240 | 1479.4972 |  | 3
65 | 75 | 67 | 66.7494 | 163200 | 91392 | 8.75 | 4160 | 687.6536 |  | 3
65 | 80 | 67 | 51.5724 | 163200 | 112608 | 8.75 | 4160 | 687.6536 |  | 3
65 | 85 | 67 | 39.6049 | 163200 | 132192 | 8.75 | 4160 | 687.6536 |  | 3
65 | 75 | 67 | 66.7494 | 172100 | 101539 | 8.77 | 5200 | 1041.8994 |  | 3
65 | 80 | 67 | 51.5724 | 172100 | 127354 | 8.77 | 5200 | 1041.8994 |  | 3
65 | 85 | 67 | 39.6049 | 172100 | 149727 | 8.77 | 5200 | 1041.8994 |  | 3
65 | 75 | 67 | 66.7494 | 179400 | 113022 | 8.79 | 6240 | 1479.4972 |  | 3
65 | 80 | 67 | 51.5724 | 179400 | 141726 | 8.79 | 6240 | 1479.4972 |  | 3
65 | 85 | 67 | 39.6049 | 179400 | 166842 | 8.79 | 6240 | 1479.4972 |  | 3
65 | 75 | 71 | 82.6659 | 174000 | 73080 | 8.78 | 4160 | 687.6536 |  | 3
65 | 80 | 71 | 65.0618 | 174000 | 95700 | 8.78 | 4160 | 687.6536 |  | 3
65 | 85 | 71 | 51.076 | 174000 | 116580 | 8.78 | 4160 | 687.6536 |  | 3
65 | 75 | 71 | 82.6659 | 183200 | 78776 | 8.8 | 5200 | 1041.8994 |  | 3
65 | 80 | 71 | 65.0618 | 183200 | 108088 | 8.8 | 5200 | 1041.8994 |  | 3
65 | 85 | 71 | 51.076 | 183200 | 133736 | 8.8 | 5200 | 1041.8994 |  | 3
65 | 75 | 71 | 82.6659 | 189800 | 85410 | 8.81 | 6240 | 1479.4972 |  | 3
65 | 80 | 71 | 65.0618 | 189800 | 117676 | 8.81 | 6240 | 1479.4972 |  | 3
65 | 85 | 71 | 51.076 | 189800 | 148044 | 8.81 | 6240 | 1479.4972 |  | 3
75 | 75 | 63 | 52.1129 | 144800 | 104256 | 9.9 | 4160 | 687.6536 |  | 3
75 | 80 | 63 | 39.1676 | 144800 | 123080 | 9.9 | 4160 | 687.6536 |  | 3
75 | 85 | 63 | 29.0563 | 144800 | 140456 | 9.9 | 4160 | 687.6536 |  | 3
75 | 75 | 63 | 52.1129 | 153300 | 119574 | 9.93 | 5200 | 1041.8994 |  | 3
75 | 80 | 63 | 39.1676 | 153300 | 141036 | 9.93 | 5200 | 1041.8994 |  | 3
75 | 85 | 63 | 29.0563 | 153300 | 153300 | 9.93 | 5200 | 1041.8994 |  | 3
75 | 75 | 63 | 52.1129 | 160100 | 132883 | 9.95 | 6240 | 1479.4972 |  | 3
75 | 80 | 63 | 39.1676 | 160100 | 156898 | 9.95 | 6240 | 1479.4972 |  | 3
75 | 85 | 63 | 29.0563 | 160100 | 160100 | 9.95 | 6240 | 1479.4972 |  | 3
75 | 75 | 67 | 66.7494 | 152000 | 85120 | 9.92 | 4160 | 687.6536 |  | 3
75 | 80 | 67 | 51.5724 | 152000 | 106400 | 9.92 | 4160 | 687.6536 |  | 3
75 | 85 | 67 | 39.6049 | 152000 | 124640 | 9.92 | 4160 | 687.6536 |  | 3
75 | 75 | 67 | 66.7494 | 160800 | 98088 | 9.95 | 5200 | 1041.8994 |  | 3
75 | 80 | 67 | 51.5724 | 160800 | 120600 | 9.95 | 5200 | 1041.8994 |  | 3
75 | 85 | 67 | 39.6049 | 160800 | 143112 | 9.95 | 5200 | 1041.8994 |  | 3
75 | 75 | 67 | 66.7494 | 167500 | 107200 | 9.97 | 6240 | 1479.4972 |  | 3
75 | 80 | 67 | 51.5724 | 167500 | 134000 | 9.97 | 6240 | 1479.4972 |  | 3
75 | 85 | 67 | 39.6049 | 167500 | 160800 | 9.97 | 6240 | 1479.4972 |  | 3
75 | 75 | 71 | 82.6659 | 162300 | 66543 | 9.96 | 4160 | 687.6536 |  | 3
75 | 80 | 71 | 65.0618 | 162300 | 89265 | 9.96 | 4160 | 687.6536 |  | 3
75 | 85 | 71 | 51.076 | 162300 | 110364 | 9.96 | 4160 | 687.6536 |  | 3
75 | 75 | 71 | 82.6659 | 170800 | 71736 | 9.98 | 5200 | 1041.8994 |  | 3
75 | 80 | 71 | 65.0618 | 170800 | 100772 | 9.98 | 5200 | 1041.8994 |  | 3
75 | 85 | 71 | 51.076 | 170800 | 126392 | 9.98 | 5200 | 1041.8994 |  | 3
75 | 75 | 71 | 82.6659 | 177000 | 77880 | 9.99 | 6240 | 1479.4972 |  | 3
75 | 80 | 71 | 65.0618 | 177000 | 109740 | 9.99 | 6240 | 1479.4972 |  | 3
75 | 85 | 71 | 51.076 | 177000 | 139830 | 9.99 | 6240 | 1479.4972 |  | 3
85 | 75 | 63 | 52.1129 | 133700 | 97601 | 11.22 | 4160 | 625.1397 |  | 3
85 | 80 | 63 | 39.1676 | 133700 | 116319 | 11.22 | 4160 | 625.1397 |  | 3
85 | 85 | 63 | 29.0563 | 133700 | 132363 | 11.22 | 4160 | 625.1397 |  | 3
85 | 75 | 63 | 52.1129 | 141300 | 111627 | 11.25 | 5200 | 1041.8994 |  | 3
85 | 80 | 63 | 39.1676 | 141300 | 134235 | 11.25 | 5200 | 1041.8994 |  | 3
85 | 85 | 63 | 29.0563 | 141300 | 141300 | 11.25 | 5200 | 1041.8994 |  | 3
85 | 75 | 63 | 52.1129 | 148400 | 126140 | 11.28 | 6240 | 1479.4972 |  | 3
85 | 80 | 63 | 39.1676 | 148400 | 146916 | 11.28 | 6240 | 1479.4972 |  | 3
85 | 85 | 63 | 29.0563 | 148400 | 148400 | 11.28 | 6240 | 1479.4972 |  | 3
85 | 75 | 67 | 66.7494 | 140300 | 77165 | 11.25 | 4160 | 687.6536 |  | 3
85 | 80 | 67 | 51.5724 | 140300 | 101016 | 11.25 | 4160 | 687.6536 |  | 3
85 | 85 | 67 | 39.6049 | 140300 | 117852 | 11.25 | 4160 | 687.6536 |  | 3
85 | 75 | 67 | 66.7494 | 148900 | 89340 | 11.28 | 5200 | 1041.8994 |  | 3
85 | 80 | 67 | 51.5724 | 148900 | 114653 | 11.28 | 5200 | 1041.8994 |  | 3
85 | 85 | 67 | 39.6049 | 148900 | 136988 | 11.28 | 5200 | 1041.8994 |  | 3
85 | 75 | 67 | 66.7494 | 154800 | 97524 | 11.3 | 6240 | 1479.4972 |  | 3
85 | 80 | 67 | 51.5724 | 154800 | 126936 | 11.3 | 6240 | 1479.4972 |  | 3
85 | 85 | 67 | 39.6049 | 154800 | 151704 | 11.3 | 6240 | 1479.4972 |  | 3
85 | 75 | 71 | 82.6659 | 150200 | 60080 | 11.28 | 4160 | 687.6536 |  | 3
85 | 80 | 71 | 65.0618 | 150200 | 82610 | 11.28 | 4160 | 687.6536 |  | 3
85 | 85 | 71 | 51.076 | 150200 | 103638 | 11.28 | 4160 | 687.6536 |  | 3
85 | 75 | 71 | 82.6659 | 158100 | 64821 | 11.31 | 5200 | 1041.8994 |  | 3
85 | 80 | 71 | 65.0618 | 158100 | 94860 | 11.31 | 5200 | 1041.8994 |  | 3
85 | 85 | 71 | 51.076 | 158100 | 118575 | 11.31 | 5200 | 1041.8994 |  | 3
85 | 75 | 71 | 82.6659 | 163600 | 70348 | 11.32 | 6240 | 1479.4972 |  | 3
85 | 80 | 71 | 65.0618 | 163600 | 103068 | 11.32 | 6240 | 1479.4972 |  | 3
85 | 85 | 71 | 51.076 | 163600 | 132516 | 11.32 | 6240 | 1479.4972 |  | 3
95 | 75 | 63 | 52.1129 | 122300 | 91725 | 12.69 | 4160 | 625.1397 |  | 3
95 | 80 | 63 | 39.1676 | 122300 | 108847 | 12.69 | 4160 | 625.1397 |  | 3
95 | 85 | 63 | 29.0563 | 122300 | 122300 | 12.69 | 4160 | 625.1397 |  | 3
95 | 75 | 63 | 52.1129 | 129500 | 104895 | 12.71 | 5200 | 958.5475 |  | 3
95 | 80 | 63 | 39.1676 | 129500 | 125615 | 12.71 | 5200 | 958.5475 |  | 3
95 | 85 | 63 | 29.0563 | 129500 | 129500 | 12.71 | 5200 | 958.5475 |  | 3
95 | 75 | 63 | 52.1129 | 136700 | 118929 | 12.73 | 6240 | 1479.4972 |  | 3
95 | 80 | 63 | 39.1676 | 136700 | 136700 | 12.73 | 6240 | 1479.4972 |  | 3
95 | 85 | 63 | 29.0563 | 136700 | 136700 | 12.73 | 6240 | 1479.4972 |  | 3
95 | 75 | 67 | 66.7494 | 128700 | 70785 | 12.71 | 4160 | 625.1397 |  | 3
95 | 80 | 67 | 51.5724 | 128700 | 92664 | 12.71 | 4160 | 625.1397 |  | 3
95 | 85 | 67 | 39.6049 | 128700 | 110682 | 12.71 | 4160 | 625.1397 |  | 3
95 | 75 | 67 | 66.7494 | 136300 | 83143 | 12.73 | 5200 | 1041.8994 |  | 3
95 | 80 | 67 | 51.5724 | 136300 | 107677 | 12.73 | 5200 | 1041.8994 |  | 3
95 | 85 | 67 | 39.6049 | 136300 | 129485 | 12.73 | 5200 | 1041.8994 |  | 3
95 | 75 | 67 | 66.7494 | 141700 | 90688 | 12.75 | 6240 | 1479.4972 |  | 3
95 | 80 | 67 | 51.5724 | 141700 | 120445 | 12.75 | 6240 | 1479.4972 |  | 3
95 | 85 | 67 | 39.6049 | 141700 | 140283 | 12.75 | 6240 | 1479.4972 |  | 3
95 | 75 | 71 | 82.6659 | 137800 | 52364 | 12.74 | 4160 | 687.6536 |  | 3
95 | 80 | 71 | 65.0618 | 137800 | 74412 | 12.74 | 4160 | 687.6536 |  | 3
95 | 85 | 71 | 51.076 | 137800 | 97838 | 12.74 | 4160 | 687.6536 |  | 3
95 | 75 | 71 | 82.6659 | 144600 | 57840 | 12.75 | 5200 | 1041.8994 |  | 3
95 | 80 | 71 | 65.0618 | 144600 | 86760 | 12.75 | 5200 | 1041.8994 |  | 3
95 | 85 | 71 | 51.076 | 144600 | 111342 | 12.75 | 5200 | 1041.8994 |  | 3
95 | 75 | 71 | 82.6659 | 149600 | 67320 | 12.77 | 6240 | 1479.4972 |  | 3
95 | 80 | 71 | 65.0618 | 149600 | 95744 | 12.77 | 6240 | 1479.4972 |  | 3
95 | 85 | 71 | 51.076 | 149600 | 124168 | 12.77 | 6240 | 1479.4972 |  | 3
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 3
Degradation Coefficient (C_d)
IEER or SEER | 17.5
Standby Power (W)
Crankcase Heater Power (W)
Net
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 75 | 63 | 52.1129 | 36100 | 32490 | 1.02 | 1600 | 208.3799 |  | 1
65 | 80 | 63 | 39.1676 | 36100 | 36100 | 1.02 | 1600 | 208.3799 |  | 1
65 | 85 | 63 | 29.0563 | 36100 | 36100 | 1.02 | 1600 | 208.3799 |  | 1
65 | 75 | 63 | 52.1129 | 38100 | 37338 | 1.01 | 2000 | 208.3799 |  | 1
65 | 80 | 63 | 39.1676 | 38100 | 38100 | 1.01 | 2000 | 208.3799 |  | 1
65 | 85 | 63 | 29.0563 | 38100 | 38100 | 1.01 | 2000 | 208.3799 |  | 1
65 | 75 | 63 | 52.1129 | 39800 | 39800 | 1.01 | 2400 | 208.3799 |  | 1
65 | 80 | 63 | 39.1676 | 39800 | 39800 | 1.01 | 2400 | 208.3799 |  | 1
65 | 85 | 63 | 29.0563 | 39800 | 39800 | 1.01 | 2400 | 208.3799 |  | 1
65 | 75 | 67 | 66.7494 | 37900 | 21603 | 1.01 | 1600 | 208.3799 |  | 1
65 | 80 | 67 | 51.5724 | 37900 | 32594 | 1.01 | 1600 | 208.3799 |  | 1
65 | 85 | 67 | 39.6049 | 37900 | 37900 | 1.01 | 1600 | 208.3799 |  | 1
65 | 75 | 67 | 66.7494 | 39400 | 24428 | 1.01 | 2000 | 208.3799 |  | 1
65 | 80 | 67 | 51.5724 | 39400 | 37036 | 1.01 | 2000 | 208.3799 |  | 1
65 | 85 | 67 | 39.6049 | 39400 | 39400 | 1.01 | 2000 | 208.3799 |  | 1
65 | 75 | 67 | 66.7494 | 40500 | 27135 | 1.01 | 2400 | 208.3799 |  | 1
65 | 80 | 67 | 51.5724 | 40500 | 40500 | 1.01 | 2400 | 208.3799 |  | 1
65 | 85 | 67 | 39.6049 | 40500 | 40500 | 1.01 | 2400 | 208.3799 |  | 1
65 | 75 | 71 | 82.6659 | 40100 | 10025 | 1.01 | 1600 | 208.3799 |  | 1
65 | 80 | 71 | 65.0618 | 40100 | 21654 | 1.01 | 1600 | 208.3799 |  | 1
65 | 85 | 71 | 51.076 | 40100 | 32481 | 1.01 | 1600 | 208.3799 |  | 1
65 | 75 | 71 | 82.6659 | 41500 | 10790 | 1.01 | 2000 | 208.3799 |  | 1
65 | 80 | 71 | 65.0618 | 41500 | 24485 | 1.01 | 2000 | 208.3799 |  | 1
65 | 85 | 71 | 51.076 | 41500 | 37350 | 1.01 | 2000 | 208.3799 |  | 1
65 | 75 | 71 | 82.6659 | 42700 | 11529 | 1.01 | 2400 | 250.0559 |  | 1
65 | 80 | 71 | 65.0618 | 42700 | 27755 | 1.01 | 2400 | 250.0559 |  | 1
65 | 85 | 71 | 51.076 | 42700 | 41846 | 1.01 | 2400 | 250.0559 |  | 1
75 | 75 | 63 | 52.1129 | 33800 | 30758 | 1.22 | 1600 | 208.3799 |  | 1
75 | 80 | 63 | 39.1676 | 33800 | 33800 | 1.22 | 1600 | 208.3799 |  | 1
75 | 85 | 63 | 29.0563 | 33800 | 33800 | 1.22 | 1600 | 208.3799 |  | 1
75 | 75 | 63 | 52.1129 | 35800 | 35800 | 1.22 | 2000 | 208.3799 |  | 1
75 | 80 | 63 | 39.1676 | 35800 | 35800 | 1.22 | 2000 | 208.3799 |  | 1
75 | 85 | 63 | 29.0563 | 35800 | 35800 | 1.22 | 2000 | 208.3799 |  | 1
75 | 75 | 63 | 52.1129 | 37500 | 37500 | 1.22 | 2400 | 208.3799 |  | 1
75 | 80 | 63 | 39.1676 | 37500 | 37500 | 1.22 | 2400 | 208.3799 |  | 1
75 | 85 | 63 | 29.0563 | 37500 | 37500 | 1.22 | 2400 | 208.3799 |  | 1
75 | 75 | 67 | 66.7494 | 35500 | 20235 | 1.22 | 1600 | 208.3799 |  | 1
75 | 80 | 67 | 51.5724 | 35500 | 30885 | 1.22 | 1600 | 208.3799 |  | 1
75 | 85 | 67 | 39.6049 | 35500 | 35500 | 1.22 | 1600 | 208.3799 |  | 1
75 | 75 | 67 | 66.7494 | 36900 | 22878 | 1.22 | 2000 | 208.3799 |  | 1
75 | 80 | 67 | 51.5724 | 36900 | 35424 | 1.22 | 2000 | 208.3799 |  | 1
75 | 85 | 67 | 39.6049 | 36900 | 36900 | 1.22 | 2000 | 208.3799 |  | 1
75 | 75 | 67 | 66.7494 | 38000 | 25460 | 1.22 | 2400 | 208.3799 |  | 1
75 | 80 | 67 | 51.5724 | 38000 | 38000 | 1.22 | 2400 | 208.3799 |  | 1
75 | 85 | 67 | 39.6049 | 38000 | 38000 | 1.22 | 2400 | 208.3799 |  | 1
75 | 75 | 71 | 82.6659 | 37600 | 8272 | 1.22 | 1600 | 208.3799 |  | 1
75 | 80 | 71 | 65.0618 | 37600 | 20304 | 1.22 | 1600 | 208.3799 |  | 1
75 | 85 | 71 | 51.076 | 37600 | 31208 | 1.22 | 1600 | 208.3799 |  | 1
75 | 75 | 71 | 82.6659 | 39000 | 9360 | 1.22 | 2000 | 208.3799 |  | 1
75 | 80 | 71 | 65.0618 | 39000 | 23400 | 1.22 | 2000 | 208.3799 |  | 1
75 | 85 | 71 | 51.076 | 39000 | 35880 | 1.22 | 2000 | 208.3799 |  | 1
75 | 75 | 71 | 82.6659 | 40000 | 10000 | 1.22 | 2400 | 208.3799 |  | 1
75 | 80 | 71 | 65.0618 | 40000 | 26400 | 1.22 | 2400 | 208.3799 |  | 1
75 | 85 | 71 | 51.076 | 40000 | 40000 | 1.22 | 2400 | 208.3799 |  | 1
85 | 75 | 63 | 52.1129 | 31700 | 29481 | 1.44 | 1600 | 208.3799 |  | 1
85 | 80 | 63 | 39.1676 | 31700 | 31700 | 1.44 | 1600 | 208.3799 |  | 1
85 | 85 | 63 | 29.0563 | 31700 | 31700 | 1.44 | 1600 | 208.3799 |  | 1
85 | 75 | 63 | 52.1129 | 33700 | 33700 | 1.44 | 2000 | 208.3799 |  | 1
85 | 80 | 63 | 39.1676 | 33700 | 33700 | 1.44 | 2000 | 208.3799 |  | 1
85 | 85 | 63 | 29.0563 | 33700 | 33700 | 1.44 | 2000 | 208.3799 |  | 1
85 | 75 | 63 | 52.1129 | 35200 | 35200 | 1.45 | 2400 | 208.3799 |  | 1
85 | 80 | 63 | 39.1676 | 35200 | 35200 | 1.45 | 2400 | 208.3799 |  | 1
85 | 85 | 63 | 29.0563 | 35200 | 35200 | 1.45 | 2400 | 208.3799 |  | 1
85 | 75 | 67 | 66.7494 | 33100 | 18536 | 1.44 | 1600 | 208.3799 |  | 1
85 | 80 | 67 | 51.5724 | 33100 | 29459 | 1.44 | 1600 | 208.3799 |  | 1
85 | 85 | 67 | 39.6049 | 33100 | 33100 | 1.44 | 1600 | 208.3799 |  | 1
85 | 75 | 67 | 66.7494 | 34500 | 21390 | 1.45 | 2000 | 208.3799 |  | 1
85 | 80 | 67 | 51.5724 | 34500 | 33810 | 1.45 | 2000 | 208.3799 |  | 1
85 | 85 | 67 | 39.6049 | 34500 | 34500 | 1.45 | 2000 | 208.3799 |  | 1
85 | 75 | 67 | 66.7494 | 35500 | 24495 | 1.45 | 2400 | 208.3799 |  | 1
85 | 80 | 67 | 51.5724 | 35500 | 35500 | 1.45 | 2400 | 208.3799 |  | 1
85 | 85 | 67 | 39.6049 | 35500 | 35500 | 1.45 | 2400 | 208.3799 |  | 1
85 | 75 | 71 | 82.6659 | 35200 | 7040 | 1.45 | 1600 | 208.3799 |  | 1
85 | 80 | 71 | 65.0618 | 35200 | 19008 | 1.45 | 1600 | 208.3799 |  | 1
85 | 85 | 71 | 51.076 | 35200 | 29568 | 1.45 | 1600 | 208.3799 |  | 1
85 | 75 | 71 | 82.6659 | 36500 | 8030 | 1.45 | 2000 | 208.3799 |  | 1
85 | 80 | 71 | 65.0618 | 36500 | 21900 | 1.45 | 2000 | 208.3799 |  | 1
85 | 85 | 71 | 51.076 | 36500 | 34310 | 1.45 | 2000 | 208.3799 |  | 1
85 | 75 | 71 | 82.6659 | 37400 | 8976 | 1.45 | 2400 | 208.3799 |  | 1
85 | 80 | 71 | 65.0618 | 37400 | 25058 | 1.45 | 2400 | 208.3799 |  | 1
85 | 85 | 71 | 51.076 | 37400 | 37400 | 1.45 | 2400 | 208.3799 |  | 1
95 | 75 | 63 | 52.1129 | 29600 | 28120 | 1.69 | 1600 | 208.3799 |  | 1
95 | 80 | 63 | 39.1676 | 29600 | 29600 | 1.69 | 1600 | 208.3799 |  | 1
95 | 85 | 63 | 29.0563 | 29600 | 29600 | 1.69 | 1600 | 208.3799 |  | 1
95 | 75 | 63 | 52.1129 | 31400 | 31400 | 1.7 | 2000 | 208.3799 |  | 1
95 | 80 | 63 | 39.1676 | 31400 | 31400 | 1.7 | 2000 | 208.3799 |  | 1
95 | 85 | 63 | 29.0563 | 31400 | 31400 | 1.7 | 2000 | 208.3799 |  | 1
95 | 75 | 63 | 52.1129 | 32900 | 32900 | 1.71 | 2400 | 208.3799 |  | 1
95 | 80 | 63 | 39.1676 | 32900 | 32900 | 1.71 | 2400 | 208.3799 |  | 1
95 | 85 | 63 | 29.0563 | 32900 | 32900 | 1.71 | 2400 | 208.3799 |  | 1
95 | 75 | 67 | 66.7494 | 30900 | 16995 | 1.7 | 1600 | 208.3799 |  | 1
95 | 80 | 67 | 51.5724 | 30900 | 28119 | 1.7 | 1600 | 208.3799 |  | 1
95 | 85 | 67 | 39.6049 | 30900 | 30900 | 1.7 | 1600 | 208.3799 |  | 1
95 | 75 | 67 | 66.7494 | 32000 | 20160 | 1.7 | 2000 | 208.3799 |  | 1
95 | 80 | 67 | 51.5724 | 32000 | 32000 | 1.7 | 2000 | 208.3799 |  | 1
95 | 85 | 67 | 39.6049 | 32000 | 32000 | 1.7 | 2000 | 208.3799 |  | 1
95 | 75 | 67 | 66.7494 | 33100 | 22839 | 1.71 | 2400 | 208.3799 |  | 1
95 | 80 | 67 | 51.5724 | 33100 | 33100 | 1.71 | 2400 | 208.3799 |  | 1
95 | 85 | 67 | 39.6049 | 33100 | 33100 | 1.71 | 2400 | 208.3799 |  | 1
95 | 75 | 71 | 82.6659 | 32800 | 5904 | 1.7 | 1600 | 208.3799 |  | 1
95 | 80 | 71 | 65.0618 | 32800 | 17712 | 1.7 | 1600 | 208.3799 |  | 1
95 | 85 | 71 | 51.076 | 32800 | 28536 | 1.7 | 1600 | 208.3799 |  | 1
95 | 75 | 71 | 82.6659 | 34000 | 6460 | 1.71 | 2000 | 208.3799 |  | 1
95 | 80 | 71 | 65.0618 | 34000 | 20740 | 1.71 | 2000 | 208.3799 |  | 1
95 | 85 | 71 | 51.076 | 34000 | 32980 | 1.71 | 2000 | 208.3799 |  | 1
95 | 75 | 71 | 82.6659 | 34900 | 7678 | 1.72 | 2400 | 208.3799 |  | 1
95 | 80 | 71 | 65.0618 | 34900 | 23732 | 1.72 | 2400 | 208.3799 |  | 1
95 | 85 | 71 | 51.076 | 34900 | 34900 | 1.72 | 2400 | 208.3799 |  | 1
65 | 75 | 63 | 52.1129 | 133700 | 96264 | 5.69 | 3600 | 479.2737 |  | 2
65 | 80 | 63 | 39.1676 | 133700 | 113645 | 5.69 | 3600 | 479.2737 |  | 2
65 | 85 | 63 | 29.0563 | 133700 | 128352 | 5.69 | 3600 | 479.2737 |  | 2
65 | 75 | 63 | 52.1129 | 140700 | 106932 | 5.71 | 4500 | 771.0056 |  | 2
65 | 80 | 63 | 39.1676 | 140700 | 126630 | 5.71 | 4500 | 771.0056 |  | 2
65 | 85 | 63 | 29.0563 | 140700 | 139293 | 5.71 | 4500 | 771.0056 |  | 2
65 | 75 | 63 | 52.1129 | 146500 | 117200 | 5.73 | 5400 | 1125.2514 |  | 2
65 | 80 | 63 | 39.1676 | 146500 | 139175 | 5.73 | 5400 | 1125.2514 |  | 2
65 | 85 | 63 | 29.0563 | 146500 | 146500 | 5.73 | 5400 | 1125.2514 |  | 2
65 | 75 | 67 | 66.7494 | 141400 | 82012 | 5.72 | 3600 | 531.3687 |  | 2
65 | 80 | 67 | 51.5724 | 141400 | 98980 | 5.72 | 3600 | 531.3687 |  | 2
65 | 85 | 67 | 39.6049 | 141400 | 115948 | 5.72 | 3600 | 531.3687 |  | 2
65 | 75 | 67 | 66.7494 | 149400 | 91134 | 5.74 | 4500 | 771.0056 |  | 2
65 | 80 | 67 | 51.5724 | 149400 | 110556 | 5.74 | 4500 | 771.0056 |  | 2
65 | 85 | 67 | 39.6049 | 149400 | 129978 | 5.74 | 4500 | 771.0056 |  | 2
65 | 75 | 67 | 66.7494 | 155100 | 97713 | 5.76 | 5400 | 1125.2514 |  | 2
65 | 80 | 67 | 51.5724 | 155100 | 120978 | 5.76 | 5400 | 1125.2514 |  | 2
65 | 85 | 67 | 39.6049 | 155100 | 144243 | 5.76 | 5400 | 1125.2514 |  | 2
65 | 75 | 71 | 82.6659 | 148700 | 66915 | 5.74 | 3600 | 531.3687 |  | 2
65 | 80 | 71 | 65.0618 | 148700 | 83272 | 5.74 | 3600 | 531.3687 |  | 2
65 | 85 | 71 | 51.076 | 148700 | 101116 | 5.74 | 3600 | 531.3687 |  | 2
65 | 75 | 71 | 82.6659 | 157000 | 72220 | 5.77 | 4500 | 771.0056 |  | 2
65 | 80 | 71 | 65.0618 | 157000 | 94200 | 5.77 | 4500 | 771.0056 |  | 2
65 | 85 | 71 | 51.076 | 157000 | 113040 | 5.77 | 4500 | 771.0056 |  | 2
65 | 75 | 71 | 82.6659 | 163300 | 76751 | 5.78 | 5400 | 1125.2514 |  | 2
65 | 80 | 71 | 65.0618 | 163300 | 101246 | 5.78 | 5400 | 1125.2514 |  | 2
65 | 85 | 71 | 51.076 | 163300 | 124108 | 5.78 | 5400 | 1125.2514 |  | 2
75 | 75 | 63 | 52.1129 | 127100 | 92783 | 6.4 | 3600 | 479.2737 |  | 2
75 | 80 | 63 | 39.1676 | 127100 | 109306 | 6.4 | 3600 | 479.2737 |  | 2
75 | 85 | 63 | 29.0563 | 127100 | 123287 | 6.4 | 3600 | 479.2737 |  | 2
75 | 75 | 63 | 52.1129 | 133600 | 102872 | 6.44 | 4500 | 708.4916 |  | 2
75 | 80 | 63 | 39.1676 | 133600 | 122912 | 6.44 | 4500 | 708.4916 |  | 2
75 | 85 | 63 | 29.0563 | 133600 | 133600 | 6.44 | 4500 | 708.4916 |  | 2
75 | 75 | 63 | 52.1129 | 139500 | 112995 | 6.46 | 5400 | 1125.2514 |  | 2
75 | 80 | 63 | 39.1676 | 139500 | 135315 | 6.46 | 5400 | 1125.2514 |  | 2
75 | 85 | 63 | 29.0563 | 139500 | 139500 | 6.46 | 5400 | 1125.2514 |  | 2
75 | 75 | 67 | 66.7494 | 134700 | 78126 | 6.44 | 3600 | 531.3687 |  | 2
75 | 80 | 67 | 51.5724 | 134700 | 95637 | 6.44 | 3600 | 531.3687 |  | 2
75 | 85 | 67 | 39.6049 | 134700 | 111801 | 6.44 | 3600 | 531.3687 |  | 2
75 | 75 | 67 | 66.7494 | 142200 | 86742 | 6.48 | 4500 | 771.0056 |  | 2
75 | 80 | 67 | 51.5724 | 142200 | 106650 | 6.48 | 4500 | 771.0056 |  | 2
75 | 85 | 67 | 39.6049 | 142200 | 126558 | 6.48 | 4500 | 771.0056 |  | 2
75 | 75 | 67 | 66.7494 | 147500 | 92925 | 6.5 | 5400 | 1125.2514 |  | 2
75 | 80 | 67 | 51.5724 | 147500 | 118000 | 6.5 | 5400 | 1125.2514 |  | 2
75 | 85 | 67 | 39.6049 | 147500 | 138650 | 6.5 | 5400 | 1125.2514 |  | 2
75 | 75 | 71 | 82.6659 | 141600 | 62304 | 6.47 | 3600 | 531.3687 |  | 2
75 | 80 | 71 | 65.0618 | 141600 | 80712 | 6.47 | 3600 | 531.3687 |  | 2
75 | 85 | 71 | 51.076 | 141600 | 97704 | 6.47 | 3600 | 531.3687 |  | 2
75 | 75 | 71 | 82.6659 | 149600 | 68816 | 6.51 | 4500 | 771.0056 |  | 2
75 | 80 | 71 | 65.0618 | 149600 | 89760 | 6.51 | 4500 | 771.0056 |  | 2
75 | 85 | 71 | 51.076 | 149600 | 109208 | 6.51 | 4500 | 771.0056 |  | 2
75 | 75 | 71 | 82.6659 | 155400 | 71484 | 6.53 | 5400 | 1125.2514 |  | 2
75 | 80 | 71 | 65.0618 | 155400 | 97902 | 6.53 | 5400 | 1125.2514 |  | 2
75 | 85 | 71 | 51.076 | 155400 | 121212 | 6.53 | 5400 | 1125.2514 |  | 2
85 | 75 | 63 | 52.1129 | 120200 | 87746 | 7.24 | 3600 | 479.2737 |  | 2
85 | 80 | 63 | 39.1676 | 120200 | 104574 | 7.24 | 3600 | 479.2737 |  | 2
85 | 85 | 63 | 29.0563 | 120200 | 117796 | 7.24 | 3600 | 479.2737 |  | 2
85 | 75 | 63 | 52.1129 | 126500 | 98670 | 7.28 | 4500 | 708.4916 |  | 2
85 | 80 | 63 | 39.1676 | 126500 | 118910 | 7.28 | 4500 | 708.4916 |  | 2
85 | 85 | 63 | 29.0563 | 126500 | 126500 | 7.28 | 4500 | 708.4916 |  | 2
85 | 75 | 63 | 52.1129 | 132100 | 109643 | 7.31 | 5400 | 1041.8994 |  | 2
85 | 80 | 63 | 39.1676 | 132100 | 129458 | 7.31 | 5400 | 1041.8994 |  | 2
85 | 85 | 63 | 29.0563 | 132100 | 132100 | 7.31 | 5400 | 1041.8994 |  | 2
85 | 75 | 67 | 66.7494 | 127600 | 74008 | 7.28 | 3600 | 479.2737 |  | 2
85 | 80 | 67 | 51.5724 | 127600 | 90596 | 7.28 | 3600 | 479.2737 |  | 2
85 | 85 | 67 | 39.6049 | 127600 | 107184 | 7.28 | 3600 | 479.2737 |  | 2
85 | 75 | 67 | 66.7494 | 134400 | 81984 | 7.32 | 4500 | 708.4916 |  | 2
85 | 80 | 67 | 51.5724 | 134400 | 102144 | 7.32 | 4500 | 708.4916 |  | 2
85 | 85 | 67 | 39.6049 | 134400 | 122304 | 7.32 | 4500 | 708.4916 |  | 2
85 | 75 | 67 | 66.7494 | 139400 | 89216 | 7.35 | 5400 | 1125.2514 |  | 2
85 | 80 | 67 | 51.5724 | 139400 | 112914 | 7.35 | 5400 | 1125.2514 |  | 2
85 | 85 | 67 | 39.6049 | 139400 | 133824 | 7.35 | 5400 | 1125.2514 |  | 2
85 | 75 | 71 | 82.6659 | 134200 | 59048 | 7.32 | 3600 | 479.2737 |  | 2
85 | 80 | 71 | 65.0618 | 134200 | 76494 | 7.32 | 3600 | 479.2737 |  | 2
85 | 85 | 71 | 51.076 | 134200 | 93940 | 7.32 | 3600 | 479.2737 |  | 2
85 | 75 | 71 | 82.6659 | 141800 | 63810 | 7.36 | 4500 | 771.0056 |  | 2
85 | 80 | 71 | 65.0618 | 141800 | 85080 | 7.36 | 4500 | 771.0056 |  | 2
85 | 85 | 71 | 51.076 | 141800 | 104932 | 7.36 | 4500 | 771.0056 |  | 2
85 | 75 | 71 | 82.6659 | 147100 | 67666 | 7.39 | 5400 | 1125.2514 |  | 2
85 | 80 | 71 | 65.0618 | 147100 | 92673 | 7.39 | 5400 | 1125.2514 |  | 2
85 | 85 | 71 | 51.076 | 147100 | 116209 | 7.39 | 5400 | 1125.2514 |  | 2
95 | 75 | 63 | 52.1129 | 112100 | 82954 | 8.16 | 3600 | 479.2737 |  | 2
95 | 80 | 63 | 39.1676 | 112100 | 99769 | 8.16 | 3600 | 479.2737 |  | 2
95 | 85 | 63 | 29.0563 | 112100 | 110979 | 8.16 | 3600 | 479.2737 |  | 2
95 | 75 | 63 | 52.1129 | 118900 | 93931 | 8.21 | 4500 | 708.4916 |  | 2
95 | 80 | 63 | 39.1676 | 118900 | 112955 | 8.21 | 4500 | 708.4916 |  | 2
95 | 85 | 63 | 29.0563 | 118900 | 118900 | 8.21 | 4500 | 708.4916 |  | 2
95 | 75 | 63 | 52.1129 | 124600 | 104664 | 8.25 | 5400 | 1041.8994 |  | 2
95 | 80 | 63 | 39.1676 | 124600 | 123354 | 8.25 | 5400 | 1041.8994 |  | 2
95 | 85 | 63 | 29.0563 | 124600 | 124600 | 8.25 | 5400 | 1041.8994 |  | 2
95 | 75 | 67 | 66.7494 | 120000 | 69600 | 8.22 | 3600 | 479.2737 |  | 2
95 | 80 | 67 | 51.5724 | 120000 | 86400 | 8.22 | 3600 | 479.2737 |  | 2
95 | 85 | 67 | 39.6049 | 120000 | 103200 | 8.22 | 3600 | 479.2737 |  | 2
95 | 75 | 67 | 66.7494 | 126300 | 78306 | 8.27 | 4500 | 708.4916 |  | 2
95 | 80 | 67 | 51.5724 | 126300 | 97251 | 8.27 | 4500 | 708.4916 |  | 2
95 | 85 | 67 | 39.6049 | 126300 | 117459 | 8.27 | 4500 | 708.4916 |  | 2
95 | 75 | 67 | 66.7494 | 130900 | 83776 | 8.3 | 5400 | 1041.8994 |  | 2
95 | 80 | 67 | 51.5724 | 130900 | 107338 | 8.3 | 5400 | 1041.8994 |  | 2
95 | 85 | 67 | 39.6049 | 130900 | 128282 | 8.3 | 5400 | 1041.8994 |  | 2
95 | 75 | 71 | 82.6659 | 126500 | 55660 | 8.27 | 3600 | 479.2737 |  | 2
95 | 80 | 71 | 65.0618 | 126500 | 72105 | 8.27 | 3600 | 479.2737 |  | 2
95 | 85 | 71 | 51.076 | 126500 | 89815 | 8.27 | 3600 | 479.2737 |  | 2
95 | 75 | 71 | 82.6659 | 133400 | 60030 | 8.31 | 4500 | 708.4916 |  | 2
95 | 80 | 71 | 65.0618 | 133400 | 81374 | 8.31 | 4500 | 708.4916 |  | 2
95 | 85 | 71 | 51.076 | 133400 | 100050 | 8.31 | 4500 | 708.4916 |  | 2
95 | 75 | 71 | 82.6659 | 138400 | 63664 | 8.34 | 5400 | 1125.2514 |  | 2
95 | 80 | 71 | 65.0618 | 138400 | 88576 | 8.34 | 5400 | 1125.2514 |  | 2
95 | 85 | 71 | 51.076 | 138400 | 112104 | 8.34 | 5400 | 1125.2514 |  | 2
85 | 75 | 63 | 52.1129 | 178200 | 126522 | 10.21 | 4800 | 843.9385 |  | 3
85 | 80 | 63 | 39.1676 | 178200 | 149688 | 10.21 | 4800 | 843.9385 |  | 3
85 | 85 | 63 | 29.0563 | 178200 | 169290 | 10.21 | 4800 | 843.9385 |  | 3
85 | 75 | 63 | 52.1129 | 188300 | 144991 | 10.26 | 6000 | 1364.8883 |  | 3
85 | 80 | 63 | 39.1676 | 188300 | 169470 | 10.26 | 6000 | 1364.8883 |  | 3
85 | 85 | 63 | 29.0563 | 188300 | 188300 | 10.26 | 6000 | 1364.8883 |  | 3
85 | 75 | 63 | 52.1129 | 195400 | 158274 | 10.31 | 7200 | 2042.1229 |  | 3
85 | 80 | 63 | 39.1676 | 195400 | 187584 | 10.31 | 7200 | 2042.1229 |  | 3
85 | 85 | 63 | 29.0563 | 195400 | 195400 | 10.31 | 7200 | 2042.1229 |  | 3
85 | 75 | 67 | 66.7494 | 187100 | 104776 | 10.27 | 4800 | 843.9385 |  | 3
85 | 80 | 67 | 51.5724 | 187100 | 129099 | 10.27 | 4800 | 843.9385 |  | 3
85 | 85 | 67 | 39.6049 | 187100 | 151551 | 10.27 | 4800 | 843.9385 |  | 3
85 | 75 | 67 | 66.7494 | 196300 | 117780 | 10.32 | 6000 | 1364.8883 |  | 3
85 | 80 | 67 | 51.5724 | 196300 | 149188 | 10.32 | 6000 | 1364.8883 |  | 3
85 | 85 | 67 | 39.6049 | 196300 | 170781 | 10.32 | 6000 | 1364.8883 |  | 3
85 | 75 | 67 | 66.7494 | 204100 | 128583 | 10.36 | 7200 | 2042.1229 |  | 3
85 | 80 | 67 | 51.5724 | 204100 | 161239 | 10.36 | 7200 | 2042.1229 |  | 3
85 | 85 | 67 | 39.6049 | 204100 | 189813 | 10.36 | 7200 | 2042.1229 |  | 3
85 | 75 | 71 | 82.6659 | 198800 | 83496 | 10.33 | 4800 | 843.9385 |  | 3
85 | 80 | 71 | 65.0618 | 198800 | 109340 | 10.33 | 4800 | 843.9385 |  | 3
85 | 85 | 71 | 51.076 | 198800 | 133196 | 10.33 | 4800 | 843.9385 |  | 3
85 | 75 | 71 | 82.6659 | 208400 | 89612 | 10.38 | 6000 | 1364.8883 |  | 3
85 | 80 | 71 | 65.0618 | 208400 | 122956 | 10.38 | 6000 | 1364.8883 |  | 3
85 | 85 | 71 | 51.076 | 208400 | 152132 | 10.38 | 6000 | 1364.8883 |  | 3
85 | 75 | 71 | 82.6659 | 215400 | 96930 | 10.42 | 7200 | 2167.1508 |  | 3
85 | 80 | 71 | 65.0618 | 215400 | 133548 | 10.42 | 7200 | 2167.1508 |  | 3
85 | 85 | 71 | 51.076 | 215400 | 168012 | 10.42 | 7200 | 2167.1508 |  | 3
95 | 75 | 63 | 52.1129 | 167400 | 120528 | 11.49 | 4800 | 843.9385 |  | 3
95 | 80 | 63 | 39.1676 | 167400 | 142290 | 11.49 | 4800 | 843.9385 |  | 3
95 | 85 | 63 | 29.0563 | 167400 | 162378 | 11.49 | 4800 | 843.9385 |  | 3
95 | 75 | 63 | 52.1129 | 176500 | 137670 | 11.55 | 6000 | 1364.8883 |  | 3
95 | 80 | 63 | 39.1676 | 176500 | 162380 | 11.55 | 6000 | 1364.8883 |  | 3
95 | 85 | 63 | 29.0563 | 176500 | 176500 | 11.55 | 6000 | 1364.8883 |  | 3
95 | 75 | 63 | 52.1129 | 183600 | 152388 | 11.6 | 7200 | 2042.1229 |  | 3
95 | 80 | 63 | 39.1676 | 183600 | 179928 | 11.6 | 7200 | 2042.1229 |  | 3
95 | 85 | 63 | 29.0563 | 183600 | 183600 | 11.6 | 7200 | 2042.1229 |  | 3
95 | 75 | 67 | 66.7494 | 175200 | 98112 | 11.55 | 4800 | 843.9385 |  | 3
95 | 80 | 67 | 51.5724 | 175200 | 124392 | 11.55 | 4800 | 843.9385 |  | 3
95 | 85 | 67 | 39.6049 | 175200 | 145416 | 11.55 | 4800 | 843.9385 |  | 3
95 | 75 | 67 | 66.7494 | 184400 | 112484 | 11.61 | 6000 | 1364.8883 |  | 3
95 | 80 | 67 | 51.5724 | 184400 | 140144 | 11.61 | 6000 | 1364.8883 |  | 3
95 | 85 | 67 | 39.6049 | 184400 | 164116 | 11.61 | 6000 | 1364.8883 |  | 3
95 | 75 | 67 | 66.7494 | 191600 | 122624 | 11.66 | 7200 | 2042.1229 |  | 3
95 | 80 | 67 | 51.5724 | 191600 | 153280 | 11.66 | 7200 | 2042.1229 |  | 3
95 | 85 | 67 | 39.6049 | 191600 | 182020 | 11.66 | 7200 | 2042.1229 |  | 3
95 | 75 | 71 | 82.6659 | 186700 | 76547 | 11.63 | 4800 | 843.9385 |  | 3
95 | 80 | 71 | 65.0618 | 186700 | 102685 | 11.63 | 4800 | 843.9385 |  | 3
95 | 85 | 71 | 51.076 | 186700 | 126956 | 11.63 | 4800 | 843.9385 |  | 3
95 | 75 | 71 | 82.6659 | 195500 | 84065 | 11.68 | 6000 | 1364.8883 |  | 3
95 | 80 | 71 | 65.0618 | 195500 | 115345 | 11.68 | 6000 | 1364.8883 |  | 3
95 | 85 | 71 | 51.076 | 195500 | 144670 | 11.68 | 6000 | 1364.8883 |  | 3
95 | 75 | 71 | 82.6659 | 202100 | 90945 | 11.72 | 7200 | 2042.1229 |  | 3
95 | 80 | 71 | 65.0618 | 202100 | 125302 | 11.72 | 7200 | 2042.1229 |  | 3
95 | 85 | 71 | 51.076 | 202100 | 159659 | 11.72 | 7200 | 2042.1229 |  | 3
105 | 75 | 63 | 52.1129 | 156100 | 115514 | 12.93 | 4800 | 843.9385 |  | 3
105 | 80 | 63 | 39.1676 | 156100 | 135807 | 12.93 | 4800 | 843.9385 |  | 3
105 | 85 | 63 | 29.0563 | 156100 | 154539 | 12.93 | 4800 | 843.9385 |  | 3
105 | 75 | 63 | 52.1129 | 164200 | 131360 | 12.99 | 6000 | 1364.8883 |  | 3
105 | 80 | 63 | 39.1676 | 164200 | 155990 | 12.99 | 6000 | 1364.8883 |  | 3
105 | 85 | 63 | 29.0563 | 164200 | 164200 | 12.99 | 6000 | 1364.8883 |  | 3
105 | 75 | 63 | 52.1129 | 171500 | 145775 | 13.05 | 7200 | 2042.1229 |  | 3
105 | 80 | 63 | 39.1676 | 171500 | 169785 | 13.05 | 7200 | 2042.1229 |  | 3
105 | 85 | 63 | 29.0563 | 171500 | 171500 | 13.05 | 7200 | 2042.1229 |  | 3
105 | 75 | 67 | 66.7494 | 163200 | 91392 | 12.98 | 4800 | 843.9385 |  | 3
105 | 80 | 67 | 51.5724 | 163200 | 117504 | 12.98 | 4800 | 843.9385 |  | 3
105 | 85 | 67 | 39.6049 | 163200 | 137088 | 12.98 | 4800 | 843.9385 |  | 3
105 | 75 | 67 | 66.7494 | 172100 | 104981 | 13.05 | 6000 | 1364.8883 |  | 3
105 | 80 | 67 | 51.5724 | 172100 | 132517 | 13.05 | 6000 | 1364.8883 |  | 3
105 | 85 | 67 | 39.6049 | 172100 | 158332 | 13.05 | 6000 | 1364.8883 |  | 3
105 | 75 | 67 | 66.7494 | 178600 | 114304 | 13.1 | 7200 | 2042.1229 |  | 3
105 | 80 | 67 | 51.5724 | 178600 | 146452 | 13.1 | 7200 | 2042.1229 |  | 3
105 | 85 | 67 | 39.6049 | 178600 | 175028 | 13.1 | 7200 | 2042.1229 |  | 3
105 | 75 | 71 | 82.6659 | 173800 | 69520 | 13.06 | 4800 | 843.9385 |  | 3
105 | 80 | 71 | 65.0618 | 173800 | 97328 | 13.06 | 4800 | 843.9385 |  | 3
105 | 85 | 71 | 51.076 | 173800 | 119922 | 13.06 | 4800 | 843.9385 |  | 3
105 | 75 | 71 | 82.6659 | 182100 | 76482 | 13.12 | 6000 | 1364.8883 |  | 3
105 | 80 | 71 | 65.0618 | 182100 | 109260 | 13.12 | 6000 | 1364.8883 |  | 3
105 | 85 | 71 | 51.076 | 182100 | 138396 | 13.12 | 6000 | 1364.8883 |  | 3
105 | 75 | 71 | 82.6659 | 187900 | 82676 | 13.17 | 7200 | 2042.1229 |  | 3
105 | 80 | 71 | 65.0618 | 187900 | 120256 | 13.17 | 7200 | 2042.1229 |  | 3
105 | 85 | 71 | 51.076 | 187900 | 152199 | 13.17 | 7200 | 2042.1229 |  | 3
115 | 75 | 63 | 52.1129 | 143800 | 107850 | 14.51 | 4800 | 843.9385 |  | 3
115 | 80 | 63 | 39.1676 | 143800 | 129420 | 14.51 | 4800 | 843.9385 |  | 3
115 | 85 | 63 | 29.0563 | 143800 | 143800 | 14.51 | 4800 | 843.9385 |  | 3
115 | 75 | 63 | 52.1129 | 151600 | 122796 | 14.58 | 6000 | 1364.8883 |  | 3
115 | 80 | 63 | 39.1676 | 151600 | 147052 | 14.58 | 6000 | 1364.8883 |  | 3
115 | 85 | 63 | 29.0563 | 151600 | 151600 | 14.58 | 6000 | 1364.8883 |  | 3
115 | 75 | 63 | 52.1129 | 159200 | 138504 | 14.64 | 7200 | 2042.1229 |  | 3
115 | 80 | 63 | 39.1676 | 159200 | 159200 | 14.64 | 7200 | 2042.1229 |  | 3
115 | 85 | 63 | 29.0563 | 159200 | 159200 | 14.64 | 7200 | 2042.1229 |  | 3
115 | 75 | 67 | 66.7494 | 150800 | 84448 | 14.57 | 4800 | 843.9385 |  | 3
115 | 80 | 67 | 51.5724 | 150800 | 110084 | 14.57 | 4800 | 843.9385 |  | 3
115 | 85 | 67 | 39.6049 | 150800 | 131196 | 14.57 | 4800 | 843.9385 |  | 3
115 | 75 | 67 | 66.7494 | 159000 | 98580 | 14.64 | 6000 | 1364.8883 |  | 3
115 | 80 | 67 | 51.5724 | 159000 | 125610 | 14.64 | 6000 | 1364.8883 |  | 3
115 | 85 | 67 | 39.6049 | 159000 | 149460 | 14.64 | 6000 | 1364.8883 |  | 3
115 | 75 | 67 | 66.7494 | 164700 | 110349 | 14.69 | 7200 | 2042.1229 |  | 3
115 | 80 | 67 | 51.5724 | 164700 | 139995 | 14.69 | 7200 | 2042.1229 |  | 3
115 | 85 | 67 | 39.6049 | 164700 | 163053 | 14.69 | 7200 | 2042.1229 |  | 3
115 | 75 | 71 | 82.6659 | 160700 | 64280 | 14.66 | 4800 | 843.9385 |  | 3
115 | 80 | 71 | 65.0618 | 160700 | 89992 | 14.66 | 4800 | 843.9385 |  | 3
115 | 85 | 71 | 51.076 | 160700 | 114097 | 14.66 | 4800 | 843.9385 |  | 3
115 | 75 | 71 | 82.6659 | 168200 | 70644 | 14.73 | 6000 | 1364.8883 |  | 3
115 | 80 | 71 | 65.0618 | 168200 | 100920 | 14.73 | 6000 | 1364.8883 |  | 3
115 | 85 | 71 | 51.076 | 168200 | 131196 | 14.73 | 6000 | 1364.8883 |  | 3
115 | 75 | 71 | 82.6659 | 173100 | 79626 | 14.77 | 7200 | 2042.1229 |  | 3
115 | 80 | 71 | 65.0618 | 173100 | 114246 | 14.77 | 7200 | 2042.1229 |  | 3
115 | 85 | 71 | 51.076 | 173100 | 143673 | 14.77 | 7200 | 2042.1229 |  | 3
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 4
Degradation Coefficient (C_d)
IEER or SEER | 18
Standby Power (W)
Crankcase Heater Power (W)
Net
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 75 | 63 | 52.1129 | 46100 | 37341 | 1.13 | 1600 | 250.0559 |  | 1
65 | 80 | 63 | 39.1676 | 46100 | 44256 | 1.13 | 1600 | 250.0559 |  | 1
65 | 85 | 63 | 29.0563 | 46100 | 46100 | 1.13 | 1600 | 250.0559 |  | 1
65 | 75 | 63 | 52.1129 | 48100 | 41847 | 1.13 | 2000 | 250.0559 |  | 1
65 | 80 | 63 | 39.1676 | 48100 | 47138 | 1.13 | 2000 | 250.0559 |  | 1
65 | 85 | 63 | 29.0563 | 48100 | 48100 | 1.13 | 2000 | 250.0559 |  | 1
65 | 75 | 63 | 52.1129 | 49900 | 45409 | 1.14 | 2400 | 250.0559 |  | 1
65 | 80 | 63 | 39.1676 | 49900 | 49900 | 1.14 | 2400 | 250.0559 |  | 1
65 | 85 | 63 | 29.0563 | 49900 | 49900 | 1.14 | 2400 | 250.0559 |  | 1
65 | 75 | 67 | 66.7494 | 48300 | 25116 | 1.13 | 1600 | 250.0559 |  | 1
65 | 80 | 67 | 51.5724 | 48300 | 36708 | 1.13 | 1600 | 250.0559 |  | 1
65 | 85 | 67 | 39.6049 | 48300 | 45402 | 1.13 | 1600 | 250.0559 |  | 1
65 | 75 | 67 | 66.7494 | 50200 | 27610 | 1.14 | 2000 | 250.0559 |  | 1
65 | 80 | 67 | 51.5724 | 50200 | 41666 | 1.14 | 2000 | 250.0559 |  | 1
65 | 85 | 67 | 39.6049 | 50200 | 48694 | 1.14 | 2000 | 250.0559 |  | 1
65 | 75 | 67 | 66.7494 | 51500 | 30385 | 1.14 | 2400 | 250.0559 |  | 1
65 | 80 | 67 | 51.5724 | 51500 | 45835 | 1.14 | 2400 | 250.0559 |  | 1
65 | 85 | 67 | 39.6049 | 51500 | 50985 | 1.14 | 2400 | 250.0559 |  | 1
65 | 75 | 71 | 82.6659 | 50600 | 11132 | 1.14 | 1600 | 250.0559 |  | 1
65 | 80 | 71 | 65.0618 | 50600 | 24288 | 1.14 | 1600 | 250.0559 |  | 1
65 | 85 | 71 | 51.076 | 50600 | 36432 | 1.14 | 1600 | 250.0559 |  | 1
65 | 75 | 71 | 82.6659 | 52400 | 12052 | 1.14 | 2000 | 250.0559 |  | 1
65 | 80 | 71 | 65.0618 | 52400 | 27248 | 1.14 | 2000 | 250.0559 |  | 1
65 | 85 | 71 | 51.076 | 52400 | 41396 | 1.14 | 2000 | 250.0559 |  | 1
65 | 75 | 71 | 82.6659 | 53700 | 12351 | 1.15 | 2400 | 250.0559 |  | 1
65 | 80 | 71 | 65.0618 | 53700 | 30072 | 1.15 | 2400 | 250.0559 |  | 1
65 | 85 | 71 | 51.076 | 53700 | 46182 | 1.15 | 2400 | 250.0559 |  | 1
75 | 75 | 63 | 52.1129 | 43800 | 35916 | 1.27 | 1600 | 250.0559 |  | 1
75 | 80 | 63 | 39.1676 | 43800 | 42048 | 1.27 | 1600 | 250.0559 |  | 1
75 | 85 | 63 | 29.0563 | 43800 | 43800 | 1.27 | 1600 | 250.0559 |  | 1
75 | 75 | 63 | 52.1129 | 45800 | 40762 | 1.27 | 2000 | 250.0559 |  | 1
75 | 80 | 63 | 39.1676 | 45800 | 45342 | 1.27 | 2000 | 250.0559 |  | 1
75 | 85 | 63 | 29.0563 | 45800 | 45800 | 1.27 | 2000 | 250.0559 |  | 1
75 | 75 | 63 | 52.1129 | 47600 | 43792 | 1.28 | 2400 | 250.0559 |  | 1
75 | 80 | 63 | 39.1676 | 47600 | 47600 | 1.28 | 2400 | 250.0559 |  | 1
75 | 85 | 63 | 29.0563 | 47600 | 47600 | 1.28 | 2400 | 250.0559 |  | 1
75 | 75 | 67 | 66.7494 | 45900 | 23409 | 1.27 | 1600 | 250.0559 |  | 1
75 | 80 | 67 | 51.5724 | 45900 | 35802 | 1.27 | 1600 | 250.0559 |  | 1
75 | 85 | 67 | 39.6049 | 45900 | 43605 | 1.27 | 1600 | 250.0559 |  | 1
75 | 75 | 67 | 66.7494 | 47600 | 26180 | 1.28 | 2000 | 250.0559 |  | 1
75 | 80 | 67 | 51.5724 | 47600 | 40460 | 1.28 | 2000 | 250.0559 |  | 1
75 | 85 | 67 | 39.6049 | 47600 | 46648 | 1.28 | 2000 | 250.0559 |  | 1
75 | 75 | 67 | 66.7494 | 48900 | 28851 | 1.28 | 2400 | 250.0559 |  | 1
75 | 80 | 67 | 51.5724 | 48900 | 44499 | 1.28 | 2400 | 250.0559 |  | 1
75 | 85 | 67 | 39.6049 | 48900 | 48900 | 1.28 | 2400 | 250.0559 |  | 1
75 | 75 | 71 | 82.6659 | 48100 | 10101 | 1.28 | 1600 | 250.0559 |  | 1
75 | 80 | 71 | 65.0618 | 48100 | 23088 | 1.28 | 1600 | 250.0559 |  | 1
75 | 85 | 71 | 51.076 | 48100 | 35113 | 1.28 | 1600 | 250.0559 |  | 1
75 | 75 | 71 | 82.6659 | 49900 | 10978 | 1.28 | 2000 | 250.0559 |  | 1
75 | 80 | 71 | 65.0618 | 49900 | 25948 | 1.28 | 2000 | 250.0559 |  | 1
75 | 85 | 71 | 51.076 | 49900 | 40419 | 1.28 | 2000 | 250.0559 |  | 1
75 | 75 | 71 | 82.6659 | 51100 | 11242 | 1.28 | 2400 | 250.0559 |  | 1
75 | 80 | 71 | 65.0618 | 51100 | 29127 | 1.28 | 2400 | 250.0559 |  | 1
75 | 85 | 71 | 51.076 | 51100 | 44968 | 1.28 | 2400 | 250.0559 |  | 1
85 | 75 | 63 | 52.1129 | 41400 | 34362 | 1.45 | 1600 | 208.3799 |  | 1
85 | 80 | 63 | 39.1676 | 41400 | 40158 | 1.45 | 1600 | 208.3799 |  | 1
85 | 85 | 63 | 29.0563 | 41400 | 41400 | 1.45 | 1600 | 208.3799 |  | 1
85 | 75 | 63 | 52.1129 | 43400 | 39060 | 1.45 | 2000 | 250.0559 |  | 1
85 | 80 | 63 | 39.1676 | 43400 | 43400 | 1.45 | 2000 | 250.0559 |  | 1
85 | 85 | 63 | 29.0563 | 43400 | 43400 | 1.45 | 2000 | 250.0559 |  | 1
85 | 75 | 63 | 52.1129 | 45100 | 41943 | 1.45 | 2400 | 250.0559 |  | 1
85 | 80 | 63 | 39.1676 | 45100 | 45100 | 1.45 | 2400 | 250.0559 |  | 1
85 | 85 | 63 | 29.0563 | 45100 | 45100 | 1.45 | 2400 | 250.0559 |  | 1
85 | 75 | 67 | 66.7494 | 43400 | 22134 | 1.45 | 1600 | 250.0559 |  | 1
85 | 80 | 67 | 51.5724 | 43400 | 34286 | 1.45 | 1600 | 250.0559 |  | 1
85 | 85 | 67 | 39.6049 | 43400 | 41230 | 1.45 | 1600 | 250.0559 |  | 1
85 | 75 | 67 | 66.7494 | 45000 | 25200 | 1.45 | 2000 | 250.0559 |  | 1
85 | 80 | 67 | 51.5724 | 45000 | 39150 | 1.45 | 2000 | 250.0559 |  | 1
85 | 85 | 67 | 39.6049 | 45000 | 44550 | 1.45 | 2000 | 250.0559 |  | 1
85 | 75 | 67 | 66.7494 | 46200 | 28182 | 1.45 | 2400 | 250.0559 |  | 1
85 | 80 | 67 | 51.5724 | 46200 | 42504 | 1.45 | 2400 | 250.0559 |  | 1
85 | 85 | 67 | 39.6049 | 46200 | 46200 | 1.45 | 2400 | 250.0559 |  | 1
85 | 75 | 71 | 82.6659 | 45600 | 9120 | 1.45 | 1600 | 250.0559 |  | 1
85 | 80 | 71 | 65.0618 | 45600 | 21888 | 1.45 | 1600 | 250.0559 |  | 1
85 | 85 | 71 | 51.076 | 45600 | 33744 | 1.45 | 1600 | 250.0559 |  | 1
85 | 75 | 71 | 82.6659 | 47200 | 9440 | 1.45 | 2000 | 250.0559 |  | 1
85 | 80 | 71 | 65.0618 | 47200 | 25016 | 1.45 | 2000 | 250.0559 |  | 1
85 | 85 | 71 | 51.076 | 47200 | 38704 | 1.45 | 2000 | 250.0559 |  | 1
85 | 75 | 71 | 82.6659 | 48300 | 10626 | 1.45 | 2400 | 250.0559 |  | 1
85 | 80 | 71 | 65.0618 | 48300 | 28014 | 1.45 | 2400 | 250.0559 |  | 1
85 | 85 | 71 | 51.076 | 48300 | 43470 | 1.45 | 2400 | 250.0559 |  | 1
95 | 75 | 63 | 52.1129 | 38900 | 33065 | 1.66 | 1600 | 208.3799 |  | 1
95 | 80 | 63 | 39.1676 | 38900 | 38122 | 1.66 | 1600 | 208.3799 |  | 1
95 | 85 | 63 | 29.0563 | 38900 | 38900 | 1.66 | 1600 | 208.3799 |  | 1
95 | 75 | 63 | 52.1129 | 41000 | 37310 | 1.66 | 2000 | 208.3799 |  | 1
95 | 80 | 63 | 39.1676 | 41000 | 41000 | 1.66 | 2000 | 208.3799 |  | 1
95 | 85 | 63 | 29.0563 | 41000 | 41000 | 1.66 | 2000 | 208.3799 |  | 1
95 | 75 | 63 | 52.1129 | 42700 | 40138 | 1.65 | 2400 | 250.0559 |  | 1
95 | 80 | 63 | 39.1676 | 42700 | 42700 | 1.65 | 2400 | 250.0559 |  | 1
95 | 85 | 63 | 29.0563 | 42700 | 42700 | 1.65 | 2400 | 250.0559 |  | 1
95 | 75 | 67 | 66.7494 | 40800 | 20808 | 1.66 | 1600 | 208.3799 |  | 1
95 | 80 | 67 | 51.5724 | 40800 | 33048 | 1.66 | 1600 | 208.3799 |  | 1
95 | 85 | 67 | 39.6049 | 40800 | 39576 | 1.66 | 1600 | 208.3799 |  | 1
95 | 75 | 67 | 66.7494 | 42400 | 24168 | 1.66 | 2000 | 208.3799 |  | 1
95 | 80 | 67 | 51.5724 | 42400 | 38160 | 1.66 | 2000 | 208.3799 |  | 1
95 | 85 | 67 | 39.6049 | 42400 | 41976 | 1.66 | 2000 | 208.3799 |  | 1
95 | 75 | 67 | 66.7494 | 43400 | 26908 | 1.65 | 2400 | 250.0559 |  | 1
95 | 80 | 67 | 51.5724 | 43400 | 40362 | 1.65 | 2400 | 250.0559 |  | 1
95 | 85 | 67 | 39.6049 | 43400 | 43400 | 1.65 | 2400 | 250.0559 |  | 1
95 | 75 | 71 | 82.6659 | 43000 | 8170 | 1.66 | 1600 | 250.0559 |  | 1
95 | 80 | 71 | 65.0618 | 43000 | 20640 | 1.66 | 1600 | 250.0559 |  | 1
95 | 85 | 71 | 51.076 | 43000 | 32680 | 1.66 | 1600 | 250.0559 |  | 1
95 | 75 | 71 | 82.6659 | 44500 | 8900 | 1.65 | 2000 | 250.0559 |  | 1
95 | 80 | 71 | 65.0618 | 44500 | 24030 | 1.65 | 2000 | 250.0559 |  | 1
95 | 85 | 71 | 51.076 | 44500 | 37825 | 1.65 | 2000 | 250.0559 |  | 1
95 | 75 | 71 | 82.6659 | 45600 | 9576 | 1.65 | 2400 | 250.0559 |  | 1
95 | 80 | 71 | 65.0618 | 45600 | 27360 | 1.65 | 2400 | 250.0559 |  | 1
95 | 85 | 71 | 51.076 | 45600 | 41496 | 1.65 | 2400 | 250.0559 |  | 1
65 | 75 | 63 | 52.1129 | 96900 | 70737 | 3.27 | 2800 | 291.7318 |  | 2
65 | 80 | 63 | 39.1676 | 96900 | 83334 | 3.27 | 2800 | 291.7318 |  | 2
65 | 85 | 63 | 29.0563 | 96900 | 94962 | 3.27 | 2800 | 291.7318 |  | 2
65 | 75 | 63 | 52.1129 | 102400 | 78848 | 3.27 | 3500 | 427.1788 |  | 2
65 | 80 | 63 | 39.1676 | 102400 | 95232 | 3.27 | 3500 | 427.1788 |  | 2
65 | 85 | 63 | 29.0563 | 102400 | 102400 | 3.27 | 3500 | 427.1788 |  | 2
65 | 75 | 63 | 52.1129 | 107300 | 87986 | 3.25 | 4200 | 625.1397 |  | 2
65 | 80 | 63 | 39.1676 | 107300 | 104081 | 3.25 | 4200 | 625.1397 |  | 2
65 | 85 | 63 | 29.0563 | 107300 | 107300 | 3.25 | 4200 | 625.1397 |  | 2
65 | 75 | 67 | 66.7494 | 102500 | 57400 | 3.27 | 2800 | 291.7318 |  | 2
65 | 80 | 67 | 51.5724 | 102500 | 72775 | 3.27 | 2800 | 291.7318 |  | 2
65 | 85 | 67 | 39.6049 | 102500 | 85075 | 3.27 | 2800 | 291.7318 |  | 2
65 | 75 | 67 | 66.7494 | 108100 | 63779 | 3.27 | 3500 | 479.2737 |  | 2
65 | 80 | 67 | 51.5724 | 108100 | 81075 | 3.27 | 3500 | 479.2737 |  | 2
65 | 85 | 67 | 39.6049 | 108100 | 96209 | 3.27 | 3500 | 479.2737 |  | 2
65 | 75 | 67 | 66.7494 | 111800 | 69316 | 3.28 | 4200 | 625.1397 |  | 2
65 | 80 | 67 | 51.5724 | 111800 | 89440 | 3.28 | 4200 | 625.1397 |  | 2
65 | 85 | 67 | 39.6049 | 111800 | 106210 | 3.28 | 4200 | 625.1397 |  | 2
65 | 75 | 71 | 82.6659 | 108000 | 47520 | 3.24 | 2800 | 333.4078 |  | 2
65 | 80 | 71 | 65.0618 | 108000 | 60480 | 3.24 | 2800 | 333.4078 |  | 2
65 | 85 | 71 | 51.076 | 108000 | 74520 | 3.24 | 2800 | 333.4078 |  | 2
65 | 75 | 71 | 82.6659 | 113900 | 47838 | 3.25 | 3500 | 479.2737 |  | 2
65 | 80 | 71 | 65.0618 | 113900 | 66062 | 3.25 | 3500 | 479.2737 |  | 2
65 | 85 | 71 | 51.076 | 113900 | 83147 | 3.25 | 3500 | 479.2737 |  | 2
65 | 75 | 71 | 82.6659 | 118300 | 52052 | 3.26 | 4200 | 625.1397 |  | 2
65 | 80 | 71 | 65.0618 | 118300 | 73346 | 3.26 | 4200 | 625.1397 |  | 2
65 | 85 | 71 | 51.076 | 118300 | 92274 | 3.26 | 4200 | 625.1397 |  | 2
75 | 75 | 63 | 52.1129 | 92100 | 67233 | 3.73 | 2800 | 291.7318 |  | 2
75 | 80 | 63 | 39.1676 | 92100 | 81048 | 3.73 | 2800 | 291.7318 |  | 2
75 | 85 | 63 | 29.0563 | 92100 | 91179 | 3.73 | 2800 | 291.7318 |  | 2
75 | 75 | 63 | 52.1129 | 97200 | 75816 | 3.74 | 3500 | 427.1788 |  | 2
75 | 80 | 63 | 39.1676 | 97200 | 91368 | 3.74 | 3500 | 427.1788 |  | 2
75 | 85 | 63 | 29.0563 | 97200 | 97200 | 3.74 | 3500 | 427.1788 |  | 2
75 | 75 | 63 | 52.1129 | 101900 | 84577 | 3.74 | 4200 | 562.6257 |  | 2
75 | 80 | 63 | 39.1676 | 101900 | 100881 | 3.74 | 4200 | 562.6257 |  | 2
75 | 85 | 63 | 29.0563 | 101900 | 101900 | 3.74 | 4200 | 562.6257 |  | 2
75 | 75 | 67 | 66.7494 | 97400 | 54544 | 3.74 | 2800 | 291.7318 |  | 2
75 | 80 | 67 | 51.5724 | 97400 | 70128 | 3.74 | 2800 | 291.7318 |  | 2
75 | 85 | 67 | 39.6049 | 97400 | 82790 | 3.74 | 2800 | 291.7318 |  | 2
75 | 75 | 67 | 66.7494 | 102400 | 61440 | 3.75 | 3500 | 427.1788 |  | 2
75 | 80 | 67 | 51.5724 | 102400 | 77824 | 3.75 | 3500 | 427.1788 |  | 2
75 | 85 | 67 | 39.6049 | 102400 | 93184 | 3.75 | 3500 | 427.1788 |  | 2
75 | 75 | 67 | 66.7494 | 106000 | 66780 | 3.76 | 4200 | 625.1397 |  | 2
75 | 80 | 67 | 51.5724 | 106000 | 85860 | 3.76 | 4200 | 625.1397 |  | 2
75 | 85 | 67 | 39.6049 | 106000 | 102820 | 3.76 | 4200 | 625.1397 |  | 2
75 | 75 | 71 | 82.6659 | 102400 | 43008 | 3.75 | 2800 | 291.7318 |  | 2
75 | 80 | 71 | 65.0618 | 102400 | 58368 | 3.75 | 2800 | 291.7318 |  | 2
75 | 85 | 71 | 51.076 | 102400 | 69632 | 3.75 | 2800 | 291.7318 |  | 2
75 | 75 | 71 | 82.6659 | 108000 | 45360 | 3.76 | 3500 | 479.2737 |  | 2
75 | 80 | 71 | 65.0618 | 108000 | 63720 | 3.76 | 3500 | 479.2737 |  | 2
75 | 85 | 71 | 51.076 | 108000 | 79920 | 3.76 | 3500 | 479.2737 |  | 2
75 | 75 | 71 | 82.6659 | 112100 | 49324 | 3.76 | 4200 | 625.1397 |  | 2
75 | 80 | 71 | 65.0618 | 112100 | 69502 | 3.76 | 4200 | 625.1397 |  | 2
75 | 85 | 71 | 51.076 | 112100 | 88559 | 3.76 | 4200 | 625.1397 |  | 2
85 | 75 | 63 | 52.1129 | 87100 | 64454 | 4.26 | 2800 | 291.7318 |  | 2
85 | 80 | 63 | 39.1676 | 87100 | 77519 | 4.26 | 2800 | 291.7318 |  | 2
85 | 85 | 63 | 29.0563 | 87100 | 87100 | 4.26 | 2800 | 291.7318 |  | 2
85 | 75 | 63 | 52.1129 | 92100 | 72759 | 4.27 | 3500 | 427.1788 |  | 2
85 | 80 | 63 | 39.1676 | 92100 | 88416 | 4.27 | 3500 | 427.1788 |  | 2
85 | 85 | 63 | 29.0563 | 92100 | 92100 | 4.27 | 3500 | 427.1788 |  | 2
85 | 75 | 63 | 52.1129 | 96600 | 82110 | 4.28 | 4200 | 562.6257 |  | 2
85 | 80 | 63 | 39.1676 | 96600 | 95634 | 4.28 | 4200 | 562.6257 |  | 2
85 | 85 | 63 | 29.0563 | 96600 | 96600 | 4.28 | 4200 | 562.6257 |  | 2
85 | 75 | 67 | 66.7494 | 92600 | 53708 | 4.23 | 2800 | 291.7318 |  | 2
85 | 80 | 67 | 51.5724 | 92600 | 66672 | 4.23 | 2800 | 291.7318 |  | 2
85 | 85 | 67 | 39.6049 | 92600 | 79636 | 4.23 | 2800 | 291.7318 |  | 2
85 | 75 | 67 | 66.7494 | 97300 | 58380 | 4.24 | 3500 | 427.1788 |  | 2
85 | 80 | 67 | 51.5724 | 97300 | 75894 | 4.24 | 3500 | 427.1788 |  | 2
85 | 85 | 67 | 39.6049 | 97300 | 90489 | 4.24 | 3500 | 427.1788 |  | 2
85 | 75 | 67 | 66.7494 | 100800 | 64512 | 4.25 | 4200 | 562.6257 |  | 2
85 | 80 | 67 | 51.5724 | 100800 | 82656 | 4.25 | 4200 | 562.6257 |  | 2
85 | 85 | 67 | 39.6049 | 100800 | 98784 | 4.25 | 4200 | 562.6257 |  | 2
85 | 75 | 71 | 82.6659 | 97600 | 40016 | 4.24 | 2800 | 291.7318 |  | 2
85 | 80 | 71 | 65.0618 | 97600 | 53680 | 4.24 | 2800 | 291.7318 |  | 2
85 | 85 | 71 | 51.076 | 97600 | 68320 | 4.24 | 2800 | 291.7318 |  | 2
85 | 75 | 71 | 82.6659 | 102700 | 43134 | 4.25 | 3500 | 427.1788 |  | 2
85 | 80 | 71 | 65.0618 | 102700 | 61620 | 4.25 | 3500 | 427.1788 |  | 2
85 | 85 | 71 | 51.076 | 102700 | 77025 | 4.25 | 3500 | 427.1788 |  | 2
85 | 75 | 71 | 82.6659 | 106500 | 46860 | 4.26 | 4200 | 625.1397 |  | 2
85 | 80 | 71 | 65.0618 | 106500 | 67095 | 4.26 | 4200 | 625.1397 |  | 2
85 | 85 | 71 | 51.076 | 106500 | 85200 | 4.26 | 4200 | 625.1397 |  | 2
95 | 75 | 63 | 52.1129 | 82200 | 61650 | 4.85 | 2800 | 291.7318 |  | 2
95 | 80 | 63 | 39.1676 | 82200 | 74802 | 4.85 | 2800 | 291.7318 |  | 2
95 | 85 | 63 | 29.0563 | 82200 | 82200 | 4.85 | 2800 | 291.7318 |  | 2
95 | 75 | 63 | 52.1129 | 87100 | 70551 | 4.86 | 3500 | 427.1788 |  | 2
95 | 80 | 63 | 39.1676 | 87100 | 85358 | 4.86 | 3500 | 427.1788 |  | 2
95 | 85 | 63 | 29.0563 | 87100 | 87100 | 4.86 | 3500 | 427.1788 |  | 2
95 | 75 | 63 | 52.1129 | 91300 | 78518 | 4.88 | 4200 | 562.6257 |  | 2
95 | 80 | 63 | 39.1676 | 91300 | 91300 | 4.88 | 4200 | 562.6257 |  | 2
95 | 85 | 63 | 29.0563 | 91300 | 91300 | 4.88 | 4200 | 562.6257 |  | 2
95 | 75 | 67 | 66.7494 | 86900 | 49533 | 4.87 | 2800 | 291.7318 |  | 2
95 | 80 | 67 | 51.5724 | 86900 | 63437 | 4.87 | 2800 | 291.7318 |  | 2
95 | 85 | 67 | 39.6049 | 86900 | 76472 | 4.87 | 2800 | 291.7318 |  | 2
95 | 75 | 67 | 66.7494 | 91100 | 55571 | 4.88 | 3500 | 427.1788 |  | 2
95 | 80 | 67 | 51.5724 | 91100 | 71969 | 4.88 | 3500 | 427.1788 |  | 2
95 | 85 | 67 | 39.6049 | 91100 | 86545 | 4.88 | 3500 | 427.1788 |  | 2
95 | 75 | 67 | 66.7494 | 94500 | 61425 | 4.88 | 4200 | 562.6257 |  | 2
95 | 80 | 67 | 51.5724 | 94500 | 79380 | 4.88 | 4200 | 562.6257 |  | 2
95 | 85 | 67 | 39.6049 | 94500 | 93555 | 4.88 | 4200 | 562.6257 |  | 2
95 | 75 | 71 | 82.6659 | 91900 | 36760 | 4.86 | 2800 | 291.7318 |  | 2
95 | 80 | 71 | 65.0618 | 91900 | 51464 | 4.86 | 2800 | 291.7318 |  | 2
95 | 85 | 71 | 51.076 | 91900 | 64330 | 4.86 | 2800 | 291.7318 |  | 2
95 | 75 | 71 | 82.6659 | 97000 | 40740 | 4.87 | 3500 | 427.1788 |  | 2
95 | 80 | 71 | 65.0618 | 97000 | 58200 | 4.87 | 3500 | 427.1788 |  | 2
95 | 85 | 71 | 51.076 | 97000 | 74690 | 4.87 | 3500 | 427.1788 |  | 2
95 | 75 | 71 | 82.6659 | 99900 | 43956 | 4.88 | 4200 | 562.6257 |  | 2
95 | 80 | 71 | 65.0618 | 99900 | 63936 | 4.88 | 4200 | 562.6257 |  | 2
95 | 85 | 71 | 51.076 | 99900 | 81918 | 4.88 | 4200 | 562.6257 |  | 2
65 | 75 | 63 | 52.1129 | 164000 | 116440 | 6.17 | 4200 | 687.6536 |  | 3
65 | 80 | 63 | 39.1676 | 164000 | 136120 | 6.17 | 4200 | 687.6536 |  | 3
65 | 85 | 63 | 29.0563 | 164000 | 154160 | 6.17 | 4200 | 687.6536 |  | 3
65 | 75 | 63 | 52.1129 | 172600 | 127724 | 6.21 | 5250 | 1041.8994 |  | 3
65 | 80 | 63 | 39.1676 | 172600 | 153614 | 6.21 | 5250 | 1041.8994 |  | 3
65 | 85 | 63 | 29.0563 | 172600 | 172600 | 6.21 | 5250 | 1041.8994 |  | 3
65 | 75 | 63 | 52.1129 | 179500 | 143600 | 6.23 | 6300 | 1479.4972 |  | 3
65 | 80 | 63 | 39.1676 | 179500 | 168730 | 6.23 | 6300 | 1479.4972 |  | 3
65 | 85 | 63 | 29.0563 | 179500 | 179500 | 6.23 | 6300 | 1479.4972 |  | 3
65 | 75 | 67 | 66.7494 | 172700 | 96712 | 6.21 | 4200 | 687.6536 |  | 3
65 | 80 | 67 | 51.5724 | 172700 | 117436 | 6.21 | 4200 | 687.6536 |  | 3
65 | 85 | 67 | 39.6049 | 172700 | 139887 | 6.21 | 4200 | 687.6536 |  | 3
65 | 75 | 67 | 66.7494 | 181000 | 106790 | 6.22 | 5250 | 1041.8994 |  | 3
65 | 80 | 67 | 51.5724 | 181000 | 132130 | 6.22 | 5250 | 1041.8994 |  | 3
65 | 85 | 67 | 39.6049 | 181000 | 155660 | 6.22 | 5250 | 1041.8994 |  | 3
65 | 75 | 67 | 66.7494 | 186500 | 113765 | 6.27 | 6300 | 1479.4972 |  | 3
65 | 80 | 67 | 51.5724 | 186500 | 143605 | 6.27 | 6300 | 1479.4972 |  | 3
65 | 85 | 67 | 39.6049 | 186500 | 169715 | 6.27 | 6300 | 1479.4972 |  | 3
65 | 75 | 71 | 82.6659 | 183100 | 75071 | 6.26 | 4200 | 687.6536 |  | 3
65 | 80 | 71 | 65.0618 | 183100 | 98874 | 6.26 | 4200 | 687.6536 |  | 3
65 | 85 | 71 | 51.076 | 183100 | 120846 | 6.26 | 4200 | 687.6536 |  | 3
65 | 75 | 71 | 82.6659 | 191100 | 80262 | 6.29 | 5250 | 1041.8994 |  | 3
65 | 80 | 71 | 65.0618 | 191100 | 107016 | 6.29 | 5250 | 1041.8994 |  | 3
65 | 85 | 71 | 51.076 | 191100 | 133770 | 6.29 | 5250 | 1041.8994 |  | 3
65 | 75 | 71 | 82.6659 | 196900 | 82698 | 6.31 | 6300 | 1479.4972 |  | 3
65 | 80 | 71 | 65.0618 | 196900 | 118140 | 6.31 | 6300 | 1479.4972 |  | 3
65 | 85 | 71 | 51.076 | 196900 | 149644 | 6.31 | 6300 | 1479.4972 |  | 3
75 | 75 | 63 | 52.1129 | 156100 | 110831 | 6.95 | 4200 | 687.6536 |  | 3
75 | 80 | 63 | 39.1676 | 156100 | 131124 | 6.95 | 4200 | 687.6536 |  | 3
75 | 85 | 63 | 29.0563 | 156100 | 148295 | 6.95 | 4200 | 687.6536 |  | 3
75 | 75 | 63 | 52.1129 | 164300 | 126511 | 6.98 | 5250 | 1041.8994 |  | 3
75 | 80 | 63 | 39.1676 | 164300 | 147870 | 6.98 | 5250 | 1041.8994 |  | 3
75 | 85 | 63 | 29.0563 | 164300 | 164300 | 6.98 | 5250 | 1041.8994 |  | 3
75 | 75 | 63 | 52.1129 | 171000 | 138510 | 6.97 | 6300 | 1479.4972 |  | 3
75 | 80 | 63 | 39.1676 | 171000 | 162450 | 6.97 | 6300 | 1479.4972 |  | 3
75 | 85 | 63 | 29.0563 | 171000 | 171000 | 6.97 | 6300 | 1479.4972 |  | 3
75 | 75 | 67 | 66.7494 | 164300 | 92008 | 6.97 | 4200 | 687.6536 |  | 3
75 | 80 | 67 | 51.5724 | 164300 | 113367 | 6.97 | 4200 | 687.6536 |  | 3
75 | 85 | 67 | 39.6049 | 164300 | 133083 | 6.97 | 4200 | 687.6536 |  | 3
75 | 75 | 67 | 66.7494 | 171900 | 99702 | 6.99 | 5250 | 1041.8994 |  | 3
75 | 80 | 67 | 51.5724 | 171900 | 127206 | 6.99 | 5250 | 1041.8994 |  | 3
75 | 85 | 67 | 39.6049 | 171900 | 149553 | 6.99 | 5250 | 1041.8994 |  | 3
75 | 75 | 67 | 66.7494 | 177300 | 108153 | 7.02 | 6300 | 1479.4972 |  | 3
75 | 80 | 67 | 51.5724 | 177300 | 138294 | 7.02 | 6300 | 1479.4972 |  | 3
75 | 85 | 67 | 39.6049 | 177300 | 164889 | 7.02 | 6300 | 1479.4972 |  | 3
75 | 75 | 71 | 82.6659 | 174400 | 71504 | 7.01 | 4200 | 687.6536 |  | 3
75 | 80 | 71 | 65.0618 | 174400 | 94176 | 7.01 | 4200 | 687.6536 |  | 3
75 | 85 | 71 | 51.076 | 174400 | 116848 | 7.01 | 4200 | 687.6536 |  | 3
75 | 75 | 71 | 82.6659 | 181800 | 74538 | 7.03 | 5250 | 1041.8994 |  | 3
75 | 80 | 71 | 65.0618 | 181800 | 103626 | 7.03 | 5250 | 1041.8994 |  | 3
75 | 85 | 71 | 51.076 | 181800 | 129078 | 7.03 | 5250 | 1041.8994 |  | 3
75 | 75 | 71 | 82.6659 | 187400 | 78708 | 7.03 | 6300 | 1479.4972 |  | 3
75 | 80 | 71 | 65.0618 | 187400 | 114314 | 7.03 | 6300 | 1479.4972 |  | 3
75 | 85 | 71 | 51.076 | 187400 | 142424 | 7.03 | 6300 | 1479.4972 |  | 3
85 | 75 | 63 | 52.1129 | 147800 | 106416 | 7.82 | 4200 | 687.6536 |  | 3
85 | 80 | 63 | 39.1676 | 147800 | 125630 | 7.82 | 4200 | 687.6536 |  | 3
85 | 85 | 63 | 29.0563 | 147800 | 143366 | 7.82 | 4200 | 687.6536 |  | 3
85 | 75 | 63 | 52.1129 | 155600 | 121368 | 7.85 | 5250 | 1041.8994 |  | 3
85 | 80 | 63 | 39.1676 | 155600 | 143152 | 7.85 | 5250 | 1041.8994 |  | 3
85 | 85 | 63 | 29.0563 | 155600 | 155600 | 7.85 | 5250 | 1041.8994 |  | 3
85 | 75 | 63 | 52.1129 | 161900 | 134377 | 7.84 | 6300 | 1479.4972 |  | 3
85 | 80 | 63 | 39.1676 | 161900 | 157043 | 7.84 | 6300 | 1479.4972 |  | 3
85 | 85 | 63 | 29.0563 | 161900 | 161900 | 7.84 | 6300 | 1479.4972 |  | 3
85 | 75 | 67 | 66.7494 | 155400 | 83916 | 7.85 | 4200 | 687.6536 |  | 3
85 | 80 | 67 | 51.5724 | 155400 | 108780 | 7.85 | 4200 | 687.6536 |  | 3
85 | 85 | 67 | 39.6049 | 155400 | 127428 | 7.85 | 4200 | 687.6536 |  | 3
85 | 75 | 67 | 66.7494 | 162300 | 95757 | 7.88 | 5250 | 1041.8994 |  | 3
85 | 80 | 67 | 51.5724 | 162300 | 121725 | 7.88 | 5250 | 1041.8994 |  | 3
85 | 85 | 67 | 39.6049 | 162300 | 144447 | 7.88 | 5250 | 1041.8994 |  | 3
85 | 75 | 67 | 66.7494 | 167400 | 102114 | 7.89 | 6300 | 1479.4972 |  | 3
85 | 80 | 67 | 51.5724 | 167400 | 135594 | 7.89 | 6300 | 1479.4972 |  | 3
85 | 85 | 67 | 39.6049 | 167400 | 159030 | 7.89 | 6300 | 1479.4972 |  | 3
85 | 75 | 71 | 82.6659 | 165000 | 66000 | 7.89 | 4200 | 687.6536 |  | 3
85 | 80 | 71 | 65.0618 | 165000 | 87450 | 7.89 | 4200 | 687.6536 |  | 3
85 | 85 | 71 | 51.076 | 165000 | 112200 | 7.89 | 4200 | 687.6536 |  | 3
85 | 75 | 71 | 82.6659 | 171800 | 70438 | 7.91 | 5250 | 1041.8994 |  | 3
85 | 80 | 71 | 65.0618 | 171800 | 97926 | 7.91 | 5250 | 1041.8994 |  | 3
85 | 85 | 71 | 51.076 | 171800 | 127132 | 7.91 | 5250 | 1041.8994 |  | 3
85 | 75 | 71 | 82.6659 | 176900 | 74298 | 7.92 | 6300 | 1479.4972 |  | 3
85 | 80 | 71 | 65.0618 | 176900 | 107909 | 7.92 | 6300 | 1479.4972 |  | 3
85 | 85 | 71 | 51.076 | 176900 | 137982 | 7.92 | 6300 | 1479.4972 |  | 3
95 | 75 | 63 | 52.1129 | 139200 | 101616 | 8.85 | 4200 | 687.6536 |  | 3
95 | 80 | 63 | 39.1676 | 139200 | 121104 | 8.85 | 4200 | 687.6536 |  | 3
95 | 85 | 63 | 29.0563 | 139200 | 137808 | 8.85 | 4200 | 687.6536 |  | 3
95 | 75 | 63 | 52.1129 | 146600 | 115814 | 8.85 | 5250 | 1041.8994 |  | 3
95 | 80 | 63 | 39.1676 | 146600 | 137804 | 8.85 | 5250 | 1041.8994 |  | 3
95 | 85 | 63 | 29.0563 | 146600 | 146600 | 8.85 | 5250 | 1041.8994 |  | 3
95 | 75 | 63 | 52.1129 | 152500 | 126575 | 8.86 | 6300 | 1479.4972 |  | 3
95 | 80 | 63 | 39.1676 | 152500 | 150975 | 8.86 | 6300 | 1479.4972 |  | 3
95 | 85 | 63 | 29.0563 | 152500 | 152500 | 8.86 | 6300 | 1479.4972 |  | 3
95 | 75 | 67 | 66.7494 | 146500 | 80575 | 8.83 | 4200 | 687.6536 |  | 3
95 | 80 | 67 | 51.5724 | 146500 | 104015 | 8.83 | 4200 | 687.6536 |  | 3
95 | 85 | 67 | 39.6049 | 146500 | 123060 | 8.83 | 4200 | 687.6536 |  | 3
95 | 75 | 67 | 66.7494 | 153000 | 91800 | 8.86 | 5250 | 1041.8994 |  | 3
95 | 80 | 67 | 51.5724 | 153000 | 116280 | 8.86 | 5250 | 1041.8994 |  | 3
95 | 85 | 67 | 39.6049 | 153000 | 139230 | 8.86 | 5250 | 1041.8994 |  | 3
95 | 75 | 67 | 66.7494 | 157300 | 97526 | 8.9 | 6300 | 1479.4972 |  | 3
95 | 80 | 67 | 51.5724 | 157300 | 128986 | 8.9 | 6300 | 1479.4972 |  | 3
95 | 85 | 67 | 39.6049 | 157300 | 152581 | 8.9 | 6300 | 1479.4972 |  | 3
95 | 75 | 71 | 82.6659 | 155300 | 60567 | 8.9 | 4200 | 687.6536 |  | 3
95 | 80 | 71 | 65.0618 | 155300 | 85415 | 8.9 | 4200 | 687.6536 |  | 3
95 | 85 | 71 | 51.076 | 155300 | 107157 | 8.9 | 4200 | 687.6536 |  | 3
95 | 75 | 71 | 82.6659 | 161600 | 66256 | 8.92 | 5250 | 1041.8994 |  | 3
95 | 80 | 71 | 65.0618 | 161600 | 95344 | 8.92 | 5250 | 1041.8994 |  | 3
95 | 85 | 71 | 51.076 | 161600 | 121200 | 8.92 | 5250 | 1041.8994 |  | 3
95 | 75 | 71 | 82.6659 | 166100 | 68101 | 8.91 | 6300 | 1479.4972 |  | 3
95 | 80 | 71 | 65.0618 | 166100 | 101321 | 8.91 | 6300 | 1479.4972 |  | 3
95 | 85 | 71 | 51.076 | 166100 | 134541 | 8.91 | 6300 | 1479.4972 |  | 3
85 | 75 | 63 | 52.1129 | 211700 | 154541 | 11.57 | 5600 | 1208.6034 |  | 4
85 | 80 | 63 | 39.1676 | 211700 | 175711 | 11.57 | 5600 | 1208.6034 |  | 4
85 | 85 | 63 | 29.0563 | 211700 | 198998 | 11.57 | 5600 | 1208.6034 |  | 4
85 | 75 | 63 | 52.1129 | 223800 | 167850 | 11.61 | 7000 | 1958.771 |  | 4
85 | 80 | 63 | 39.1676 | 223800 | 199182 | 11.61 | 7000 | 1958.771 |  | 4
85 | 85 | 63 | 29.0563 | 223800 | 223800 | 11.61 | 7000 | 1958.771 |  | 4
85 | 75 | 63 | 52.1129 | 233200 | 186560 | 11.65 | 8400 | 3042.3464 |  | 4
85 | 80 | 63 | 39.1676 | 233200 | 221540 | 11.65 | 8400 | 3042.3464 |  | 4
85 | 85 | 63 | 29.0563 | 233200 | 233200 | 11.65 | 8400 | 3042.3464 |  | 4
85 | 75 | 67 | 66.7494 | 221900 | 124264 | 11.61 | 5600 | 1208.6034 |  | 4
85 | 80 | 67 | 51.5724 | 221900 | 157549 | 11.61 | 5600 | 1208.6034 |  | 4
85 | 85 | 67 | 39.6049 | 221900 | 177520 | 11.61 | 5600 | 1208.6034 |  | 4
85 | 75 | 67 | 66.7494 | 232600 | 137234 | 11.65 | 7000 | 1958.771 |  | 4
85 | 80 | 67 | 51.5724 | 232600 | 174450 | 11.65 | 7000 | 1958.771 |  | 4
85 | 85 | 67 | 39.6049 | 232600 | 202362 | 11.65 | 7000 | 1958.771 |  | 4
85 | 75 | 67 | 66.7494 | 241100 | 149482 | 11.68 | 8400 | 3042.3464 |  | 4
85 | 80 | 67 | 51.5724 | 241100 | 185647 | 11.68 | 8400 | 3042.3464 |  | 4
85 | 85 | 67 | 39.6049 | 241100 | 221812 | 11.68 | 8400 | 3042.3464 |  | 4
85 | 75 | 71 | 82.6659 | 236800 | 97088 | 11.67 | 5600 | 1208.6034 |  | 4
85 | 80 | 71 | 65.0618 | 236800 | 130240 | 11.67 | 5600 | 1208.6034 |  | 4
85 | 85 | 71 | 51.076 | 236800 | 163392 | 11.67 | 5600 | 1208.6034 |  | 4
85 | 75 | 71 | 82.6659 | 247400 | 106382 | 11.71 | 7000 | 1958.771 |  | 4
85 | 80 | 71 | 65.0618 | 247400 | 145966 | 11.71 | 7000 | 1958.771 |  | 4
85 | 85 | 71 | 51.076 | 247400 | 180602 | 11.71 | 7000 | 1958.771 |  | 4
85 | 75 | 71 | 82.6659 | 254700 | 114615 | 11.74 | 8400 | 3042.3464 |  | 4
85 | 80 | 71 | 65.0618 | 254700 | 157914 | 11.74 | 8400 | 3042.3464 |  | 4
85 | 85 | 71 | 51.076 | 254700 | 193572 | 11.74 | 8400 | 3042.3464 |  | 4
95 | 75 | 63 | 52.1129 | 199600 | 145708 | 13.07 | 5600 | 1125.2514 |  | 4
95 | 80 | 63 | 39.1676 | 199600 | 169660 | 13.07 | 5600 | 1125.2514 |  | 4
95 | 85 | 63 | 29.0563 | 199600 | 191616 | 13.07 | 5600 | 1125.2514 |  | 4
95 | 75 | 63 | 52.1129 | 210700 | 160132 | 13.12 | 7000 | 1958.771 |  | 4
95 | 80 | 63 | 39.1676 | 210700 | 191737 | 13.12 | 7000 | 1958.771 |  | 4
95 | 85 | 63 | 29.0563 | 210700 | 210700 | 13.12 | 7000 | 1958.771 |  | 4
95 | 75 | 63 | 52.1129 | 219700 | 180154 | 13.16 | 8400 | 3042.3464 |  | 4
95 | 80 | 63 | 39.1676 | 219700 | 213109 | 13.16 | 8400 | 3042.3464 |  | 4
95 | 85 | 63 | 29.0563 | 219700 | 219700 | 13.16 | 8400 | 3042.3464 |  | 4
95 | 75 | 67 | 66.7494 | 208800 | 114840 | 13.12 | 5600 | 1125.2514 |  | 4
95 | 80 | 67 | 51.5724 | 208800 | 148248 | 13.12 | 5600 | 1125.2514 |  | 4
95 | 85 | 67 | 39.6049 | 208800 | 171216 | 13.12 | 5600 | 1125.2514 |  | 4
95 | 75 | 67 | 66.7494 | 218800 | 131280 | 13.16 | 7000 | 1958.771 |  | 4
95 | 80 | 67 | 51.5724 | 218800 | 166288 | 13.16 | 7000 | 1958.771 |  | 4
95 | 85 | 67 | 39.6049 | 218800 | 192544 | 13.16 | 7000 | 1958.771 |  | 4
95 | 75 | 67 | 66.7494 | 226700 | 142821 | 13.19 | 8400 | 3042.3464 |  | 4
95 | 80 | 67 | 51.5724 | 226700 | 179093 | 13.19 | 8400 | 3042.3464 |  | 4
95 | 85 | 67 | 39.6049 | 226700 | 213098 | 13.19 | 8400 | 3042.3464 |  | 4
95 | 75 | 71 | 82.6659 | 223000 | 89200 | 13.19 | 5600 | 1208.6034 |  | 4
95 | 80 | 71 | 65.0618 | 223000 | 122650 | 13.19 | 5600 | 1208.6034 |  | 4
95 | 85 | 71 | 51.076 | 223000 | 153870 | 13.19 | 5600 | 1208.6034 |  | 4
95 | 75 | 71 | 82.6659 | 232600 | 97692 | 13.22 | 7000 | 1958.771 |  | 4
95 | 80 | 71 | 65.0618 | 232600 | 137234 | 13.22 | 7000 | 1958.771 |  | 4
95 | 85 | 71 | 51.076 | 232600 | 172124 | 13.22 | 7000 | 1958.771 |  | 4
95 | 75 | 71 | 82.6659 | 239100 | 109986 | 13.25 | 8400 | 3042.3464 |  | 4
95 | 80 | 71 | 65.0618 | 239100 | 150633 | 13.25 | 8400 | 3042.3464 |  | 4
95 | 85 | 71 | 51.076 | 239100 | 186498 | 13.25 | 8400 | 3042.3464 |  | 4
105 | 75 | 63 | 52.1129 | 186700 | 138158 | 14.79 | 5600 | 1125.2514 |  | 4
105 | 80 | 63 | 39.1676 | 186700 | 162429 | 14.79 | 5600 | 1125.2514 |  | 4
105 | 85 | 63 | 29.0563 | 186700 | 182966 | 14.79 | 5600 | 1125.2514 |  | 4
105 | 75 | 63 | 52.1129 | 197200 | 153816 | 14.84 | 7000 | 1854.581 |  | 4
105 | 80 | 63 | 39.1676 | 197200 | 183396 | 14.84 | 7000 | 1854.581 |  | 4
105 | 85 | 63 | 29.0563 | 197200 | 197200 | 14.84 | 7000 | 1854.581 |  | 4
105 | 75 | 63 | 52.1129 | 205900 | 172956 | 14.87 | 8400 | 2906.8994 |  | 4
105 | 80 | 63 | 39.1676 | 205900 | 203841 | 14.87 | 8400 | 2906.8994 |  | 4
105 | 85 | 63 | 29.0563 | 205900 | 205900 | 14.87 | 8400 | 2906.8994 |  | 4
105 | 75 | 67 | 66.7494 | 194800 | 111036 | 14.84 | 5600 | 1125.2514 |  | 4
105 | 80 | 67 | 51.5724 | 194800 | 142204 | 14.84 | 5600 | 1125.2514 |  | 4
105 | 85 | 67 | 39.6049 | 194800 | 163632 | 14.84 | 5600 | 1125.2514 |  | 4
105 | 75 | 67 | 66.7494 | 204500 | 124745 | 14.87 | 7000 | 1854.581 |  | 4
105 | 80 | 67 | 51.5724 | 204500 | 157465 | 14.87 | 7000 | 1854.581 |  | 4
105 | 85 | 67 | 39.6049 | 204500 | 184050 | 14.87 | 7000 | 1854.581 |  | 4
105 | 75 | 67 | 66.7494 | 212000 | 137800 | 14.9 | 8400 | 3042.3464 |  | 4
105 | 80 | 67 | 51.5724 | 212000 | 173840 | 14.9 | 8400 | 3042.3464 |  | 4
105 | 85 | 67 | 39.6049 | 212000 | 205640 | 14.9 | 8400 | 3042.3464 |  | 4
105 | 75 | 71 | 82.6659 | 208700 | 81393 | 14.9 | 5600 | 1125.2514 |  | 4
105 | 80 | 71 | 65.0618 | 208700 | 114785 | 14.9 | 5600 | 1125.2514 |  | 4
105 | 85 | 71 | 51.076 | 208700 | 146090 | 14.9 | 5600 | 1125.2514 |  | 4
105 | 75 | 71 | 82.6659 | 216900 | 95436 | 14.93 | 7000 | 1958.771 |  | 4
105 | 80 | 71 | 65.0618 | 216900 | 132309 | 14.93 | 7000 | 1958.771 |  | 4
105 | 85 | 71 | 51.076 | 216900 | 160506 | 14.93 | 7000 | 1958.771 |  | 4
105 | 75 | 71 | 82.6659 | 222600 | 106848 | 14.95 | 8400 | 3042.3464 |  | 4
105 | 80 | 71 | 65.0618 | 222600 | 144690 | 14.95 | 8400 | 3042.3464 |  | 4
105 | 85 | 71 | 51.076 | 222600 | 178080 | 14.95 | 8400 | 3042.3464 |  | 4
115 | 75 | 63 | 52.1129 | 173300 | 128242 | 16.71 | 5600 | 1125.2514 |  | 4
115 | 80 | 63 | 39.1676 | 173300 | 154237 | 16.71 | 5600 | 1125.2514 |  | 4
115 | 85 | 63 | 29.0563 | 173300 | 171567 | 16.71 | 5600 | 1125.2514 |  | 4
115 | 75 | 63 | 52.1129 | 183300 | 148473 | 16.76 | 7000 | 1854.581 |  | 4
115 | 80 | 63 | 39.1676 | 183300 | 175968 | 16.76 | 7000 | 1854.581 |  | 4
115 | 85 | 63 | 29.0563 | 183300 | 183300 | 16.76 | 7000 | 1854.581 |  | 4
115 | 75 | 63 | 52.1129 | 191600 | 164776 | 16.79 | 8400 | 2906.8994 |  | 4
115 | 80 | 63 | 39.1676 | 191600 | 191600 | 16.79 | 8400 | 2906.8994 |  | 4
115 | 85 | 63 | 29.0563 | 191600 | 191600 | 16.79 | 8400 | 2906.8994 |  | 4
115 | 75 | 67 | 66.7494 | 180700 | 102999 | 16.75 | 5600 | 1125.2514 |  | 4
115 | 80 | 67 | 51.5724 | 180700 | 131911 | 16.75 | 5600 | 1125.2514 |  | 4
115 | 85 | 67 | 39.6049 | 180700 | 155402 | 16.75 | 5600 | 1125.2514 |  | 4
115 | 75 | 67 | 66.7494 | 189700 | 119511 | 16.78 | 7000 | 1854.581 |  | 4
115 | 80 | 67 | 51.5724 | 189700 | 147966 | 16.78 | 7000 | 1854.581 |  | 4
115 | 85 | 67 | 39.6049 | 189700 | 176421 | 16.78 | 7000 | 1854.581 |  | 4
115 | 75 | 67 | 66.7494 | 196500 | 131655 | 16.8 | 8400 | 2906.8994 |  | 4
115 | 80 | 67 | 51.5724 | 196500 | 165060 | 16.8 | 8400 | 2906.8994 |  | 4
115 | 85 | 67 | 39.6049 | 196500 | 194535 | 16.8 | 8400 | 2906.8994 |  | 4
115 | 75 | 71 | 82.6659 | 192900 | 77160 | 16.8 | 5600 | 1125.2514 |  | 4
115 | 80 | 71 | 65.0618 | 192900 | 109953 | 16.8 | 5600 | 1125.2514 |  | 4
115 | 85 | 71 | 51.076 | 192900 | 136959 | 16.8 | 5600 | 1125.2514 |  | 4
115 | 75 | 71 | 82.6659 | 200000 | 90000 | 16.83 | 7000 | 1854.581 |  | 4
115 | 80 | 71 | 65.0618 | 200000 | 126000 | 16.83 | 7000 | 1854.581 |  | 4
115 | 85 | 71 | 51.076 | 200000 | 152000 | 16.83 | 7000 | 1854.581 |  | 4
115 | 75 | 71 | 82.6659 | 206000 | 96820 | 16.84 | 8400 | 2906.8994 |  | 4
115 | 80 | 71 | 65.0618 | 206000 | 138020 | 16.84 | 8400 | 2906.8994 |  | 4
115 | 85 | 71 | 51.076 | 206000 | 168920 | 16.84 | 8400 | 2906.8994 |  | 4
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 5
Degradation Coefficient (C_d)
IEER or SEER | 17.5
Standby Power (W)
Crankcase Heater Power (W)
Net
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 75 | 63 | 52.1129 | 51600 | 41280 | 1.76 | 1600 | 250.0559 |  | 1
65 | 80 | 63 | 39.1676 | 51600 | 47988 | 1.76 | 1600 | 250.0559 |  | 1
65 | 85 | 63 | 29.0563 | 51600 | 51084 | 1.76 | 1600 | 250.0559 |  | 1
65 | 75 | 63 | 52.1129 | 54400 | 45696 | 1.75 | 2000 | 250.0559 |  | 1
65 | 80 | 63 | 39.1676 | 54400 | 51680 | 1.75 | 2000 | 250.0559 |  | 1
65 | 85 | 63 | 29.0563 | 54400 | 54400 | 1.75 | 2000 | 250.0559 |  | 1
65 | 75 | 63 | 52.1129 | 56500 | 49155 | 1.74 | 2400 | 250.0559 |  | 1
65 | 80 | 63 | 39.1676 | 56500 | 54805 | 1.74 | 2400 | 250.0559 |  | 1
65 | 85 | 63 | 29.0563 | 56500 | 56500 | 1.74 | 2400 | 250.0559 |  | 1
65 | 75 | 67 | 66.7494 | 54500 | 28340 | 1.75 | 1600 | 250.0559 |  | 1
65 | 80 | 67 | 51.5724 | 54500 | 40330 | 1.75 | 1600 | 250.0559 |  | 1
65 | 85 | 67 | 39.6049 | 54500 | 49050 | 1.75 | 1600 | 250.0559 |  | 1
65 | 75 | 67 | 66.7494 | 57300 | 30942 | 1.73 | 2000 | 250.0559 |  | 1
65 | 80 | 67 | 51.5724 | 57300 | 45840 | 1.73 | 2000 | 250.0559 |  | 1
65 | 85 | 67 | 39.6049 | 57300 | 53289 | 1.73 | 2000 | 250.0559 |  | 1
65 | 75 | 67 | 66.7494 | 59300 | 33801 | 1.72 | 2400 | 250.0559 |  | 1
65 | 80 | 67 | 51.5724 | 59300 | 49812 | 1.72 | 2400 | 250.0559 |  | 1
65 | 85 | 67 | 39.6049 | 59300 | 56928 | 1.72 | 2400 | 250.0559 |  | 1
65 | 75 | 71 | 82.6659 | 57500 | 13800 | 1.73 | 1600 | 250.0559 |  | 1
65 | 80 | 71 | 65.0618 | 57500 | 27025 | 1.73 | 1600 | 250.0559 |  | 1
65 | 85 | 71 | 51.076 | 57500 | 39675 | 1.73 | 1600 | 250.0559 |  | 1
65 | 75 | 71 | 82.6659 | 60300 | 14472 | 1.72 | 2000 | 250.0559 |  | 1
65 | 80 | 71 | 65.0618 | 60300 | 30150 | 1.72 | 2000 | 250.0559 |  | 1
65 | 85 | 71 | 51.076 | 60300 | 44622 | 1.72 | 2000 | 250.0559 |  | 1
65 | 75 | 71 | 82.6659 | 62500 | 15000 | 1.71 | 2400 | 250.0559 |  | 1
65 | 80 | 71 | 65.0618 | 62500 | 33125 | 1.71 | 2400 | 250.0559 |  | 1
65 | 85 | 71 | 51.076 | 62500 | 50000 | 1.71 | 2400 | 250.0559 |  | 1
75 | 75 | 63 | 52.1129 | 49400 | 39520 | 1.98 | 1600 | 250.0559 |  | 1
75 | 80 | 63 | 39.1676 | 49400 | 45942 | 1.98 | 1600 | 250.0559 |  | 1
75 | 85 | 63 | 29.0563 | 49400 | 48906 | 1.98 | 1600 | 250.0559 |  | 1
75 | 75 | 63 | 52.1129 | 51900 | 44115 | 1.97 | 2000 | 250.0559 |  | 1
75 | 80 | 63 | 39.1676 | 51900 | 49824 | 1.97 | 2000 | 250.0559 |  | 1
75 | 85 | 63 | 29.0563 | 51900 | 51900 | 1.97 | 2000 | 250.0559 |  | 1
75 | 75 | 63 | 52.1129 | 54000 | 47520 | 1.97 | 2400 | 250.0559 |  | 1
75 | 80 | 63 | 39.1676 | 54000 | 52920 | 1.97 | 2400 | 250.0559 |  | 1
75 | 85 | 63 | 29.0563 | 54000 | 54000 | 1.97 | 2400 | 250.0559 |  | 1
75 | 75 | 67 | 66.7494 | 52000 | 26520 | 1.97 | 1600 | 250.0559 |  | 1
75 | 80 | 67 | 51.5724 | 52000 | 39000 | 1.97 | 1600 | 250.0559 |  | 1
75 | 85 | 67 | 39.6049 | 52000 | 46800 | 1.97 | 1600 | 250.0559 |  | 1
75 | 75 | 67 | 66.7494 | 54700 | 28991 | 1.97 | 2000 | 250.0559 |  | 1
75 | 80 | 67 | 51.5724 | 54700 | 44307 | 1.97 | 2000 | 250.0559 |  | 1
75 | 85 | 67 | 39.6049 | 54700 | 51418 | 1.97 | 2000 | 250.0559 |  | 1
75 | 75 | 67 | 66.7494 | 56600 | 32262 | 1.97 | 2400 | 250.0559 |  | 1
75 | 80 | 67 | 51.5724 | 56600 | 48110 | 1.97 | 2400 | 250.0559 |  | 1
75 | 85 | 67 | 39.6049 | 56600 | 54336 | 1.97 | 2400 | 250.0559 |  | 1
75 | 75 | 71 | 82.6659 | 54900 | 12078 | 1.97 | 1600 | 250.0559 |  | 1
75 | 80 | 71 | 65.0618 | 54900 | 25803 | 1.97 | 1600 | 250.0559 |  | 1
75 | 85 | 71 | 51.076 | 54900 | 37881 | 1.97 | 1600 | 250.0559 |  | 1
75 | 75 | 71 | 82.6659 | 57600 | 12672 | 1.96 | 2000 | 250.0559 |  | 1
75 | 80 | 71 | 65.0618 | 57600 | 28800 | 1.96 | 2000 | 250.0559 |  | 1
75 | 85 | 71 | 51.076 | 57600 | 43200 | 1.96 | 2000 | 250.0559 |  | 1
75 | 75 | 71 | 82.6659 | 59500 | 13090 | 1.96 | 2400 | 250.0559 |  | 1
75 | 80 | 71 | 65.0618 | 59500 | 31535 | 1.96 | 2400 | 250.0559 |  | 1
75 | 85 | 71 | 51.076 | 59500 | 48195 | 1.96 | 2400 | 250.0559 |  | 1
85 | 75 | 63 | 52.1129 | 46600 | 37280 | 2.28 | 1600 | 250.0559 |  | 1
85 | 80 | 63 | 39.1676 | 46600 | 43804 | 2.28 | 1600 | 250.0559 |  | 1
85 | 85 | 63 | 29.0563 | 46600 | 46134 | 2.28 | 1600 | 250.0559 |  | 1
85 | 75 | 63 | 52.1129 | 49000 | 41650 | 2.28 | 2000 | 250.0559 |  | 1
85 | 80 | 63 | 39.1676 | 49000 | 47040 | 2.28 | 2000 | 250.0559 |  | 1
85 | 85 | 63 | 29.0563 | 49000 | 49000 | 2.28 | 2000 | 250.0559 |  | 1
85 | 75 | 63 | 52.1129 | 51100 | 44968 | 2.28 | 2400 | 250.0559 |  | 1
85 | 80 | 63 | 39.1676 | 51100 | 50589 | 2.28 | 2400 | 250.0559 |  | 1
85 | 85 | 63 | 29.0563 | 51100 | 51100 | 2.28 | 2400 | 250.0559 |  | 1
85 | 75 | 67 | 66.7494 | 49200 | 24600 | 2.28 | 1600 | 250.0559 |  | 1
85 | 80 | 67 | 51.5724 | 49200 | 36900 | 2.28 | 1600 | 250.0559 |  | 1
85 | 85 | 67 | 39.6049 | 49200 | 44772 | 2.28 | 1600 | 250.0559 |  | 1
85 | 75 | 67 | 66.7494 | 51600 | 27348 | 2.28 | 2000 | 250.0559 |  | 1
85 | 80 | 67 | 51.5724 | 51600 | 42312 | 2.28 | 2000 | 250.0559 |  | 1
85 | 85 | 67 | 39.6049 | 51600 | 49020 | 2.28 | 2000 | 250.0559 |  | 1
85 | 75 | 67 | 66.7494 | 53400 | 29904 | 2.28 | 2400 | 250.0559 |  | 1
85 | 80 | 67 | 51.5724 | 53400 | 45924 | 2.28 | 2400 | 250.0559 |  | 1
85 | 85 | 67 | 39.6049 | 53400 | 51798 | 2.28 | 2400 | 250.0559 |  | 1
85 | 75 | 71 | 82.6659 | 52000 | 10400 | 2.28 | 1600 | 250.0559 |  | 1
85 | 80 | 71 | 65.0618 | 52000 | 23920 | 2.28 | 1600 | 250.0559 |  | 1
85 | 85 | 71 | 51.076 | 52000 | 36400 | 2.28 | 1600 | 250.0559 |  | 1
85 | 75 | 71 | 82.6659 | 54500 | 10900 | 2.28 | 2000 | 250.0559 |  | 1
85 | 80 | 71 | 65.0618 | 54500 | 27250 | 2.28 | 2000 | 250.0559 |  | 1
85 | 85 | 71 | 51.076 | 54500 | 41965 | 2.28 | 2000 | 250.0559 |  | 1
85 | 75 | 71 | 82.6659 | 56300 | 11823 | 2.28 | 2400 | 250.0559 |  | 1
85 | 80 | 71 | 65.0618 | 56300 | 29839 | 2.28 | 2400 | 250.0559 |  | 1
85 | 85 | 71 | 51.076 | 56300 | 46729 | 2.28 | 2400 | 250.0559 |  | 1
95 | 75 | 63 | 52.1129 | 43500 | 35235 | 2.63 | 1600 | 250.0559 |  | 1
95 | 80 | 63 | 39.1676 | 43500 | 41325 | 2.63 | 1600 | 250.0559 |  | 1
95 | 85 | 63 | 29.0563 | 43500 | 43500 | 2.63 | 1600 | 250.0559 |  | 1
95 | 75 | 63 | 52.1129 | 45900 | 39474 | 2.63 | 2000 | 250.0559 |  | 1
95 | 80 | 63 | 39.1676 | 45900 | 44523 | 2.63 | 2000 | 250.0559 |  | 1
95 | 85 | 63 | 29.0563 | 45900 | 45900 | 2.63 | 2000 | 250.0559 |  | 1
95 | 75 | 63 | 52.1129 | 47900 | 42631 | 2.64 | 2400 | 250.0559 |  | 1
95 | 80 | 63 | 39.1676 | 47900 | 47421 | 2.64 | 2400 | 250.0559 |  | 1
95 | 85 | 63 | 29.0563 | 47900 | 47900 | 2.64 | 2400 | 250.0559 |  | 1
95 | 75 | 67 | 66.7494 | 46100 | 22589 | 2.63 | 1600 | 250.0559 |  | 1
95 | 80 | 67 | 51.5724 | 46100 | 35036 | 2.63 | 1600 | 250.0559 |  | 1
95 | 85 | 67 | 39.6049 | 46100 | 42412 | 2.63 | 1600 | 250.0559 |  | 1
95 | 75 | 67 | 66.7494 | 48300 | 25599 | 2.64 | 2000 | 250.0559 |  | 1
95 | 80 | 67 | 51.5724 | 48300 | 40089 | 2.64 | 2000 | 250.0559 |  | 1
95 | 85 | 67 | 39.6049 | 48300 | 45885 | 2.64 | 2000 | 250.0559 |  | 1
95 | 75 | 67 | 66.7494 | 50000 | 28500 | 2.64 | 2400 | 250.0559 |  | 1
95 | 80 | 67 | 51.5724 | 50000 | 43500 | 2.64 | 2400 | 250.0559 |  | 1
95 | 85 | 67 | 39.6049 | 50000 | 49000 | 2.64 | 2400 | 250.0559 |  | 1
95 | 75 | 71 | 82.6659 | 48800 | 8784 | 2.64 | 1600 | 250.0559 |  | 1
95 | 80 | 71 | 65.0618 | 48800 | 21960 | 2.64 | 1600 | 250.0559 |  | 1
95 | 85 | 71 | 51.076 | 48800 | 34648 | 2.64 | 1600 | 250.0559 |  | 1
95 | 75 | 71 | 82.6659 | 51100 | 9198 | 2.64 | 2000 | 250.0559 |  | 1
95 | 80 | 71 | 65.0618 | 51100 | 25039 | 2.64 | 2000 | 250.0559 |  | 1
95 | 85 | 71 | 51.076 | 51100 | 39858 | 2.64 | 2000 | 250.0559 |  | 1
95 | 75 | 71 | 82.6659 | 52800 | 10032 | 2.64 | 2400 | 250.0559 |  | 1
95 | 80 | 71 | 65.0618 | 52800 | 28512 | 2.64 | 2400 | 250.0559 |  | 1
95 | 85 | 71 | 51.076 | 52800 | 44352 | 2.64 | 2400 | 250.0559 |  | 1
65 | 75 | 63 | 52.1129 | 113600 | 84064 | 4.19 | 3200 | 416.7598 |  | 2
65 | 80 | 63 | 39.1676 | 113600 | 98832 | 4.19 | 3200 | 416.7598 |  | 2
65 | 85 | 63 | 29.0563 | 113600 | 109056 | 4.19 | 3200 | 416.7598 |  | 2
65 | 75 | 63 | 52.1129 | 119000 | 94010 | 4.21 | 4000 | 583.4637 |  | 2
65 | 80 | 63 | 39.1676 | 119000 | 109480 | 4.21 | 4000 | 583.4637 |  | 2
65 | 85 | 63 | 29.0563 | 119000 | 119000 | 4.21 | 4000 | 583.4637 |  | 2
65 | 75 | 63 | 52.1129 | 123100 | 100942 | 4.24 | 4800 | 771.0056 |  | 2
65 | 80 | 63 | 39.1676 | 123100 | 118176 | 4.24 | 4800 | 771.0056 |  | 2
65 | 85 | 63 | 29.0563 | 123100 | 123100 | 4.24 | 4800 | 771.0056 |  | 2
65 | 75 | 67 | 66.7494 | 119800 | 63494 | 4.21 | 3200 | 416.7598 |  | 2
65 | 80 | 67 | 51.5724 | 119800 | 85058 | 4.21 | 3200 | 416.7598 |  | 2
65 | 85 | 67 | 39.6049 | 119800 | 100632 | 4.21 | 3200 | 416.7598 |  | 2
65 | 75 | 67 | 66.7494 | 124800 | 71136 | 4.23 | 4000 | 583.4637 |  | 2
65 | 80 | 67 | 51.5724 | 124800 | 93600 | 4.23 | 4000 | 583.4637 |  | 2
65 | 85 | 67 | 39.6049 | 124800 | 111072 | 4.23 | 4000 | 583.4637 |  | 2
65 | 75 | 67 | 66.7494 | 128200 | 75638 | 4.25 | 4800 | 771.0056 |  | 2
65 | 80 | 67 | 51.5724 | 128200 | 102560 | 4.25 | 4800 | 771.0056 |  | 2
65 | 85 | 67 | 39.6049 | 128200 | 119226 | 4.25 | 4800 | 771.0056 |  | 2
65 | 75 | 71 | 82.6659 | 126500 | 45540 | 4.25 | 3200 | 416.7598 |  | 2
65 | 80 | 71 | 65.0618 | 126500 | 64515 | 4.25 | 3200 | 416.7598 |  | 2
65 | 85 | 71 | 51.076 | 126500 | 84755 | 4.25 | 3200 | 416.7598 |  | 2
65 | 75 | 71 | 82.6659 | 131300 | 45955 | 4.28 | 4000 | 583.4637 |  | 2
65 | 80 | 71 | 65.0618 | 131300 | 70902 | 4.28 | 4000 | 583.4637 |  | 2
65 | 85 | 71 | 51.076 | 131300 | 94536 | 4.28 | 4000 | 583.4637 |  | 2
65 | 75 | 71 | 82.6659 | 134400 | 47040 | 4.3 | 4800 | 771.0056 |  | 2
65 | 80 | 71 | 65.0618 | 134400 | 77952 | 4.3 | 4800 | 771.0056 |  | 2
65 | 85 | 71 | 51.076 | 134400 | 103488 | 4.3 | 4800 | 771.0056 |  | 2
75 | 75 | 63 | 52.1129 | 107700 | 78621 | 4.73 | 3200 | 416.7598 |  | 2
75 | 80 | 63 | 39.1676 | 107700 | 94776 | 4.73 | 3200 | 416.7598 |  | 2
75 | 85 | 63 | 29.0563 | 107700 | 104469 | 4.73 | 3200 | 416.7598 |  | 2
75 | 75 | 63 | 52.1129 | 112700 | 90160 | 4.77 | 4000 | 583.4637 |  | 2
75 | 80 | 63 | 39.1676 | 112700 | 104811 | 4.77 | 4000 | 583.4637 |  | 2
75 | 85 | 63 | 29.0563 | 112700 | 112700 | 4.77 | 4000 | 583.4637 |  | 2
75 | 75 | 63 | 52.1129 | 116600 | 96778 | 4.79 | 4800 | 771.0056 |  | 2
75 | 80 | 63 | 39.1676 | 116600 | 111936 | 4.79 | 4800 | 771.0056 |  | 2
75 | 85 | 63 | 29.0563 | 116600 | 116600 | 4.79 | 4800 | 771.0056 |  | 2
75 | 75 | 67 | 66.7494 | 113600 | 61344 | 4.76 | 3200 | 416.7598 |  | 2
75 | 80 | 67 | 51.5724 | 113600 | 79520 | 4.76 | 3200 | 416.7598 |  | 2
75 | 85 | 67 | 39.6049 | 113600 | 96560 | 4.76 | 3200 | 416.7598 |  | 2
75 | 75 | 67 | 66.7494 | 117900 | 66024 | 4.79 | 4000 | 583.4637 |  | 2
75 | 80 | 67 | 51.5724 | 117900 | 89604 | 4.79 | 4000 | 583.4637 |  | 2
75 | 85 | 67 | 39.6049 | 117900 | 106110 | 4.79 | 4000 | 583.4637 |  | 2
75 | 75 | 67 | 66.7494 | 121200 | 71508 | 4.8 | 4800 | 771.0056 |  | 2
75 | 80 | 67 | 51.5724 | 121200 | 98172 | 4.8 | 4800 | 771.0056 |  | 2
75 | 85 | 67 | 39.6049 | 121200 | 115140 | 4.8 | 4800 | 771.0056 |  | 2
75 | 75 | 71 | 82.6659 | 119800 | 41930 | 4.8 | 3200 | 416.7598 |  | 2
75 | 80 | 71 | 65.0618 | 119800 | 62296 | 4.8 | 3200 | 416.7598 |  | 2
75 | 85 | 71 | 51.076 | 119800 | 80266 | 4.8 | 3200 | 416.7598 |  | 2
75 | 75 | 71 | 82.6659 | 124000 | 43400 | 4.82 | 4000 | 583.4637 |  | 2
75 | 80 | 71 | 65.0618 | 124000 | 68200 | 4.82 | 4000 | 583.4637 |  | 2
75 | 85 | 71 | 51.076 | 124000 | 90520 | 4.82 | 4000 | 583.4637 |  | 2
75 | 75 | 71 | 82.6659 | 127100 | 44485 | 4.84 | 4800 | 771.0056 |  | 2
75 | 80 | 71 | 65.0618 | 127100 | 73718 | 4.84 | 4800 | 771.0056 |  | 2
75 | 85 | 71 | 51.076 | 127100 | 100409 | 4.84 | 4800 | 771.0056 |  | 2
85 | 75 | 63 | 52.1129 | 101300 | 75975 | 5.36 | 3200 | 375.0838 |  | 2
85 | 80 | 63 | 39.1676 | 101300 | 91170 | 5.36 | 3200 | 375.0838 |  | 2
85 | 85 | 63 | 29.0563 | 101300 | 99274 | 5.36 | 3200 | 375.0838 |  | 2
85 | 75 | 63 | 52.1129 | 105900 | 85779 | 5.4 | 4000 | 583.4637 |  | 2
85 | 80 | 63 | 39.1676 | 105900 | 99546 | 5.4 | 4000 | 583.4637 |  | 2
85 | 85 | 63 | 29.0563 | 105900 | 105900 | 5.4 | 4000 | 583.4637 |  | 2
85 | 75 | 63 | 52.1129 | 110100 | 92484 | 5.4 | 4800 | 771.0056 |  | 2
85 | 80 | 63 | 39.1676 | 110100 | 107898 | 5.4 | 4800 | 771.0056 |  | 2
85 | 85 | 63 | 29.0563 | 110100 | 110100 | 5.4 | 4800 | 771.0056 |  | 2
85 | 75 | 67 | 66.7494 | 106800 | 56604 | 5.38 | 3200 | 416.7598 |  | 2
85 | 80 | 67 | 51.5724 | 106800 | 76896 | 5.38 | 3200 | 416.7598 |  | 2
85 | 85 | 67 | 39.6049 | 106800 | 91848 | 5.38 | 3200 | 416.7598 |  | 2
85 | 75 | 67 | 66.7494 | 110900 | 62104 | 5.41 | 4000 | 583.4637 |  | 2
85 | 80 | 67 | 51.5724 | 110900 | 86502 | 5.41 | 4000 | 583.4637 |  | 2
85 | 85 | 67 | 39.6049 | 110900 | 102028 | 5.41 | 4000 | 583.4637 |  | 2
85 | 75 | 67 | 66.7494 | 114000 | 67260 | 5.42 | 4800 | 771.0056 |  | 2
85 | 80 | 67 | 51.5724 | 114000 | 93480 | 5.42 | 4800 | 771.0056 |  | 2
85 | 85 | 67 | 39.6049 | 114000 | 109440 | 5.42 | 4800 | 771.0056 |  | 2
85 | 75 | 71 | 82.6659 | 112900 | 38386 | 5.42 | 3200 | 416.7598 |  | 2
85 | 80 | 71 | 65.0618 | 112900 | 57579 | 5.42 | 3200 | 416.7598 |  | 2
85 | 85 | 71 | 51.076 | 112900 | 77901 | 5.42 | 3200 | 416.7598 |  | 2
85 | 75 | 71 | 82.6659 | 116800 | 40880 | 5.44 | 4000 | 583.4637 |  | 2
85 | 80 | 71 | 65.0618 | 116800 | 64240 | 5.44 | 4000 | 583.4637 |  | 2
85 | 85 | 71 | 51.076 | 116800 | 87600 | 5.44 | 4000 | 583.4637 |  | 2
85 | 75 | 71 | 82.6659 | 119500 | 41825 | 5.45 | 4800 | 771.0056 |  | 2
85 | 80 | 71 | 65.0618 | 119500 | 70505 | 5.45 | 4800 | 771.0056 |  | 2
85 | 85 | 71 | 51.076 | 119500 | 96795 | 5.45 | 4800 | 771.0056 |  | 2
95 | 75 | 63 | 52.1129 | 94700 | 71972 | 6.06 | 3200 | 375.0838 |  | 2
95 | 80 | 63 | 39.1676 | 94700 | 86177 | 6.06 | 3200 | 375.0838 |  | 2
95 | 85 | 63 | 29.0563 | 94700 | 93753 | 6.06 | 3200 | 375.0838 |  | 2
95 | 75 | 63 | 52.1129 | 99300 | 82419 | 6.09 | 4000 | 520.9497 |  | 2
95 | 80 | 63 | 39.1676 | 99300 | 94335 | 6.09 | 4000 | 520.9497 |  | 2
95 | 85 | 63 | 29.0563 | 99300 | 99300 | 6.09 | 4000 | 520.9497 |  | 2
95 | 75 | 63 | 52.1129 | 103200 | 89784 | 6.11 | 4800 | 698.0726 |  | 2
95 | 80 | 63 | 39.1676 | 103200 | 102168 | 6.11 | 4800 | 698.0726 |  | 2
95 | 85 | 63 | 29.0563 | 103200 | 103200 | 6.11 | 4800 | 698.0726 |  | 2
95 | 75 | 67 | 66.7494 | 99800 | 53892 | 6.09 | 3200 | 375.0838 |  | 2
95 | 80 | 67 | 51.5724 | 99800 | 71856 | 6.09 | 3200 | 375.0838 |  | 2
95 | 85 | 67 | 39.6049 | 99800 | 87824 | 6.09 | 3200 | 375.0838 |  | 2
95 | 75 | 67 | 66.7494 | 103600 | 58016 | 6.12 | 4000 | 520.9497 |  | 2
95 | 80 | 67 | 51.5724 | 103600 | 82880 | 6.12 | 4000 | 520.9497 |  | 2
95 | 85 | 67 | 39.6049 | 103600 | 97384 | 6.12 | 4000 | 520.9497 |  | 2
95 | 75 | 67 | 66.7494 | 106500 | 63900 | 6.13 | 4800 | 771.0056 |  | 2
95 | 80 | 67 | 51.5724 | 106500 | 89460 | 6.13 | 4800 | 771.0056 |  | 2
95 | 85 | 67 | 39.6049 | 106500 | 103305 | 6.13 | 4800 | 771.0056 |  | 2
95 | 75 | 71 | 82.6659 | 105600 | 34848 | 6.12 | 3200 | 416.7598 |  | 2
95 | 80 | 71 | 65.0618 | 105600 | 53856 | 6.12 | 3200 | 416.7598 |  | 2
95 | 85 | 71 | 51.076 | 105600 | 73920 | 6.12 | 3200 | 416.7598 |  | 2
95 | 75 | 71 | 82.6659 | 109300 | 36069 | 6.13 | 4000 | 583.4637 |  | 2
95 | 80 | 71 | 65.0618 | 109300 | 61208 | 6.13 | 4000 | 583.4637 |  | 2
95 | 85 | 71 | 51.076 | 109300 | 81975 | 6.13 | 4000 | 583.4637 |  | 2
95 | 75 | 71 | 82.6659 | 111800 | 38012 | 6.14 | 4800 | 771.0056 |  | 2
95 | 80 | 71 | 65.0618 | 111800 | 65962 | 6.14 | 4800 | 771.0056 |  | 2
95 | 85 | 71 | 51.076 | 111800 | 92794 | 6.14 | 4800 | 771.0056 |  | 2
65 | 75 | 63 | 52.1129 | 182500 | 135050 | 6.82 | 4800 | 843.9385 |  | 3
65 | 80 | 63 | 39.1676 | 182500 | 155125 | 6.82 | 4800 | 843.9385 |  | 3
65 | 85 | 63 | 29.0563 | 182500 | 171550 | 6.82 | 4800 | 843.9385 |  | 3
65 | 75 | 63 | 52.1129 | 192500 | 150150 | 6.87 | 6000 | 1364.8883 |  | 3
65 | 80 | 63 | 39.1676 | 192500 | 171325 | 6.87 | 6000 | 1364.8883 |  | 3
65 | 85 | 63 | 29.0563 | 192500 | 186725 | 6.87 | 6000 | 1364.8883 |  | 3
65 | 75 | 63 | 52.1129 | 200700 | 164574 | 6.91 | 7200 | 2042.1229 |  | 3
65 | 80 | 63 | 39.1676 | 200700 | 186651 | 6.91 | 7200 | 2042.1229 |  | 3
65 | 85 | 63 | 29.0563 | 200700 | 200700 | 6.91 | 7200 | 2042.1229 |  | 3
65 | 75 | 67 | 66.7494 | 193900 | 110523 | 6.88 | 4800 | 843.9385 |  | 3
65 | 80 | 67 | 51.5724 | 193900 | 135730 | 6.88 | 4800 | 843.9385 |  | 3
65 | 85 | 67 | 39.6049 | 193900 | 158998 | 6.88 | 4800 | 843.9385 |  | 3
65 | 75 | 67 | 66.7494 | 202500 | 121500 | 6.93 | 6000 | 1364.8883 |  | 3
65 | 80 | 67 | 51.5724 | 202500 | 151875 | 6.93 | 6000 | 1364.8883 |  | 3
65 | 85 | 67 | 39.6049 | 202500 | 176175 | 6.93 | 6000 | 1364.8883 |  | 3
65 | 75 | 67 | 66.7494 | 208100 | 126941 | 6.96 | 7200 | 2042.1229 |  | 3
65 | 80 | 67 | 51.5724 | 208100 | 166480 | 6.96 | 7200 | 2042.1229 |  | 3
65 | 85 | 67 | 39.6049 | 208100 | 189371 | 6.96 | 7200 | 2042.1229 |  | 3
65 | 75 | 71 | 82.6659 | 205100 | 84091 | 6.94 | 4800 | 843.9385 |  | 3
65 | 80 | 71 | 65.0618 | 205100 | 112805 | 6.94 | 4800 | 843.9385 |  | 3
65 | 85 | 71 | 51.076 | 205100 | 137417 | 6.94 | 4800 | 843.9385 |  | 3
65 | 75 | 71 | 82.6659 | 214000 | 89880 | 6.99 | 6000 | 1458.6592 |  | 3
65 | 80 | 71 | 65.0618 | 214000 | 121980 | 6.99 | 6000 | 1458.6592 |  | 3
65 | 85 | 71 | 51.076 | 214000 | 154080 | 6.99 | 6000 | 1458.6592 |  | 3
65 | 75 | 71 | 82.6659 | 220200 | 96888 | 7.02 | 7200 | 2167.1508 |  | 3
65 | 80 | 71 | 65.0618 | 220200 | 132120 | 7.02 | 7200 | 2167.1508 |  | 3
65 | 85 | 71 | 51.076 | 220200 | 171756 | 7.02 | 7200 | 2167.1508 |  | 3
75 | 75 | 63 | 52.1129 | 173000 | 129750 | 7.77 | 4800 | 843.9385 |  | 3
75 | 80 | 63 | 39.1676 | 173000 | 147050 | 7.77 | 4800 | 843.9385 |  | 3
75 | 85 | 63 | 29.0563 | 173000 | 164350 | 7.77 | 4800 | 843.9385 |  | 3
75 | 75 | 63 | 52.1129 | 182800 | 144412 | 7.81 | 6000 | 1364.8883 |  | 3
75 | 80 | 63 | 39.1676 | 182800 | 164520 | 7.81 | 6000 | 1364.8883 |  | 3
75 | 85 | 63 | 29.0563 | 182800 | 179144 | 7.81 | 6000 | 1364.8883 |  | 3
75 | 75 | 63 | 52.1129 | 190500 | 158115 | 7.85 | 7200 | 2042.1229 |  | 3
75 | 80 | 63 | 39.1676 | 190500 | 179070 | 7.85 | 7200 | 2042.1229 |  | 3
75 | 85 | 63 | 29.0563 | 190500 | 190500 | 7.85 | 7200 | 2042.1229 |  | 3
75 | 75 | 67 | 66.7494 | 183800 | 102928 | 7.82 | 4800 | 843.9385 |  | 3
75 | 80 | 67 | 51.5724 | 183800 | 128660 | 7.82 | 4800 | 843.9385 |  | 3
75 | 85 | 67 | 39.6049 | 183800 | 152554 | 7.82 | 4800 | 843.9385 |  | 3
75 | 75 | 67 | 66.7494 | 191300 | 112867 | 7.85 | 6000 | 1364.8883 |  | 3
75 | 80 | 67 | 51.5724 | 191300 | 147301 | 7.85 | 6000 | 1364.8883 |  | 3
75 | 85 | 67 | 39.6049 | 191300 | 168344 | 7.85 | 6000 | 1364.8883 |  | 3
75 | 75 | 67 | 66.7494 | 197000 | 122140 | 7.88 | 7200 | 2042.1229 |  | 3
75 | 80 | 67 | 51.5724 | 197000 | 157600 | 7.88 | 7200 | 2042.1229 |  | 3
75 | 85 | 67 | 39.6049 | 197000 | 181240 | 7.88 | 7200 | 2042.1229 |  | 3
75 | 75 | 71 | 82.6659 | 194500 | 81690 | 7.88 | 4800 | 843.9385 |  | 3
75 | 80 | 71 | 65.0618 | 194500 | 105030 | 7.88 | 4800 | 843.9385 |  | 3
75 | 85 | 71 | 51.076 | 194500 | 130315 | 7.88 | 4800 | 843.9385 |  | 3
75 | 75 | 71 | 82.6659 | 196900 | 82698 | 7.99 | 6000 | 1364.8883 |  | 3
75 | 80 | 71 | 65.0618 | 196900 | 118140 | 7.99 | 6000 | 1364.8883 |  | 3
75 | 85 | 71 | 51.076 | 196900 | 143737 | 7.99 | 6000 | 1364.8883 |  | 3
75 | 75 | 71 | 82.6659 | 208500 | 91740 | 7.94 | 7200 | 2042.1229 |  | 3
75 | 80 | 71 | 65.0618 | 208500 | 129270 | 7.94 | 7200 | 2042.1229 |  | 3
75 | 85 | 71 | 51.076 | 208500 | 162630 | 7.94 | 7200 | 2042.1229 |  | 3
85 | 75 | 63 | 52.1129 | 163100 | 120694 | 8.8 | 4800 | 843.9385 |  | 3
85 | 80 | 63 | 39.1676 | 163100 | 141897 | 8.8 | 4800 | 843.9385 |  | 3
85 | 85 | 63 | 29.0563 | 163100 | 156576 | 8.8 | 4800 | 843.9385 |  | 3
85 | 75 | 63 | 52.1129 | 172500 | 138000 | 8.85 | 6000 | 1364.8883 |  | 3
85 | 80 | 63 | 39.1676 | 172500 | 158700 | 8.85 | 6000 | 1364.8883 |  | 3
85 | 85 | 63 | 29.0563 | 172500 | 170775 | 8.85 | 6000 | 1364.8883 |  | 3
85 | 75 | 63 | 52.1129 | 180100 | 149483 | 8.88 | 7200 | 2042.1229 |  | 3
85 | 80 | 63 | 39.1676 | 180100 | 171095 | 8.88 | 7200 | 2042.1229 |  | 3
85 | 85 | 63 | 29.0563 | 180100 | 180100 | 8.88 | 7200 | 2042.1229 |  | 3
85 | 75 | 67 | 66.7494 | 172900 | 98553 | 8.85 | 4800 | 843.9385 |  | 3
85 | 80 | 67 | 51.5724 | 172900 | 122759 | 8.85 | 4800 | 843.9385 |  | 3
85 | 85 | 67 | 39.6049 | 172900 | 145236 | 8.85 | 4800 | 843.9385 |  | 3
85 | 75 | 67 | 66.7494 | 179600 | 107760 | 8.88 | 6000 | 1364.8883 |  | 3
85 | 80 | 67 | 51.5724 | 179600 | 138292 | 8.88 | 6000 | 1364.8883 |  | 3
85 | 85 | 67 | 39.6049 | 179600 | 159844 | 8.88 | 6000 | 1364.8883 |  | 3
85 | 75 | 67 | 66.7494 | 185500 | 116865 | 8.91 | 7200 | 2042.1229 |  | 3
85 | 80 | 67 | 51.5724 | 185500 | 152110 | 8.91 | 7200 | 2042.1229 |  | 3
85 | 85 | 67 | 39.6049 | 185500 | 172515 | 8.91 | 7200 | 2042.1229 |  | 3
85 | 75 | 71 | 82.6659 | 183500 | 73400 | 8.9 | 4800 | 843.9385 |  | 3
85 | 80 | 71 | 65.0618 | 183500 | 99090 | 8.9 | 4800 | 843.9385 |  | 3
85 | 85 | 71 | 51.076 | 183500 | 126615 | 8.9 | 4800 | 843.9385 |  | 3
85 | 75 | 71 | 82.6659 | 191100 | 72618 | 8.94 | 6000 | 1364.8883 |  | 3
85 | 80 | 71 | 65.0618 | 191100 | 112749 | 8.94 | 6000 | 1364.8883 |  | 3
85 | 85 | 71 | 51.076 | 191100 | 143325 | 8.94 | 6000 | 1364.8883 |  | 3
85 | 75 | 71 | 82.6659 | 196200 | 78480 | 8.95 | 7200 | 2042.1229 |  | 3
85 | 80 | 71 | 65.0618 | 196200 | 123606 | 8.95 | 7200 | 2042.1229 |  | 3
85 | 85 | 71 | 51.076 | 196200 | 154998 | 8.95 | 7200 | 2042.1229 |  | 3
95 | 75 | 63 | 52.1129 | 153000 | 116280 | 9.96 | 4800 | 843.9385 |  | 3
95 | 80 | 63 | 39.1676 | 153000 | 133110 | 9.96 | 4800 | 843.9385 |  | 3
95 | 85 | 63 | 29.0563 | 153000 | 148410 | 9.96 | 4800 | 843.9385 |  | 3
95 | 75 | 63 | 52.1129 | 162100 | 131301 | 9.99 | 6000 | 1364.8883 |  | 3
95 | 80 | 63 | 39.1676 | 162100 | 150753 | 9.99 | 6000 | 1364.8883 |  | 3
95 | 85 | 63 | 29.0563 | 162100 | 162100 | 9.99 | 6000 | 1364.8883 |  | 3
95 | 75 | 63 | 52.1129 | 169100 | 143735 | 10.03 | 7200 | 2042.1229 |  | 3
95 | 80 | 63 | 39.1676 | 169100 | 162336 | 10.03 | 7200 | 2042.1229 |  | 3
95 | 85 | 63 | 29.0563 | 169100 | 169100 | 10.03 | 7200 | 2042.1229 |  | 3
95 | 75 | 67 | 66.7494 | 161700 | 90552 | 9.99 | 4800 | 843.9385 |  | 3
95 | 80 | 67 | 51.5724 | 161700 | 118041 | 9.99 | 4800 | 843.9385 |  | 3
95 | 85 | 67 | 39.6049 | 161700 | 137445 | 9.99 | 4800 | 843.9385 |  | 3
95 | 75 | 67 | 66.7494 | 168400 | 101040 | 10.02 | 6000 | 1364.8883 |  | 3
95 | 80 | 67 | 51.5724 | 168400 | 133036 | 10.02 | 6000 | 1364.8883 |  | 3
95 | 85 | 67 | 39.6049 | 168400 | 151560 | 10.02 | 6000 | 1364.8883 |  | 3
95 | 75 | 67 | 66.7494 | 173900 | 111296 | 10.04 | 7200 | 2042.1229 |  | 3
95 | 80 | 67 | 51.5724 | 173900 | 144337 | 10.04 | 7200 | 2042.1229 |  | 3
95 | 85 | 67 | 39.6049 | 173900 | 165205 | 10.04 | 7200 | 2042.1229 |  | 3
95 | 75 | 71 | 82.6659 | 171900 | 65322 | 10.04 | 4800 | 843.9385 |  | 3
95 | 80 | 71 | 65.0618 | 171900 | 94545 | 10.04 | 4800 | 843.9385 |  | 3
95 | 85 | 71 | 51.076 | 171900 | 118611 | 10.04 | 4800 | 843.9385 |  | 3
95 | 75 | 71 | 82.6659 | 179000 | 68020 | 10.07 | 6000 | 1364.8883 |  | 3
95 | 80 | 71 | 65.0618 | 179000 | 103820 | 10.07 | 6000 | 1364.8883 |  | 3
95 | 85 | 71 | 51.076 | 179000 | 136040 | 10.07 | 6000 | 1364.8883 |  | 3
95 | 75 | 71 | 82.6659 | 183700 | 71643 | 10.09 | 7200 | 2042.1229 |  | 3
95 | 80 | 71 | 65.0618 | 183700 | 113894 | 10.09 | 7200 | 2042.1229 |  | 3
95 | 85 | 71 | 51.076 | 183700 | 150634 | 10.09 | 7200 | 2042.1229 |  | 3
85 | 75 | 63 | 52.1129 | 242500 | 177025 | 13.9 | 6400 | 1708.7151 |  | 4
85 | 80 | 63 | 39.1676 | 242500 | 201275 | 13.9 | 6400 | 1708.7151 |  | 4
85 | 85 | 63 | 29.0563 | 242500 | 227950 | 13.9 | 6400 | 1708.7151 |  | 4
85 | 75 | 63 | 52.1129 | 257400 | 195624 | 14.01 | 8000 | 2667.2626 |  | 4
85 | 80 | 63 | 39.1676 | 257400 | 229086 | 14.01 | 8000 | 2667.2626 |  | 4
85 | 85 | 63 | 29.0563 | 257400 | 254826 | 14.01 | 8000 | 2667.2626 |  | 4
85 | 75 | 63 | 52.1129 | 268100 | 214480 | 14.1 | 9600 | 3959.2179 |  | 4
85 | 80 | 63 | 39.1676 | 268100 | 252014 | 14.1 | 9600 | 3959.2179 |  | 4
85 | 85 | 63 | 29.0563 | 268100 | 268100 | 14.1 | 9600 | 3959.2179 |  | 4
85 | 75 | 67 | 66.7494 | 255700 | 143192 | 14.02 | 6400 | 1708.7151 |  | 4
85 | 80 | 67 | 51.5724 | 255700 | 178990 | 14.02 | 6400 | 1708.7151 |  | 4
85 | 85 | 67 | 39.6049 | 255700 | 204560 | 14.02 | 6400 | 1708.7151 |  | 4
85 | 75 | 67 | 66.7494 | 268000 | 163480 | 14.11 | 8000 | 2667.2626 |  | 4
85 | 80 | 67 | 51.5724 | 268000 | 201000 | 14.11 | 8000 | 2667.2626 |  | 4
85 | 85 | 67 | 39.6049 | 268000 | 230480 | 14.11 | 8000 | 2667.2626 |  | 4
85 | 75 | 67 | 66.7494 | 278000 | 175140 | 14.18 | 9600 | 3959.2179 |  | 4
85 | 80 | 67 | 51.5724 | 278000 | 219620 | 14.18 | 9600 | 3959.2179 |  | 4
85 | 85 | 67 | 39.6049 | 278000 | 252980 | 14.18 | 9600 | 3959.2179 |  | 4
85 | 75 | 71 | 82.6659 | 272900 | 114618 | 14.17 | 6400 | 1708.7151 |  | 4
85 | 80 | 71 | 65.0618 | 272900 | 152824 | 14.17 | 6400 | 1708.7151 |  | 4
85 | 85 | 71 | 51.076 | 272900 | 185572 | 14.17 | 6400 | 1708.7151 |  | 4
85 | 75 | 71 | 82.6659 | 286100 | 123023 | 14.26 | 8000 | 2792.2905 |  | 4
85 | 80 | 71 | 65.0618 | 286100 | 168799 | 14.26 | 8000 | 2792.2905 |  | 4
85 | 85 | 71 | 51.076 | 286100 | 208853 | 14.26 | 8000 | 2792.2905 |  | 4
85 | 75 | 71 | 82.6659 | 294900 | 132705 | 14.32 | 9600 | 4105.0838 |  | 4
85 | 80 | 71 | 65.0618 | 294900 | 185787 | 14.32 | 9600 | 4105.0838 |  | 4
85 | 85 | 71 | 51.076 | 294900 | 227073 | 14.32 | 9600 | 4105.0838 |  | 4
95 | 75 | 63 | 52.1129 | 228200 | 168868 | 15.64 | 6400 | 1708.7151 |  | 4
95 | 80 | 63 | 39.1676 | 228200 | 191688 | 15.64 | 6400 | 1708.7151 |  | 4
95 | 85 | 63 | 29.0563 | 228200 | 216790 | 15.64 | 6400 | 1708.7151 |  | 4
95 | 75 | 63 | 52.1129 | 241800 | 188604 | 15.75 | 8000 | 2667.2626 |  | 4
95 | 80 | 63 | 39.1676 | 241800 | 217620 | 15.75 | 8000 | 2667.2626 |  | 4
95 | 85 | 63 | 29.0563 | 241800 | 241800 | 15.75 | 8000 | 2667.2626 |  | 4
95 | 75 | 63 | 52.1129 | 252300 | 206886 | 15.84 | 9600 | 3959.2179 |  | 4
95 | 80 | 63 | 39.1676 | 252300 | 242208 | 15.84 | 9600 | 3959.2179 |  | 4
95 | 85 | 63 | 29.0563 | 252300 | 252300 | 15.84 | 9600 | 3959.2179 |  | 4
95 | 75 | 67 | 66.7494 | 239700 | 136629 | 15.75 | 6400 | 1708.7151 |  | 4
95 | 80 | 67 | 51.5724 | 239700 | 170187 | 15.75 | 6400 | 1708.7151 |  | 4
95 | 85 | 67 | 39.6049 | 239700 | 196554 | 15.75 | 6400 | 1708.7151 |  | 4
95 | 75 | 67 | 66.7494 | 251700 | 153537 | 15.84 | 8000 | 2667.2626 |  | 4
95 | 80 | 67 | 51.5724 | 251700 | 193809 | 15.84 | 8000 | 2667.2626 |  | 4
95 | 85 | 67 | 39.6049 | 251700 | 221496 | 15.84 | 8000 | 2667.2626 |  | 4
95 | 75 | 67 | 66.7494 | 261200 | 167168 | 15.92 | 9600 | 3959.2179 |  | 4
95 | 80 | 67 | 51.5724 | 261200 | 206348 | 15.92 | 9600 | 3959.2179 |  | 4
95 | 85 | 67 | 39.6049 | 261200 | 242916 | 15.92 | 9600 | 3959.2179 |  | 4
95 | 75 | 71 | 82.6659 | 256700 | 105247 | 15.9 | 6400 | 1708.7151 |  | 4
95 | 80 | 71 | 65.0618 | 256700 | 143752 | 15.9 | 6400 | 1708.7151 |  | 4
95 | 85 | 71 | 51.076 | 256700 | 177123 | 15.9 | 6400 | 1708.7151 |  | 4
95 | 75 | 71 | 82.6659 | 268600 | 112812 | 16 | 8000 | 2667.2626 |  | 4
95 | 80 | 71 | 65.0618 | 268600 | 161160 | 16 | 8000 | 2667.2626 |  | 4
95 | 85 | 71 | 51.076 | 268600 | 198764 | 16 | 8000 | 2667.2626 |  | 4
95 | 75 | 71 | 82.6659 | 276600 | 121704 | 16.06 | 9600 | 3959.2179 |  | 4
95 | 80 | 71 | 65.0618 | 276600 | 174258 | 16.06 | 9600 | 3959.2179 |  | 4
95 | 85 | 71 | 51.076 | 276600 | 215748 | 16.06 | 9600 | 3959.2179 |  | 4
105 | 75 | 63 | 52.1129 | 213200 | 157768 | 17.55 | 6400 | 1708.7151 |  | 4
105 | 80 | 63 | 39.1676 | 213200 | 183352 | 17.55 | 6400 | 1708.7151 |  | 4
105 | 85 | 63 | 29.0563 | 213200 | 206804 | 17.55 | 6400 | 1708.7151 |  | 4
105 | 75 | 63 | 52.1129 | 225600 | 175968 | 17.67 | 8000 | 2667.2626 |  | 4
105 | 80 | 63 | 39.1676 | 225600 | 207552 | 17.67 | 8000 | 2667.2626 |  | 4
105 | 85 | 63 | 29.0563 | 225600 | 225600 | 17.67 | 8000 | 2667.2626 |  | 4
105 | 75 | 63 | 52.1129 | 235900 | 198156 | 17.76 | 9600 | 3959.2179 |  | 4
105 | 80 | 63 | 39.1676 | 235900 | 231182 | 17.76 | 9600 | 3959.2179 |  | 4
105 | 85 | 63 | 29.0563 | 235900 | 235900 | 17.76 | 9600 | 3959.2179 |  | 4
105 | 75 | 67 | 66.7494 | 223200 | 127224 | 17.66 | 6400 | 1708.7151 |  | 4
105 | 80 | 67 | 51.5724 | 223200 | 160704 | 17.66 | 6400 | 1708.7151 |  | 4
105 | 85 | 67 | 39.6049 | 223200 | 185256 | 17.66 | 6400 | 1708.7151 |  | 4
105 | 75 | 67 | 66.7494 | 234800 | 145576 | 17.76 | 8000 | 2667.2626 |  | 4
105 | 80 | 67 | 51.5724 | 234800 | 180796 | 17.76 | 8000 | 2667.2626 |  | 4
105 | 85 | 67 | 39.6049 | 234800 | 211320 | 17.76 | 8000 | 2667.2626 |  | 4
105 | 75 | 67 | 66.7494 | 243700 | 155968 | 17.84 | 9600 | 3959.2179 |  | 4
105 | 80 | 67 | 51.5724 | 243700 | 197397 | 17.84 | 9600 | 3959.2179 |  | 4
105 | 85 | 67 | 39.6049 | 243700 | 231515 | 17.84 | 9600 | 3959.2179 |  | 4
105 | 75 | 71 | 82.6659 | 239600 | 95840 | 17.83 | 6400 | 1708.7151 |  | 4
105 | 80 | 71 | 65.0618 | 239600 | 131780 | 17.83 | 6400 | 1708.7151 |  | 4
105 | 85 | 71 | 51.076 | 239600 | 167720 | 17.83 | 6400 | 1708.7151 |  | 4
105 | 75 | 71 | 82.6659 | 251100 | 105462 | 17.93 | 8000 | 2667.2626 |  | 4
105 | 80 | 71 | 65.0618 | 251100 | 148149 | 17.93 | 8000 | 2667.2626 |  | 4
105 | 85 | 71 | 51.076 | 251100 | 185814 | 17.93 | 8000 | 2667.2626 |  | 4
105 | 75 | 71 | 82.6659 | 258100 | 116145 | 17.99 | 9600 | 3959.2179 |  | 4
105 | 80 | 71 | 65.0618 | 258100 | 165184 | 17.99 | 9600 | 3959.2179 |  | 4
105 | 85 | 71 | 51.076 | 258100 | 206480 | 17.99 | 9600 | 3959.2179 |  | 4
115 | 75 | 63 | 52.1129 | 197400 | 150024 | 19.66 | 6400 | 1604.5251 |  | 4
115 | 80 | 63 | 39.1676 | 197400 | 173712 | 19.66 | 6400 | 1604.5251 |  | 4
115 | 85 | 63 | 29.0563 | 197400 | 195426 | 19.66 | 6400 | 1604.5251 |  | 4
115 | 75 | 63 | 52.1129 | 209100 | 167280 | 19.78 | 8000 | 2531.8156 |  | 4
115 | 80 | 63 | 39.1676 | 209100 | 198645 | 19.78 | 8000 | 2531.8156 |  | 4
115 | 85 | 63 | 29.0563 | 209100 | 209100 | 19.78 | 8000 | 2531.8156 |  | 4
115 | 75 | 63 | 52.1129 | 219200 | 186320 | 19.88 | 9600 | 3959.2179 |  | 4
115 | 80 | 63 | 39.1676 | 219200 | 217008 | 19.88 | 9600 | 3959.2179 |  | 4
115 | 85 | 63 | 29.0563 | 219200 | 219200 | 19.88 | 9600 | 3959.2179 |  | 4
115 | 75 | 67 | 66.7494 | 206200 | 117534 | 19.77 | 6400 | 1604.5251 |  | 4
115 | 80 | 67 | 51.5724 | 206200 | 152588 | 19.77 | 6400 | 1604.5251 |  | 4
115 | 85 | 67 | 39.6049 | 206200 | 175270 | 19.77 | 6400 | 1604.5251 |  | 4
115 | 75 | 67 | 66.7494 | 217300 | 134726 | 19.88 | 8000 | 2667.2626 |  | 4
115 | 80 | 67 | 51.5724 | 217300 | 169494 | 19.88 | 8000 | 2667.2626 |  | 4
115 | 85 | 67 | 39.6049 | 217300 | 199916 | 19.88 | 8000 | 2667.2626 |  | 4
115 | 75 | 67 | 66.7494 | 225900 | 149094 | 19.96 | 9600 | 3959.2179 |  | 4
115 | 80 | 67 | 51.5724 | 225900 | 187497 | 19.96 | 9600 | 3959.2179 |  | 4
115 | 85 | 67 | 39.6049 | 225900 | 221382 | 19.96 | 9600 | 3959.2179 |  | 4
115 | 75 | 71 | 82.6659 | 221800 | 88720 | 19.94 | 6400 | 1708.7151 |  | 4
115 | 80 | 71 | 65.0618 | 221800 | 124208 | 19.94 | 6400 | 1708.7151 |  | 4
115 | 85 | 71 | 51.076 | 221800 | 157478 | 19.94 | 6400 | 1708.7151 |  | 4
115 | 75 | 71 | 82.6659 | 231900 | 99717 | 20.04 | 8000 | 2667.2626 |  | 4
115 | 80 | 71 | 65.0618 | 231900 | 139140 | 20.04 | 8000 | 2667.2626 |  | 4
115 | 85 | 71 | 51.076 | 231900 | 176244 | 20.04 | 8000 | 2667.2626 |  | 4
115 | 75 | 71 | 82.6659 | 237800 | 111766 | 20.1 | 9600 | 3959.2179 |  | 4
115 | 80 | 71 | 65.0618 | 237800 | 156948 | 20.1 | 9600 | 3959.2179 |  | 4
115 | 85 | 71 | 51.076 | 237800 | 192618 | 20.1 | 9600 | 3959.2179 |  | 4
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 6
Degradation Coefficient (C_d)
IEER or SEER | 16.5
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 75 | 63 | 52.1129 | 57900 | 46320 | 1.84 | 2000 | 250.0559 |  | 1
65 | 80 | 63 | 39.1676 | 57900 | 54426 | 1.84 | 2000 | 250.0559 |  | 1
65 | 85 | 63 | 29.0563 | 57900 | 57321 | 1.84 | 2000 | 250.0559 |  | 1
65 | 75 | 63 | 52.1129 | 60700 | 52202 | 1.83 | 2500 | 250.0559 |  | 1
65 | 80 | 63 | 39.1676 | 60700 | 58272 | 1.83 | 2500 | 250.0559 |  | 1
65 | 85 | 63 | 29.0563 | 60700 | 60700 | 1.83 | 2500 | 250.0559 |  | 1
65 | 75 | 63 | 52.1129 | 63100 | 55528 | 1.82 | 3000 | 291.7318 |  | 1
65 | 80 | 63 | 39.1676 | 63100 | 61838 | 1.82 | 3000 | 291.7318 |  | 1
65 | 85 | 63 | 29.0563 | 63100 | 63100 | 1.82 | 3000 | 291.7318 |  | 1
65 | 75 | 67 | 66.7494 | 60900 | 31059 | 1.83 | 2000 | 250.0559 |  | 1
65 | 80 | 67 | 51.5724 | 60900 | 45675 | 1.83 | 2000 | 250.0559 |  | 1
65 | 85 | 67 | 39.6049 | 60900 | 55419 | 1.83 | 2000 | 250.0559 |  | 1
65 | 75 | 67 | 66.7494 | 63800 | 34452 | 1.81 | 2500 | 250.0559 |  | 1
65 | 80 | 67 | 51.5724 | 63800 | 51678 | 1.81 | 2500 | 250.0559 |  | 1
65 | 85 | 67 | 39.6049 | 63800 | 59972 | 1.81 | 2500 | 250.0559 |  | 1
65 | 75 | 67 | 66.7494 | 66000 | 37620 | 1.8 | 3000 | 291.7318 |  | 1
65 | 80 | 67 | 51.5724 | 66000 | 56760 | 1.8 | 3000 | 291.7318 |  | 1
65 | 85 | 67 | 39.6049 | 66000 | 64020 | 1.8 | 3000 | 291.7318 |  | 1
65 | 75 | 71 | 82.6659 | 64200 | 14766 | 1.82 | 2000 | 250.0559 |  | 1
65 | 80 | 71 | 65.0618 | 64200 | 30174 | 1.82 | 2000 | 250.0559 |  | 1
65 | 85 | 71 | 51.076 | 64200 | 44940 | 1.82 | 2000 | 250.0559 |  | 1
65 | 75 | 71 | 82.6659 | 67100 | 15433 | 1.8 | 2500 | 250.0559 |  | 1
65 | 80 | 71 | 65.0618 | 67100 | 34221 | 1.8 | 2500 | 250.0559 |  | 1
65 | 85 | 71 | 51.076 | 67100 | 50996 | 1.8 | 2500 | 250.0559 |  | 1
65 | 75 | 71 | 82.6659 | 69200 | 15916 | 1.79 | 3000 | 291.7318 |  | 1
65 | 80 | 71 | 65.0618 | 69200 | 37368 | 1.79 | 3000 | 291.7318 |  | 1
65 | 85 | 71 | 51.076 | 69200 | 56744 | 1.79 | 3000 | 291.7318 |  | 1
75 | 75 | 63 | 52.1129 | 55300 | 44793 | 2.07 | 2000 | 250.0559 |  | 1
75 | 80 | 63 | 39.1676 | 55300 | 51982 | 2.07 | 2000 | 250.0559 |  | 1
75 | 85 | 63 | 29.0563 | 55300 | 55300 | 2.07 | 2000 | 250.0559 |  | 1
75 | 75 | 63 | 52.1129 | 58000 | 49880 | 2.07 | 2500 | 250.0559 |  | 1
75 | 80 | 63 | 39.1676 | 58000 | 56260 | 2.07 | 2500 | 250.0559 |  | 1
75 | 85 | 63 | 29.0563 | 58000 | 58000 | 2.07 | 2500 | 250.0559 |  | 1
75 | 75 | 63 | 52.1129 | 60400 | 53756 | 2.06 | 3000 | 291.7318 |  | 1
75 | 80 | 63 | 39.1676 | 60400 | 59796 | 2.06 | 3000 | 291.7318 |  | 1
75 | 85 | 63 | 29.0563 | 60400 | 60400 | 2.06 | 3000 | 291.7318 |  | 1
75 | 75 | 67 | 66.7494 | 58300 | 29733 | 2.07 | 2000 | 250.0559 |  | 1
75 | 80 | 67 | 51.5724 | 58300 | 44308 | 2.07 | 2000 | 250.0559 |  | 1
75 | 85 | 67 | 39.6049 | 58300 | 53636 | 2.07 | 2000 | 250.0559 |  | 1
75 | 75 | 67 | 66.7494 | 60900 | 32886 | 2.06 | 2500 | 250.0559 |  | 1
75 | 80 | 67 | 51.5724 | 60900 | 49938 | 2.06 | 2500 | 250.0559 |  | 1
75 | 85 | 67 | 39.6049 | 60900 | 57855 | 2.06 | 2500 | 250.0559 |  | 1
75 | 75 | 67 | 66.7494 | 63000 | 36540 | 2.06 | 3000 | 291.7318 |  | 1
75 | 80 | 67 | 51.5724 | 63000 | 54810 | 2.06 | 3000 | 291.7318 |  | 1
75 | 85 | 67 | 39.6049 | 63000 | 61110 | 2.06 | 3000 | 291.7318 |  | 1
75 | 75 | 71 | 82.6659 | 61400 | 12894 | 2.06 | 2000 | 250.0559 |  | 1
75 | 80 | 71 | 65.0618 | 61400 | 28858 | 2.06 | 2000 | 250.0559 |  | 1
75 | 85 | 71 | 51.076 | 61400 | 42980 | 2.06 | 2000 | 250.0559 |  | 1
75 | 75 | 71 | 82.6659 | 64200 | 13482 | 2.05 | 2500 | 250.0559 |  | 1
75 | 80 | 71 | 65.0618 | 64200 | 32100 | 2.05 | 2500 | 250.0559 |  | 1
75 | 85 | 71 | 51.076 | 64200 | 49434 | 2.05 | 2500 | 250.0559 |  | 1
75 | 75 | 71 | 82.6659 | 66100 | 14542 | 2.05 | 3000 | 291.7318 |  | 1
75 | 80 | 71 | 65.0618 | 66100 | 35694 | 2.05 | 3000 | 291.7318 |  | 1
75 | 85 | 71 | 51.076 | 66100 | 54863 | 2.05 | 3000 | 291.7318 |  | 1
85 | 75 | 63 | 52.1129 | 52300 | 42886 | 2.39 | 2000 | 250.0559 |  | 1
85 | 80 | 63 | 39.1676 | 52300 | 49685 | 2.39 | 2000 | 250.0559 |  | 1
85 | 85 | 63 | 29.0563 | 52300 | 52300 | 2.39 | 2000 | 250.0559 |  | 1
85 | 75 | 63 | 52.1129 | 54900 | 47763 | 2.39 | 2500 | 250.0559 |  | 1
85 | 80 | 63 | 39.1676 | 54900 | 53802 | 2.39 | 2500 | 250.0559 |  | 1
85 | 85 | 63 | 29.0563 | 54900 | 54900 | 2.39 | 2500 | 250.0559 |  | 1
85 | 75 | 63 | 52.1129 | 57200 | 51480 | 2.39 | 3000 | 291.7318 |  | 1
85 | 80 | 63 | 39.1676 | 57200 | 56628 | 2.39 | 3000 | 291.7318 |  | 1
85 | 85 | 63 | 29.0563 | 57200 | 57200 | 2.39 | 3000 | 291.7318 |  | 1
85 | 75 | 67 | 66.7494 | 55200 | 27600 | 2.39 | 2000 | 250.0559 |  | 1
85 | 80 | 67 | 51.5724 | 55200 | 42504 | 2.39 | 2000 | 250.0559 |  | 1
85 | 85 | 67 | 39.6049 | 55200 | 51336 | 2.39 | 2000 | 250.0559 |  | 1
85 | 75 | 67 | 66.7494 | 57700 | 31158 | 2.39 | 2500 | 250.0559 |  | 1
85 | 80 | 67 | 51.5724 | 57700 | 48468 | 2.39 | 2500 | 250.0559 |  | 1
85 | 85 | 67 | 39.6049 | 57700 | 55392 | 2.39 | 2500 | 250.0559 |  | 1
85 | 75 | 67 | 66.7494 | 59500 | 34510 | 2.39 | 3000 | 291.7318 |  | 1
85 | 80 | 67 | 51.5724 | 59500 | 51765 | 2.39 | 3000 | 291.7318 |  | 1
85 | 85 | 67 | 39.6049 | 59500 | 58310 | 2.39 | 3000 | 291.7318 |  | 1
85 | 75 | 71 | 82.6659 | 58200 | 11058 | 2.39 | 2000 | 250.0559 |  | 1
85 | 80 | 71 | 65.0618 | 58200 | 26772 | 2.39 | 2000 | 250.0559 |  | 1
85 | 85 | 71 | 51.076 | 58200 | 41322 | 2.39 | 2000 | 250.0559 |  | 1
85 | 75 | 71 | 82.6659 | 60700 | 12140 | 2.39 | 2500 | 250.0559 |  | 1
85 | 80 | 71 | 65.0618 | 60700 | 30350 | 2.39 | 2500 | 250.0559 |  | 1
85 | 85 | 71 | 51.076 | 60700 | 47953 | 2.39 | 2500 | 250.0559 |  | 1
85 | 75 | 71 | 82.6659 | 62600 | 13146 | 2.39 | 3000 | 291.7318 |  | 1
85 | 80 | 71 | 65.0618 | 62600 | 34430 | 2.39 | 3000 | 291.7318 |  | 1
85 | 85 | 71 | 51.076 | 62600 | 53210 | 2.39 | 3000 | 291.7318 |  | 1
95 | 75 | 63 | 52.1129 | 48900 | 40587 | 2.76 | 2000 | 250.0559 |  | 1
95 | 80 | 63 | 39.1676 | 48900 | 46944 | 2.76 | 2000 | 250.0559 |  | 1
95 | 85 | 63 | 29.0563 | 48900 | 48900 | 2.76 | 2000 | 250.0559 |  | 1
95 | 75 | 63 | 52.1129 | 51600 | 45408 | 2.77 | 2500 | 250.0559 |  | 1
95 | 80 | 63 | 39.1676 | 51600 | 50568 | 2.77 | 2500 | 250.0559 |  | 1
95 | 85 | 63 | 29.0563 | 51600 | 51600 | 2.77 | 2500 | 250.0559 |  | 1
95 | 75 | 63 | 52.1129 | 53800 | 48420 | 2.77 | 3000 | 291.7318 |  | 1
95 | 80 | 63 | 39.1676 | 53800 | 53800 | 2.77 | 3000 | 291.7318 |  | 1
95 | 85 | 63 | 29.0563 | 53800 | 53800 | 2.77 | 3000 | 291.7318 |  | 1
95 | 75 | 67 | 66.7494 | 51700 | 25850 | 2.77 | 2000 | 250.0559 |  | 1
95 | 80 | 67 | 51.5724 | 51700 | 40326 | 2.77 | 2000 | 250.0559 |  | 1
95 | 85 | 67 | 39.6049 | 51700 | 48598 | 2.77 | 2000 | 250.0559 |  | 1
95 | 75 | 67 | 66.7494 | 54000 | 29160 | 2.77 | 2500 | 250.0559 |  | 1
95 | 80 | 67 | 51.5724 | 54000 | 45900 | 2.77 | 2500 | 250.0559 |  | 1
95 | 85 | 67 | 39.6049 | 54000 | 52380 | 2.77 | 2500 | 250.0559 |  | 1
95 | 75 | 67 | 66.7494 | 55600 | 32248 | 2.77 | 3000 | 291.7318 |  | 1
95 | 80 | 67 | 51.5724 | 55600 | 48928 | 2.77 | 3000 | 291.7318 |  | 1
95 | 85 | 67 | 39.6049 | 55600 | 55044 | 2.77 | 3000 | 291.7318 |  | 1
95 | 75 | 71 | 82.6659 | 54700 | 9846 | 2.77 | 2000 | 250.0559 |  | 1
95 | 80 | 71 | 65.0618 | 54700 | 25162 | 2.77 | 2000 | 250.0559 |  | 1
95 | 85 | 71 | 51.076 | 54700 | 39931 | 2.77 | 2000 | 250.0559 |  | 1
95 | 75 | 71 | 82.6659 | 57000 | 10260 | 2.77 | 2500 | 250.0559 |  | 1
95 | 80 | 71 | 65.0618 | 57000 | 29070 | 2.77 | 2500 | 250.0559 |  | 1
95 | 85 | 71 | 51.076 | 57000 | 45600 | 2.77 | 2500 | 250.0559 |  | 1
95 | 75 | 71 | 82.6659 | 58700 | 11153 | 2.77 | 3000 | 291.7318 |  | 1
95 | 80 | 71 | 65.0618 | 58700 | 32285 | 2.77 | 3000 | 291.7318 |  | 1
95 | 85 | 71 | 51.076 | 58700 | 50482 | 2.77 | 3000 | 291.7318 |  | 1
65 | 75 | 63 | 52.1129 | 131300 | 95849 | 5.21 | 4000 | 583.4637 |  | 2
65 | 80 | 63 | 39.1676 | 131300 | 112918 | 5.21 | 4000 | 583.4637 |  | 2
65 | 85 | 63 | 29.0563 | 131300 | 128674 | 5.21 | 4000 | 583.4637 |  | 2
65 | 75 | 63 | 52.1129 | 138400 | 106568 | 5.21 | 5000 | 948.1285 |  | 2
65 | 80 | 63 | 39.1676 | 138400 | 127328 | 5.21 | 5000 | 948.1285 |  | 2
65 | 85 | 63 | 29.0563 | 138400 | 138400 | 5.21 | 5000 | 948.1285 |  | 2
65 | 75 | 63 | 52.1129 | 144600 | 117126 | 5.22 | 6000 | 1364.8883 |  | 2
65 | 80 | 63 | 39.1676 | 144600 | 138816 | 5.22 | 6000 | 1364.8883 |  | 2
65 | 85 | 63 | 29.0563 | 144600 | 144600 | 5.22 | 6000 | 1364.8883 |  | 2
65 | 75 | 67 | 66.7494 | 139400 | 80852 | 5.21 | 4000 | 645.9777 |  | 2
65 | 80 | 67 | 51.5724 | 139400 | 98974 | 5.21 | 4000 | 645.9777 |  | 2
65 | 85 | 67 | 39.6049 | 139400 | 115702 | 5.21 | 4000 | 645.9777 |  | 2
65 | 75 | 67 | 66.7494 | 146100 | 87660 | 5.22 | 5000 | 948.1285 |  | 2
65 | 80 | 67 | 51.5724 | 146100 | 109575 | 5.22 | 5000 | 948.1285 |  | 2
65 | 85 | 67 | 39.6049 | 146100 | 130029 | 5.22 | 5000 | 948.1285 |  | 2
65 | 75 | 67 | 66.7494 | 151100 | 93682 | 5.24 | 6000 | 1364.8883 |  | 2
65 | 80 | 67 | 51.5724 | 151100 | 119369 | 5.24 | 6000 | 1364.8883 |  | 2
65 | 85 | 67 | 39.6049 | 151100 | 142034 | 5.24 | 6000 | 1364.8883 |  | 2
65 | 75 | 71 | 82.6659 | 147200 | 63296 | 5.21 | 4000 | 645.9777 |  | 2
65 | 80 | 71 | 65.0618 | 147200 | 82432 | 5.21 | 4000 | 645.9777 |  | 2
65 | 85 | 71 | 51.076 | 147200 | 101568 | 5.21 | 4000 | 645.9777 |  | 2
65 | 75 | 71 | 82.6659 | 154200 | 69390 | 5.23 | 5000 | 948.1285 |  | 2
65 | 80 | 71 | 65.0618 | 154200 | 92520 | 5.23 | 5000 | 948.1285 |  | 2
65 | 85 | 71 | 51.076 | 154200 | 112566 | 5.23 | 5000 | 948.1285 |  | 2
65 | 75 | 71 | 82.6659 | 159600 | 68628 | 5.24 | 6000 | 1364.8883 |  | 2
65 | 80 | 71 | 65.0618 | 159600 | 98952 | 5.24 | 6000 | 1364.8883 |  | 2
65 | 85 | 71 | 51.076 | 159600 | 122892 | 5.24 | 6000 | 1364.8883 |  | 2
75 | 75 | 63 | 52.1129 | 125200 | 91396 | 5.83 | 4000 | 583.4637 |  | 2
75 | 80 | 63 | 39.1676 | 125200 | 108924 | 5.83 | 4000 | 583.4637 |  | 2
75 | 85 | 63 | 29.0563 | 125200 | 123948 | 5.83 | 4000 | 583.4637 |  | 2
75 | 75 | 63 | 52.1129 | 132200 | 103116 | 5.86 | 5000 | 854.3575 |  | 2
75 | 80 | 63 | 39.1676 | 132200 | 122946 | 5.86 | 5000 | 854.3575 |  | 2
75 | 85 | 63 | 29.0563 | 132200 | 132200 | 5.86 | 5000 | 854.3575 |  | 2
75 | 75 | 63 | 52.1129 | 138000 | 113160 | 5.88 | 6000 | 1364.8883 |  | 2
75 | 80 | 63 | 39.1676 | 138000 | 133860 | 5.88 | 6000 | 1364.8883 |  | 2
75 | 85 | 63 | 29.0563 | 138000 | 138000 | 5.88 | 6000 | 1364.8883 |  | 2
75 | 75 | 67 | 66.7494 | 132800 | 77024 | 5.86 | 4000 | 583.4637 |  | 2
75 | 80 | 67 | 51.5724 | 132800 | 94288 | 5.86 | 4000 | 583.4637 |  | 2
75 | 85 | 67 | 39.6049 | 132800 | 111552 | 5.86 | 4000 | 583.4637 |  | 2
75 | 75 | 67 | 66.7494 | 139300 | 84973 | 5.88 | 5000 | 948.1285 |  | 2
75 | 80 | 67 | 51.5724 | 139300 | 105868 | 5.88 | 5000 | 948.1285 |  | 2
75 | 85 | 67 | 39.6049 | 139300 | 125370 | 5.88 | 5000 | 948.1285 |  | 2
75 | 75 | 67 | 66.7494 | 143700 | 89094 | 5.9 | 6000 | 1364.8883 |  | 2
75 | 80 | 67 | 51.5724 | 143700 | 114960 | 5.9 | 6000 | 1364.8883 |  | 2
75 | 85 | 67 | 39.6049 | 143700 | 136515 | 5.9 | 6000 | 1364.8883 |  | 2
75 | 75 | 71 | 82.6659 | 140100 | 60243 | 5.87 | 4000 | 645.9777 |  | 2
75 | 80 | 71 | 65.0618 | 140100 | 79857 | 5.87 | 4000 | 645.9777 |  | 2
75 | 85 | 71 | 51.076 | 140100 | 96669 | 5.87 | 4000 | 645.9777 |  | 2
75 | 75 | 71 | 82.6659 | 146900 | 61698 | 5.9 | 5000 | 948.1285 |  | 2
75 | 80 | 71 | 65.0618 | 146900 | 88140 | 5.9 | 5000 | 948.1285 |  | 2
75 | 85 | 71 | 51.076 | 146900 | 108706 | 5.9 | 5000 | 948.1285 |  | 2
75 | 75 | 71 | 82.6659 | 151700 | 65231 | 5.91 | 6000 | 1364.8883 |  | 2
75 | 80 | 71 | 65.0618 | 151700 | 92537 | 5.91 | 6000 | 1364.8883 |  | 2
75 | 85 | 71 | 51.076 | 151700 | 118326 | 5.91 | 6000 | 1364.8883 |  | 2
85 | 75 | 63 | 52.1129 | 118600 | 87764 | 6.61 | 4000 | 583.4637 |  | 2
85 | 80 | 63 | 39.1676 | 118600 | 104368 | 6.61 | 4000 | 583.4637 |  | 2
85 | 85 | 63 | 29.0563 | 118600 | 118600 | 6.61 | 4000 | 583.4637 |  | 2
85 | 75 | 63 | 52.1129 | 125200 | 98908 | 6.64 | 5000 | 854.3575 |  | 2
85 | 80 | 63 | 39.1676 | 125200 | 118940 | 6.64 | 5000 | 854.3575 |  | 2
85 | 85 | 63 | 29.0563 | 125200 | 125200 | 6.64 | 5000 | 854.3575 |  | 2
85 | 75 | 63 | 52.1129 | 131000 | 108730 | 6.67 | 6000 | 1271.1173 |  | 2
85 | 80 | 63 | 39.1676 | 131000 | 128380 | 6.67 | 6000 | 1271.1173 |  | 2
85 | 85 | 63 | 29.0563 | 131000 | 131000 | 6.67 | 6000 | 1271.1173 |  | 2
85 | 75 | 67 | 66.7494 | 125600 | 72848 | 6.64 | 4000 | 583.4637 |  | 2
85 | 80 | 67 | 51.5724 | 125600 | 90432 | 6.64 | 4000 | 583.4637 |  | 2
85 | 85 | 67 | 39.6049 | 125600 | 106760 | 6.64 | 4000 | 583.4637 |  | 2
85 | 75 | 67 | 66.7494 | 131600 | 80276 | 6.68 | 5000 | 854.3575 |  | 2
85 | 80 | 67 | 51.5724 | 131600 | 101332 | 6.68 | 5000 | 854.3575 |  | 2
85 | 85 | 67 | 39.6049 | 131600 | 121072 | 6.68 | 5000 | 854.3575 |  | 2
85 | 75 | 67 | 66.7494 | 135400 | 83948 | 6.69 | 6000 | 1364.8883 |  | 2
85 | 80 | 67 | 51.5724 | 135400 | 109674 | 6.69 | 6000 | 1364.8883 |  | 2
85 | 85 | 67 | 39.6049 | 135400 | 131338 | 6.69 | 6000 | 1364.8883 |  | 2
85 | 75 | 71 | 82.6659 | 132700 | 57061 | 6.67 | 4000 | 583.4637 |  | 2
85 | 80 | 71 | 65.0618 | 132700 | 75639 | 6.67 | 4000 | 583.4637 |  | 2
85 | 85 | 71 | 51.076 | 132700 | 92890 | 6.67 | 4000 | 583.4637 |  | 2
85 | 75 | 71 | 82.6659 | 139100 | 59813 | 6.71 | 5000 | 948.1285 |  | 2
85 | 80 | 71 | 65.0618 | 139100 | 83460 | 6.71 | 5000 | 948.1285 |  | 2
85 | 85 | 71 | 51.076 | 139100 | 104325 | 6.71 | 5000 | 948.1285 |  | 2
85 | 75 | 71 | 82.6659 | 143700 | 61791 | 6.72 | 6000 | 1364.8883 |  | 2
85 | 80 | 71 | 65.0618 | 143700 | 87657 | 6.72 | 6000 | 1364.8883 |  | 2
85 | 85 | 71 | 51.076 | 143700 | 114960 | 6.72 | 6000 | 1364.8883 |  | 2
95 | 75 | 63 | 52.1129 | 111100 | 83325 | 7.51 | 4000 | 583.4637 |  | 2
95 | 80 | 63 | 39.1676 | 111100 | 99990 | 7.51 | 4000 | 583.4637 |  | 2
95 | 85 | 63 | 29.0563 | 111100 | 111100 | 7.51 | 4000 | 583.4637 |  | 2
95 | 75 | 63 | 52.1129 | 117800 | 94240 | 7.56 | 5000 | 854.3575 |  | 2
95 | 80 | 63 | 39.1676 | 117800 | 113088 | 7.56 | 5000 | 854.3575 |  | 2
95 | 85 | 63 | 29.0563 | 117800 | 117800 | 7.56 | 5000 | 854.3575 |  | 2
95 | 75 | 63 | 52.1129 | 123400 | 104890 | 7.59 | 6000 | 1271.1173 |  | 2
95 | 80 | 63 | 39.1676 | 123400 | 122166 | 7.59 | 6000 | 1271.1173 |  | 2
95 | 85 | 63 | 29.0563 | 123400 | 123400 | 7.59 | 6000 | 1271.1173 |  | 2
95 | 75 | 67 | 66.7494 | 117900 | 68382 | 7.55 | 4000 | 583.4637 |  | 2
95 | 80 | 67 | 51.5724 | 117900 | 86067 | 7.55 | 4000 | 583.4637 |  | 2
95 | 85 | 67 | 39.6049 | 117900 | 102573 | 7.55 | 4000 | 583.4637 |  | 2
95 | 75 | 67 | 66.7494 | 123200 | 73920 | 7.58 | 5000 | 854.3575 |  | 2
95 | 80 | 67 | 51.5724 | 123200 | 96096 | 7.58 | 5000 | 854.3575 |  | 2
95 | 85 | 67 | 39.6049 | 123200 | 115808 | 7.58 | 5000 | 854.3575 |  | 2
95 | 75 | 67 | 66.7494 | 127400 | 80262 | 7.62 | 6000 | 1271.1173 |  | 2
95 | 80 | 67 | 51.5724 | 127400 | 105742 | 7.62 | 6000 | 1271.1173 |  | 2
95 | 85 | 67 | 39.6049 | 127400 | 124852 | 7.62 | 6000 | 1271.1173 |  | 2
95 | 75 | 71 | 82.6659 | 124700 | 51127 | 7.59 | 4000 | 583.4637 |  | 2
95 | 80 | 71 | 65.0618 | 124700 | 71079 | 7.59 | 4000 | 583.4637 |  | 2
95 | 85 | 71 | 51.076 | 124700 | 88537 | 7.59 | 4000 | 583.4637 |  | 2
95 | 75 | 71 | 82.6659 | 130800 | 52320 | 7.63 | 5000 | 854.3575 |  | 2
95 | 80 | 71 | 65.0618 | 130800 | 77172 | 7.63 | 5000 | 854.3575 |  | 2
95 | 85 | 71 | 51.076 | 130800 | 99408 | 7.63 | 5000 | 854.3575 |  | 2
95 | 75 | 71 | 82.6659 | 134800 | 57964 | 7.65 | 6000 | 1364.8883 |  | 2
95 | 80 | 71 | 65.0618 | 134800 | 86272 | 7.65 | 6000 | 1364.8883 |  | 2
95 | 85 | 71 | 51.076 | 134800 | 109188 | 7.65 | 6000 | 1364.8883 |  | 2
65 | 75 | 63 | 52.1129 | 218900 | 153230 | 9.6 | 5600 | 1208.6034 |  | 3
65 | 80 | 63 | 39.1676 | 218900 | 179498 | 9.6 | 5600 | 1208.6034 |  | 3
65 | 85 | 63 | 29.0563 | 218900 | 203577 | 9.6 | 5600 | 1208.6034 |  | 3
65 | 75 | 63 | 52.1129 | 230500 | 168265 | 9.64 | 7000 | 1958.771 |  | 3
65 | 80 | 63 | 39.1676 | 230500 | 200535 | 9.64 | 7000 | 1958.771 |  | 3
65 | 85 | 63 | 29.0563 | 230500 | 225890 | 9.64 | 7000 | 1958.771 |  | 3
65 | 75 | 63 | 52.1129 | 239000 | 184030 | 9.67 | 8400 | 3042.3464 |  | 3
65 | 80 | 63 | 39.1676 | 239000 | 224660 | 9.67 | 8400 | 3042.3464 |  | 3
65 | 85 | 63 | 29.0563 | 239000 | 239000 | 9.67 | 8400 | 3042.3464 |  | 3
65 | 75 | 67 | 66.7494 | 231900 | 127545 | 9.65 | 5600 | 1208.6034 |  | 3
65 | 80 | 67 | 51.5724 | 231900 | 155373 | 9.65 | 5600 | 1208.6034 |  | 3
65 | 85 | 67 | 39.6049 | 231900 | 180882 | 9.65 | 5600 | 1208.6034 |  | 3
65 | 75 | 67 | 66.7494 | 243200 | 138624 | 9.7 | 7000 | 1958.771 |  | 3
65 | 80 | 67 | 51.5724 | 243200 | 172672 | 9.7 | 7000 | 1958.771 |  | 3
65 | 85 | 67 | 39.6049 | 243200 | 206720 | 9.7 | 7000 | 1958.771 |  | 3
65 | 75 | 67 | 66.7494 | 251400 | 145812 | 9.72 | 8400 | 3042.3464 |  | 3
65 | 80 | 67 | 51.5724 | 251400 | 188550 | 9.72 | 8400 | 3042.3464 |  | 3
65 | 85 | 67 | 39.6049 | 251400 | 226260 | 9.72 | 8400 | 3042.3464 |  | 3
65 | 75 | 71 | 82.6659 | 246500 | 101065 | 9.72 | 5600 | 1208.6034 |  | 3
65 | 80 | 71 | 65.0618 | 246500 | 130645 | 9.72 | 5600 | 1208.6034 |  | 3
65 | 85 | 71 | 51.076 | 246500 | 157760 | 9.72 | 5600 | 1208.6034 |  | 3
65 | 75 | 71 | 82.6659 | 258300 | 105903 | 9.75 | 7000 | 1958.771 |  | 3
65 | 80 | 71 | 65.0618 | 258300 | 142065 | 9.75 | 7000 | 1958.771 |  | 3
65 | 85 | 71 | 51.076 | 258300 | 178227 | 9.75 | 7000 | 1958.771 |  | 3
65 | 75 | 71 | 82.6659 | 266300 | 109183 | 9.78 | 8400 | 3042.3464 |  | 3
65 | 80 | 71 | 65.0618 | 266300 | 154454 | 9.78 | 8400 | 3042.3464 |  | 3
65 | 85 | 71 | 51.076 | 266300 | 194399 | 9.78 | 8400 | 3042.3464 |  | 3
75 | 75 | 63 | 52.1129 | 208500 | 143865 | 10.77 | 5600 | 1125.2514 |  | 3
75 | 80 | 63 | 39.1676 | 208500 | 170970 | 10.77 | 5600 | 1125.2514 |  | 3
75 | 85 | 63 | 29.0563 | 208500 | 195990 | 10.77 | 5600 | 1125.2514 |  | 3
75 | 75 | 63 | 52.1129 | 219400 | 164550 | 10.83 | 7000 | 1958.771 |  | 3
75 | 80 | 63 | 39.1676 | 219400 | 195266 | 10.83 | 7000 | 1958.771 |  | 3
75 | 85 | 63 | 29.0563 | 219400 | 217206 | 10.83 | 7000 | 1958.771 |  | 3
75 | 75 | 63 | 52.1129 | 227900 | 177762 | 10.87 | 8400 | 3042.3464 |  | 3
75 | 80 | 63 | 39.1676 | 227900 | 214226 | 10.87 | 8400 | 3042.3464 |  | 3
75 | 85 | 63 | 29.0563 | 227900 | 227900 | 10.87 | 8400 | 3042.3464 |  | 3
75 | 75 | 67 | 66.7494 | 220900 | 121495 | 10.85 | 5600 | 1208.6034 |  | 3
75 | 80 | 67 | 51.5724 | 220900 | 148003 | 10.85 | 5600 | 1208.6034 |  | 3
75 | 85 | 67 | 39.6049 | 220900 | 174511 | 10.85 | 5600 | 1208.6034 |  | 3
75 | 75 | 67 | 66.7494 | 231600 | 132012 | 10.9 | 7000 | 1958.771 |  | 3
75 | 80 | 67 | 51.5724 | 231600 | 164436 | 10.9 | 7000 | 1958.771 |  | 3
75 | 85 | 67 | 39.6049 | 231600 | 196860 | 10.9 | 7000 | 1958.771 |  | 3
75 | 75 | 67 | 66.7494 | 239200 | 143520 | 10.93 | 8400 | 3042.3464 |  | 3
75 | 80 | 67 | 51.5724 | 239200 | 179400 | 10.93 | 8400 | 3042.3464 |  | 3
75 | 85 | 67 | 39.6049 | 239200 | 217672 | 10.93 | 8400 | 3042.3464 |  | 3
75 | 75 | 71 | 82.6659 | 234700 | 93880 | 10.93 | 5600 | 1208.6034 |  | 3
75 | 80 | 71 | 65.0618 | 234700 | 126738 | 10.93 | 5600 | 1208.6034 |  | 3
75 | 85 | 71 | 51.076 | 234700 | 152555 | 10.93 | 5600 | 1208.6034 |  | 3
75 | 75 | 71 | 82.6659 | 245400 | 100614 | 10.98 | 7000 | 1958.771 |  | 3
75 | 80 | 71 | 65.0618 | 245400 | 137424 | 10.98 | 7000 | 1958.771 |  | 3
75 | 85 | 71 | 51.076 | 245400 | 169326 | 10.98 | 7000 | 1958.771 |  | 3
75 | 75 | 71 | 82.6659 | 253100 | 106302 | 11.02 | 8400 | 3042.3464 |  | 3
75 | 80 | 71 | 65.0618 | 253100 | 146798 | 11.02 | 8400 | 3042.3464 |  | 3
75 | 85 | 71 | 51.076 | 253100 | 187294 | 11.02 | 8400 | 3042.3464 |  | 3
85 | 75 | 63 | 52.1129 | 197200 | 138040 | 12.14 | 5600 | 1125.2514 |  | 3
85 | 80 | 63 | 39.1676 | 197200 | 167620 | 12.14 | 5600 | 1125.2514 |  | 3
85 | 85 | 63 | 29.0563 | 197200 | 189312 | 12.14 | 5600 | 1125.2514 |  | 3
85 | 75 | 63 | 52.1129 | 207400 | 155550 | 12.2 | 7000 | 1854.581 |  | 3
85 | 80 | 63 | 39.1676 | 207400 | 188734 | 12.2 | 7000 | 1854.581 |  | 3
85 | 85 | 63 | 29.0563 | 207400 | 207400 | 12.2 | 7000 | 1854.581 |  | 3
85 | 75 | 63 | 52.1129 | 215700 | 170403 | 12.26 | 8400 | 3042.3464 |  | 3
85 | 80 | 63 | 39.1676 | 215700 | 204915 | 12.26 | 8400 | 3042.3464 |  | 3
85 | 85 | 63 | 29.0563 | 215700 | 215700 | 12.26 | 8400 | 3042.3464 |  | 3
85 | 75 | 67 | 66.7494 | 208900 | 112806 | 12.22 | 5600 | 1125.2514 |  | 3
85 | 80 | 67 | 51.5724 | 208900 | 144141 | 12.22 | 5600 | 1125.2514 |  | 3
85 | 85 | 67 | 39.6049 | 208900 | 171298 | 12.22 | 5600 | 1125.2514 |  | 3
85 | 75 | 67 | 66.7494 | 218900 | 122584 | 12.28 | 7000 | 1958.771 |  | 3
85 | 80 | 67 | 51.5724 | 218900 | 159797 | 12.28 | 7000 | 1958.771 |  | 3
85 | 85 | 67 | 39.6049 | 218900 | 192632 | 12.28 | 7000 | 1958.771 |  | 3
85 | 75 | 67 | 66.7494 | 226000 | 133340 | 12.32 | 8400 | 3042.3464 |  | 3
85 | 80 | 67 | 51.5724 | 226000 | 174020 | 12.32 | 8400 | 3042.3464 |  | 3
85 | 85 | 67 | 39.6049 | 226000 | 210180 | 12.32 | 8400 | 3042.3464 |  | 3
85 | 75 | 71 | 82.6659 | 222500 | 89000 | 12.33 | 5600 | 1208.6034 |  | 3
85 | 80 | 71 | 65.0618 | 222500 | 120150 | 12.33 | 5600 | 1208.6034 |  | 3
85 | 85 | 71 | 51.076 | 222500 | 146850 | 12.33 | 5600 | 1208.6034 |  | 3
85 | 75 | 71 | 82.6659 | 232400 | 92960 | 12.39 | 7000 | 1958.771 |  | 3
85 | 80 | 71 | 65.0618 | 232400 | 130144 | 12.39 | 7000 | 1958.771 |  | 3
85 | 85 | 71 | 51.076 | 232400 | 162680 | 12.39 | 7000 | 1958.771 |  | 3
85 | 75 | 71 | 82.6659 | 239500 | 100590 | 12.43 | 8400 | 3042.3464 |  | 3
85 | 80 | 71 | 65.0618 | 239500 | 138910 | 12.43 | 8400 | 3042.3464 |  | 3
85 | 85 | 71 | 51.076 | 239500 | 182020 | 12.43 | 8400 | 3042.3464 |  | 3
95 | 75 | 63 | 52.1129 | 185500 | 133560 | 13.67 | 5600 | 1125.2514 |  | 3
95 | 80 | 63 | 39.1676 | 185500 | 159530 | 13.67 | 5600 | 1125.2514 |  | 3
95 | 85 | 63 | 29.0563 | 185500 | 179935 | 13.67 | 5600 | 1125.2514 |  | 3
95 | 75 | 63 | 52.1129 | 195200 | 148352 | 13.75 | 7000 | 1854.581 |  | 3
95 | 80 | 63 | 39.1676 | 195200 | 179584 | 13.75 | 7000 | 1854.581 |  | 3
95 | 85 | 63 | 29.0563 | 195200 | 195200 | 13.75 | 7000 | 1854.581 |  | 3
95 | 75 | 63 | 52.1129 | 203400 | 166788 | 13.81 | 8400 | 2906.8994 |  | 3
95 | 80 | 63 | 39.1676 | 203400 | 197298 | 13.81 | 8400 | 2906.8994 |  | 3
95 | 85 | 63 | 29.0563 | 203400 | 203400 | 13.81 | 8400 | 2906.8994 |  | 3
95 | 75 | 67 | 66.7494 | 196600 | 106164 | 13.77 | 5600 | 1125.2514 |  | 3
95 | 80 | 67 | 51.5724 | 196600 | 135654 | 13.77 | 5600 | 1125.2514 |  | 3
95 | 85 | 67 | 39.6049 | 196600 | 163178 | 13.77 | 5600 | 1125.2514 |  | 3
95 | 75 | 67 | 66.7494 | 205900 | 119422 | 13.84 | 7000 | 1854.581 |  | 3
95 | 80 | 67 | 51.5724 | 205900 | 152366 | 13.84 | 7000 | 1854.581 |  | 3
95 | 85 | 67 | 39.6049 | 205900 | 181192 | 13.84 | 7000 | 1854.581 |  | 3
95 | 75 | 67 | 66.7494 | 212400 | 129564 | 13.88 | 8400 | 3042.3464 |  | 3
95 | 80 | 67 | 51.5724 | 212400 | 167796 | 13.88 | 8400 | 3042.3464 |  | 3
95 | 85 | 67 | 39.6049 | 212400 | 201780 | 13.88 | 8400 | 3042.3464 |  | 3
95 | 75 | 71 | 82.6659 | 209600 | 81744 | 13.87 | 5600 | 1125.2514 |  | 3
95 | 80 | 71 | 65.0618 | 209600 | 111088 | 13.87 | 5600 | 1125.2514 |  | 3
95 | 85 | 71 | 51.076 | 209600 | 140432 | 13.87 | 5600 | 1125.2514 |  | 3
95 | 75 | 71 | 82.6659 | 218700 | 87480 | 13.95 | 7000 | 1958.771 |  | 3
95 | 80 | 71 | 65.0618 | 218700 | 122472 | 13.95 | 7000 | 1958.771 |  | 3
95 | 85 | 71 | 51.076 | 218700 | 155277 | 13.95 | 7000 | 1958.771 |  | 3
95 | 75 | 71 | 82.6659 | 225000 | 92250 | 13.99 | 8400 | 3042.3464 |  | 3
95 | 80 | 71 | 65.0618 | 225000 | 135000 | 13.99 | 8400 | 3042.3464 |  | 3
95 | 85 | 71 | 51.076 | 225000 | 171000 | 13.99 | 8400 | 3042.3464 |  | 3
85 | 75 | 63 | 52.1129 | 277900 | 197309 | 18.5 | 7000 | 1958.771 |  | 4
85 | 80 | 63 | 39.1676 | 277900 | 225099 | 18.5 | 7000 | 1958.771 |  | 4
85 | 85 | 63 | 29.0563 | 277900 | 252889 | 18.5 | 7000 | 1958.771 |  | 4
85 | 75 | 63 | 52.1129 | 292300 | 222148 | 18.65 | 8500 | 3177.7933 |  | 4
85 | 80 | 63 | 39.1676 | 292300 | 251378 | 18.65 | 8500 | 3177.7933 |  | 4
85 | 85 | 63 | 29.0563 | 292300 | 280608 | 18.65 | 8500 | 3177.7933 |  | 4
85 | 75 | 63 | 52.1129 | 303900 | 237042 | 18.77 | 10000 | 4657.2905 |  | 4
85 | 80 | 63 | 39.1676 | 303900 | 273510 | 18.77 | 10000 | 4657.2905 |  | 4
85 | 85 | 63 | 29.0563 | 303900 | 303900 | 18.77 | 10000 | 4657.2905 |  | 4
85 | 75 | 67 | 66.7494 | 294600 | 170868 | 18.69 | 7000 | 2073.3799 |  | 4
85 | 80 | 67 | 51.5724 | 294600 | 206220 | 18.69 | 7000 | 2073.3799 |  | 4
85 | 85 | 67 | 39.6049 | 294600 | 232734 | 18.69 | 7000 | 2073.3799 |  | 4
85 | 75 | 67 | 66.7494 | 307100 | 199615 | 18.82 | 8500 | 3177.7933 |  | 4
85 | 80 | 67 | 51.5724 | 307100 | 227254 | 18.82 | 8500 | 3177.7933 |  | 4
85 | 85 | 67 | 39.6049 | 307100 | 254893 | 18.82 | 8500 | 3177.7933 |  | 4
85 | 75 | 67 | 66.7494 | 316800 | 199584 | 18.91 | 10000 | 4657.2905 |  | 4
85 | 80 | 67 | 51.5724 | 316800 | 243936 | 18.91 | 10000 | 4657.2905 |  | 4
85 | 85 | 67 | 39.6049 | 316800 | 275616 | 18.91 | 10000 | 4657.2905 |  | 4
85 | 75 | 71 | 82.6659 | 313200 | 137808 | 18.91 | 7000 | 2073.3799 |  | 4
85 | 80 | 71 | 65.0618 | 313200 | 178524 | 18.91 | 7000 | 2073.3799 |  | 4
85 | 85 | 71 | 51.076 | 313200 | 209844 | 18.91 | 7000 | 2073.3799 |  | 4
85 | 75 | 71 | 82.6659 | 326300 | 143572 | 19.05 | 8500 | 3177.7933 |  | 4
85 | 80 | 71 | 65.0618 | 326300 | 192517 | 19.05 | 8500 | 3177.7933 |  | 4
85 | 85 | 71 | 51.076 | 326300 | 234936 | 19.05 | 8500 | 3177.7933 |  | 4
85 | 75 | 71 | 82.6659 | 333600 | 160128 | 19.13 | 10000 | 4657.2905 |  | 4
85 | 80 | 71 | 65.0618 | 333600 | 206832 | 19.13 | 10000 | 4657.2905 |  | 4
85 | 85 | 71 | 51.076 | 333600 | 250200 | 19.13 | 10000 | 4657.2905 |  | 4
95 | 75 | 63 | 52.1129 | 262000 | 188640 | 20.73 | 7000 | 1958.771 |  | 4
95 | 80 | 63 | 39.1676 | 262000 | 214840 | 20.73 | 7000 | 1958.771 |  | 4
95 | 85 | 63 | 29.0563 | 262000 | 243660 | 20.73 | 7000 | 1958.771 |  | 4
95 | 75 | 63 | 52.1129 | 275700 | 209532 | 20.88 | 8500 | 3042.3464 |  | 4
95 | 80 | 63 | 39.1676 | 275700 | 239859 | 20.88 | 8500 | 3042.3464 |  | 4
95 | 85 | 63 | 29.0563 | 275700 | 270186 | 20.88 | 8500 | 3042.3464 |  | 4
95 | 75 | 63 | 52.1129 | 286400 | 226256 | 20.99 | 10000 | 4657.2905 |  | 4
95 | 80 | 63 | 39.1676 | 286400 | 263488 | 20.99 | 10000 | 4657.2905 |  | 4
95 | 85 | 63 | 29.0563 | 286400 | 286400 | 20.99 | 10000 | 4657.2905 |  | 4
95 | 75 | 67 | 66.7494 | 276900 | 163371 | 20.92 | 7000 | 1958.771 |  | 4
95 | 80 | 67 | 51.5724 | 276900 | 196599 | 20.92 | 7000 | 1958.771 |  | 4
95 | 85 | 67 | 39.6049 | 276900 | 218751 | 20.92 | 7000 | 1958.771 |  | 4
95 | 75 | 67 | 66.7494 | 288700 | 173220 | 21.05 | 8500 | 3177.7933 |  | 4
95 | 80 | 67 | 51.5724 | 288700 | 216525 | 21.05 | 8500 | 3177.7933 |  | 4
95 | 85 | 67 | 39.6049 | 288700 | 245395 | 21.05 | 8500 | 3177.7933 |  | 4
95 | 75 | 67 | 66.7494 | 298100 | 190784 | 21.14 | 10000 | 4657.2905 |  | 4
95 | 80 | 67 | 51.5724 | 298100 | 232518 | 21.14 | 10000 | 4657.2905 |  | 4
95 | 85 | 67 | 39.6049 | 298100 | 265309 | 21.14 | 10000 | 4657.2905 |  | 4
95 | 75 | 71 | 82.6659 | 294800 | 129712 | 21.14 | 7000 | 2073.3799 |  | 4
95 | 80 | 71 | 65.0618 | 294800 | 170984 | 21.14 | 7000 | 2073.3799 |  | 4
95 | 85 | 71 | 51.076 | 294800 | 197516 | 21.14 | 7000 | 2073.3799 |  | 4
95 | 75 | 71 | 82.6659 | 304800 | 137160 | 21.25 | 8500 | 3177.7933 |  | 4
95 | 80 | 71 | 65.0618 | 304800 | 179832 | 21.25 | 8500 | 3177.7933 |  | 4
95 | 85 | 71 | 51.076 | 304800 | 219456 | 21.25 | 8500 | 3177.7933 |  | 4
95 | 75 | 71 | 82.6659 | 316600 | 161466 | 21.4 | 10000 | 4657.2905 |  | 4
95 | 80 | 71 | 65.0618 | 316600 | 196292 | 21.4 | 10000 | 4657.2905 |  | 4
95 | 85 | 71 | 51.076 | 316600 | 240616 | 21.4 | 10000 | 4657.2905 |  | 4
105 | 75 | 63 | 52.1129 | 245100 | 178923 | 23.21 | 7000 | 1958.771 |  | 4
105 | 80 | 63 | 39.1676 | 245100 | 205884 | 23.21 | 7000 | 1958.771 |  | 4
105 | 85 | 63 | 29.0563 | 245100 | 232845 | 23.21 | 7000 | 1958.771 |  | 4
105 | 75 | 63 | 52.1129 | 258200 | 201396 | 23.37 | 8500 | 3042.3464 |  | 4
105 | 80 | 63 | 39.1676 | 258200 | 229798 | 23.37 | 8500 | 3042.3464 |  | 4
105 | 85 | 63 | 29.0563 | 258200 | 255618 | 23.37 | 8500 | 3042.3464 |  | 4
105 | 75 | 63 | 52.1129 | 268100 | 217161 | 23.48 | 10000 | 4501.0056 |  | 4
105 | 80 | 63 | 39.1676 | 268100 | 252014 | 23.48 | 10000 | 4501.0056 |  | 4
105 | 85 | 63 | 29.0563 | 268100 | 268100 | 23.48 | 10000 | 4501.0056 |  | 4
105 | 75 | 67 | 66.7494 | 258800 | 147516 | 23.39 | 7000 | 1958.771 |  | 4
105 | 80 | 67 | 51.5724 | 258800 | 183748 | 23.39 | 7000 | 1958.771 |  | 4
105 | 85 | 67 | 39.6049 | 258800 | 207040 | 23.39 | 7000 | 1958.771 |  | 4
105 | 75 | 67 | 66.7494 | 269800 | 167276 | 23.54 | 8500 | 3042.3464 |  | 4
105 | 80 | 67 | 51.5724 | 269800 | 202350 | 23.54 | 8500 | 3042.3464 |  | 4
105 | 85 | 67 | 39.6049 | 269800 | 232028 | 23.54 | 8500 | 3042.3464 |  | 4
105 | 75 | 67 | 66.7494 | 279100 | 181415 | 23.65 | 10000 | 4501.0056 |  | 4
105 | 80 | 67 | 51.5724 | 279100 | 217698 | 23.65 | 10000 | 4501.0056 |  | 4
105 | 85 | 67 | 39.6049 | 279100 | 253981 | 23.65 | 10000 | 4501.0056 |  | 4
105 | 75 | 71 | 82.6659 | 270400 | 116272 | 23.57 | 7000 | 1958.771 |  | 4
105 | 80 | 71 | 65.0618 | 270400 | 167648 | 23.57 | 7000 | 1958.771 |  | 4
105 | 85 | 71 | 51.076 | 270400 | 186576 | 23.57 | 7000 | 1958.771 |  | 4
105 | 75 | 71 | 82.6659 | 287600 | 132296 | 23.79 | 8500 | 3177.7933 |  | 4
105 | 80 | 71 | 65.0618 | 287600 | 172560 | 23.79 | 8500 | 3177.7933 |  | 4
105 | 85 | 71 | 51.076 | 287600 | 212824 | 23.79 | 8500 | 3177.7933 |  | 4
105 | 75 | 71 | 82.6659 | 295300 | 138791 | 23.87 | 10000 | 4657.2905 |  | 4
105 | 80 | 71 | 65.0618 | 295300 | 188992 | 23.87 | 10000 | 4657.2905 |  | 4
105 | 85 | 71 | 51.076 | 295300 | 230334 | 23.87 | 10000 | 4657.2905 |  | 4
115 | 75 | 63 | 52.1129 | 227700 | 168498 | 25.99 | 7000 | 1958.771 |  | 4
115 | 80 | 63 | 39.1676 | 227700 | 193545 | 25.99 | 7000 | 1958.771 |  | 4
115 | 85 | 63 | 29.0563 | 227700 | 220869 | 25.99 | 7000 | 1958.771 |  | 4
115 | 75 | 63 | 52.1129 | 239500 | 186810 | 26.14 | 8500 | 3042.3464 |  | 4
115 | 80 | 63 | 39.1676 | 239500 | 217945 | 26.14 | 8500 | 3042.3464 |  | 4
115 | 85 | 63 | 29.0563 | 239500 | 239500 | 26.14 | 8500 | 3042.3464 |  | 4
115 | 75 | 63 | 52.1129 | 248800 | 204016 | 26.28 | 10000 | 4501.0056 |  | 4
115 | 80 | 63 | 39.1676 | 248800 | 238848 | 26.28 | 10000 | 4501.0056 |  | 4
115 | 85 | 63 | 29.0563 | 248800 | 248800 | 26.28 | 10000 | 4501.0056 |  | 4
115 | 75 | 67 | 66.7494 | 239400 | 138852 | 26.18 | 7000 | 1958.771 |  | 4
115 | 80 | 67 | 51.5724 | 239400 | 174762 | 26.18 | 7000 | 1958.771 |  | 4
115 | 85 | 67 | 39.6049 | 239400 | 198702 | 26.18 | 7000 | 1958.771 |  | 4
115 | 75 | 67 | 66.7494 | 250200 | 160128 | 26.31 | 8500 | 3042.3464 |  | 4
115 | 80 | 67 | 51.5724 | 250200 | 192654 | 26.31 | 8500 | 3042.3464 |  | 4
115 | 85 | 67 | 39.6049 | 250200 | 220176 | 26.31 | 8500 | 3042.3464 |  | 4
115 | 75 | 67 | 66.7494 | 258700 | 173329 | 26.42 | 10000 | 4501.0056 |  | 4
115 | 80 | 67 | 51.5724 | 258700 | 206960 | 26.42 | 10000 | 4501.0056 |  | 4
115 | 85 | 67 | 39.6049 | 258700 | 240591 | 26.42 | 10000 | 4501.0056 |  | 4
115 | 75 | 71 | 82.6659 | 256500 | 112860 | 26.43 | 7000 | 1958.771 |  | 4
115 | 80 | 71 | 65.0618 | 256500 | 143640 | 26.43 | 7000 | 1958.771 |  | 4
115 | 85 | 71 | 51.076 | 256500 | 179550 | 26.43 | 7000 | 1958.771 |  | 4
115 | 75 | 71 | 82.6659 | 266000 | 125020 | 26.57 | 8500 | 3042.3464 |  | 4
115 | 80 | 71 | 65.0618 | 266000 | 164920 | 26.57 | 8500 | 3042.3464 |  | 4
115 | 85 | 71 | 51.076 | 266000 | 196840 | 26.57 | 8500 | 3042.3464 |  | 4
115 | 75 | 71 | 82.6659 | 273600 | 125856 | 26.67 | 10000 | 4501.0056 |  | 4
115 | 80 | 71 | 65.0618 | 273600 | 180576 | 26.67 | 10000 | 4501.0056 |  | 4
115 | 85 | 71 | 51.076 | 273600 | 216144 | 26.67 | 10000 | 4501.0056 |  | 4
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 7
Degradation Coefficient (C_d)
IEER or SEER | 22
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 75 | 63 | 52.1129 | 66200 | 36410 | 3.77 | 800 | 250.0559 |  | 1
65 | 80 | 63 | 39.1676 | 66200 | 41044 | 3.77 | 800 | 250.0559 |  | 1
65 | 85 | 63 | 29.0563 | 66200 | 47002 | 3.77 | 800 | 250.0559 |  | 1
65 | 75 | 63 | 52.1129 | 80200 | 48120 | 3.8 | 1335 | 291.7318 |  | 1
65 | 80 | 63 | 39.1676 | 80200 | 56140 | 3.8 | 1335 | 291.7318 |  | 1
65 | 85 | 63 | 29.0563 | 80200 | 63358 | 3.8 | 1335 | 291.7318 |  | 1
65 | 75 | 63 | 52.1129 | 89000 | 56070 | 3.82 | 1875 | 291.7318 |  | 1
65 | 80 | 63 | 39.1676 | 89000 | 66750 | 3.82 | 1875 | 291.7318 |  | 1
65 | 85 | 63 | 29.0563 | 89000 | 77430 | 3.82 | 1875 | 291.7318 |  | 1
65 | 75 | 67 | 66.7494 | 69800 | 33504 | 3.76 | 800 | 250.0559 |  | 1
65 | 80 | 67 | 51.5724 | 69800 | 39786 | 3.76 | 800 | 250.0559 |  | 1
65 | 85 | 67 | 39.6049 | 69800 | 43276 | 3.76 | 800 | 250.0559 |  | 1
65 | 75 | 67 | 66.7494 | 84400 | 41356 | 3.81 | 1335 | 291.7318 |  | 1
65 | 80 | 67 | 51.5724 | 84400 | 48108 | 3.81 | 1335 | 291.7318 |  | 1
65 | 85 | 67 | 39.6049 | 84400 | 55704 | 3.81 | 1335 | 291.7318 |  | 1
65 | 75 | 67 | 66.7494 | 93800 | 48776 | 3.84 | 1875 | 291.7318 |  | 1
65 | 80 | 67 | 51.5724 | 93800 | 57218 | 3.84 | 1875 | 291.7318 |  | 1
65 | 85 | 67 | 39.6049 | 93800 | 67536 | 3.84 | 1875 | 291.7318 |  | 1
65 | 75 | 71 | 82.6659 | 72800 | 28392 | 3.77 | 800 | 291.7318 |  | 1
65 | 80 | 71 | 65.0618 | 72800 | 34216 | 3.77 | 800 | 291.7318 |  | 1
65 | 85 | 71 | 51.076 | 72800 | 38584 | 3.77 | 800 | 291.7318 |  | 1
65 | 75 | 71 | 82.6659 | 88600 | 35440 | 3.82 | 1335 | 291.7318 |  | 1
65 | 80 | 71 | 65.0618 | 88600 | 42528 | 3.82 | 1335 | 291.7318 |  | 1
65 | 85 | 71 | 51.076 | 88600 | 48730 | 3.82 | 1335 | 291.7318 |  | 1
65 | 75 | 71 | 82.6659 | 98300 | 39320 | 3.85 | 1875 | 291.7318 |  | 1
65 | 80 | 71 | 65.0618 | 98300 | 49150 | 3.85 | 1875 | 291.7318 |  | 1
65 | 85 | 71 | 51.076 | 98300 | 57997 | 3.85 | 1875 | 291.7318 |  | 1
75 | 75 | 63 | 52.1129 | 64300 | 35365 | 4.37 | 800 | 250.0559 |  | 1
75 | 80 | 63 | 39.1676 | 64300 | 41152 | 4.37 | 800 | 250.0559 |  | 1
75 | 85 | 63 | 29.0563 | 64300 | 45653 | 4.37 | 800 | 250.0559 |  | 1
75 | 75 | 63 | 52.1129 | 77600 | 47336 | 4.41 | 1335 | 291.7318 |  | 1
75 | 80 | 63 | 39.1676 | 77600 | 54320 | 4.41 | 1335 | 291.7318 |  | 1
75 | 85 | 63 | 29.0563 | 77600 | 62080 | 4.41 | 1335 | 291.7318 |  | 1
75 | 75 | 63 | 52.1129 | 85800 | 54912 | 4.44 | 1875 | 291.7318 |  | 1
75 | 80 | 63 | 39.1676 | 85800 | 66066 | 4.44 | 1875 | 291.7318 |  | 1
75 | 85 | 63 | 29.0563 | 85800 | 76362 | 4.44 | 1875 | 291.7318 |  | 1
75 | 75 | 67 | 66.7494 | 67500 | 32400 | 4.37 | 800 | 250.0559 |  | 1
75 | 80 | 67 | 51.5724 | 67500 | 37800 | 4.37 | 800 | 250.0559 |  | 1
75 | 85 | 67 | 39.6049 | 67500 | 41850 | 4.37 | 800 | 250.0559 |  | 1
75 | 75 | 67 | 66.7494 | 81700 | 40850 | 4.42 | 1335 | 291.7318 |  | 1
75 | 80 | 67 | 51.5724 | 81700 | 47386 | 4.42 | 1335 | 291.7318 |  | 1
75 | 85 | 67 | 39.6049 | 81700 | 54739 | 4.42 | 1335 | 291.7318 |  | 1
75 | 75 | 67 | 66.7494 | 90400 | 46104 | 4.45 | 1875 | 291.7318 |  | 1
75 | 80 | 67 | 51.5724 | 90400 | 56048 | 4.45 | 1875 | 291.7318 |  | 1
75 | 85 | 67 | 39.6049 | 90400 | 65992 | 4.45 | 1875 | 291.7318 |  | 1
75 | 75 | 71 | 82.6659 | 70300 | 29526 | 4.38 | 800 | 250.0559 |  | 1
75 | 80 | 71 | 65.0618 | 70300 | 33041 | 4.38 | 800 | 250.0559 |  | 1
75 | 85 | 71 | 51.076 | 70300 | 37259 | 4.38 | 800 | 250.0559 |  | 1
75 | 75 | 71 | 82.6659 | 85700 | 34280 | 4.43 | 1335 | 291.7318 |  | 1
75 | 80 | 71 | 65.0618 | 85700 | 41136 | 4.43 | 1335 | 291.7318 |  | 1
75 | 85 | 71 | 51.076 | 85700 | 47135 | 4.43 | 1335 | 291.7318 |  | 1
75 | 75 | 71 | 82.6659 | 94900 | 37960 | 4.47 | 1875 | 291.7318 |  | 1
75 | 80 | 71 | 65.0618 | 94900 | 47450 | 4.47 | 1875 | 291.7318 |  | 1
75 | 85 | 71 | 51.076 | 94900 | 55991 | 4.47 | 1875 | 291.7318 |  | 1
85 | 75 | 63 | 52.1129 | 62000 | 37200 | 4.99 | 800 | 250.0559 |  | 1
85 | 80 | 63 | 39.1676 | 62000 | 39680 | 4.99 | 800 | 250.0559 |  | 1
85 | 85 | 63 | 29.0563 | 62000 | 44020 | 4.99 | 800 | 250.0559 |  | 1
85 | 75 | 63 | 52.1129 | 74900 | 45689 | 5.04 | 1335 | 291.7318 |  | 1
85 | 80 | 63 | 39.1676 | 74900 | 53179 | 5.04 | 1335 | 291.7318 |  | 1
85 | 85 | 63 | 29.0563 | 74900 | 60669 | 5.04 | 1335 | 291.7318 |  | 1
85 | 75 | 63 | 52.1129 | 82400 | 53560 | 5.07 | 1875 | 291.7318 |  | 1
85 | 80 | 63 | 39.1676 | 82400 | 64272 | 5.07 | 1875 | 291.7318 |  | 1
85 | 85 | 63 | 29.0563 | 82400 | 74984 | 5.07 | 1875 | 291.7318 |  | 1
85 | 75 | 67 | 66.7494 | 65200 | 32600 | 5 | 800 | 250.0559 |  | 1
85 | 80 | 67 | 51.5724 | 65200 | 36512 | 5 | 800 | 250.0559 |  | 1
85 | 85 | 67 | 39.6049 | 65200 | 41076 | 5 | 800 | 250.0559 |  | 1
85 | 75 | 67 | 66.7494 | 78800 | 39400 | 5.06 | 1335 | 291.7318 |  | 1
85 | 80 | 67 | 51.5724 | 78800 | 45704 | 5.06 | 1335 | 291.7318 |  | 1
85 | 85 | 67 | 39.6049 | 78800 | 53584 | 5.06 | 1335 | 291.7318 |  | 1
85 | 75 | 67 | 66.7494 | 86900 | 45188 | 5.09 | 1875 | 291.7318 |  | 1
85 | 80 | 67 | 51.5724 | 86900 | 54747 | 5.09 | 1875 | 291.7318 |  | 1
85 | 85 | 67 | 39.6049 | 86900 | 65175 | 5.09 | 1875 | 291.7318 |  | 1
85 | 75 | 71 | 82.6659 | 68000 | 27880 | 5.01 | 800 | 250.0559 |  | 1
85 | 80 | 71 | 65.0618 | 68000 | 31960 | 5.01 | 800 | 250.0559 |  | 1
85 | 85 | 71 | 51.076 | 68000 | 36040 | 5.01 | 800 | 250.0559 |  | 1
85 | 75 | 71 | 82.6659 | 82700 | 33080 | 5.07 | 1335 | 291.7318 |  | 1
85 | 80 | 71 | 65.0618 | 82700 | 39696 | 5.07 | 1335 | 291.7318 |  | 1
85 | 85 | 71 | 51.076 | 82700 | 46312 | 5.07 | 1335 | 291.7318 |  | 1
85 | 75 | 71 | 82.6659 | 91300 | 36520 | 5.11 | 1875 | 291.7318 |  | 1
85 | 80 | 71 | 65.0618 | 91300 | 45650 | 5.11 | 1875 | 291.7318 |  | 1
85 | 85 | 71 | 51.076 | 91300 | 54780 | 5.11 | 1875 | 291.7318 |  | 1
95 | 75 | 63 | 52.1129 | 59700 | 35223 | 5.68 | 800 | 250.0559 |  | 1
95 | 80 | 63 | 39.1676 | 59700 | 39999 | 5.68 | 800 | 250.0559 |  | 1
95 | 85 | 63 | 29.0563 | 59700 | 44178 | 5.68 | 800 | 250.0559 |  | 1
95 | 75 | 63 | 52.1129 | 71800 | 44516 | 5.73 | 1335 | 291.7318 |  | 1
95 | 80 | 63 | 39.1676 | 71800 | 52414 | 5.73 | 1335 | 291.7318 |  | 1
95 | 85 | 63 | 29.0563 | 71800 | 59594 | 5.73 | 1335 | 291.7318 |  | 1
95 | 75 | 63 | 52.1129 | 78700 | 52729 | 5.76 | 1875 | 291.7318 |  | 1
95 | 80 | 63 | 39.1676 | 78700 | 63747 | 5.76 | 1875 | 291.7318 |  | 1
95 | 85 | 63 | 29.0563 | 78700 | 73191 | 5.76 | 1875 | 291.7318 |  | 1
95 | 75 | 67 | 66.7494 | 62500 | 30625 | 5.69 | 800 | 250.0559 |  | 1
95 | 80 | 67 | 51.5724 | 62500 | 35000 | 5.69 | 800 | 250.0559 |  | 1
95 | 85 | 67 | 39.6049 | 62500 | 39375 | 5.69 | 800 | 250.0559 |  | 1
95 | 75 | 67 | 66.7494 | 75600 | 37800 | 5.75 | 1335 | 291.7318 |  | 1
95 | 80 | 67 | 51.5724 | 75600 | 44604 | 5.75 | 1335 | 291.7318 |  | 1
95 | 85 | 67 | 39.6049 | 75600 | 52164 | 5.75 | 1335 | 291.7318 |  | 1
95 | 75 | 67 | 66.7494 | 83000 | 43990 | 5.78 | 1875 | 291.7318 |  | 1
95 | 80 | 67 | 51.5724 | 83000 | 53120 | 5.78 | 1875 | 291.7318 |  | 1
95 | 85 | 67 | 39.6049 | 83000 | 63080 | 5.78 | 1875 | 291.7318 |  | 1
95 | 75 | 71 | 82.6659 | 65600 | 26240 | 5.71 | 800 | 250.0559 |  | 1
95 | 80 | 71 | 65.0618 | 65600 | 30832 | 5.71 | 800 | 250.0559 |  | 1
95 | 85 | 71 | 51.076 | 65600 | 34768 | 5.71 | 800 | 250.0559 |  | 1
95 | 75 | 71 | 82.6659 | 79400 | 30966 | 5.77 | 1335 | 291.7318 |  | 1
95 | 80 | 71 | 65.0618 | 79400 | 38112 | 5.77 | 1335 | 291.7318 |  | 1
95 | 85 | 71 | 51.076 | 79400 | 44464 | 5.77 | 1335 | 291.7318 |  | 1
95 | 75 | 71 | 82.6659 | 87200 | 34880 | 5.81 | 1875 | 291.7318 |  | 1
95 | 80 | 71 | 65.0618 | 87200 | 44472 | 5.81 | 1875 | 291.7318 |  | 1
95 | 85 | 71 | 51.076 | 87200 | 52320 | 5.81 | 1875 | 291.7318 |  | 1
85 | 75 | 63 | 52.1129 | 82400 | 52736 | 5.07 | 1875 | 291.7318 |  | 2
85 | 80 | 63 | 39.1676 | 82400 | 63448 | 5.07 | 1875 | 291.7318 |  | 2
85 | 85 | 63 | 29.0563 | 82400 | 74160 | 5.07 | 1875 | 291.7318 |  | 2
85 | 75 | 63 | 52.1129 | 88800 | 63048 | 5.1 | 2625 | 291.7318 |  | 2
85 | 80 | 63 | 39.1676 | 88800 | 78144 | 5.1 | 2625 | 291.7318 |  | 2
85 | 85 | 63 | 29.0563 | 88800 | 88800 | 5.1 | 2625 | 291.7318 |  | 2
85 | 75 | 63 | 52.1129 | 94900 | 76869 | 5.12 | 3600 | 427.1788 |  | 2
85 | 80 | 63 | 39.1676 | 94900 | 94900 | 5.12 | 3600 | 427.1788 |  | 2
85 | 85 | 63 | 29.0563 | 94900 | 94900 | 5.12 | 3600 | 427.1788 |  | 2
85 | 75 | 67 | 66.7494 | 86900 | 45188 | 5.09 | 1875 | 291.7318 |  | 2
85 | 80 | 67 | 51.5724 | 86900 | 53878 | 5.09 | 1875 | 291.7318 |  | 2
85 | 85 | 67 | 39.6049 | 86900 | 63437 | 5.09 | 1875 | 291.7318 |  | 2
85 | 75 | 67 | 66.7494 | 93700 | 52472 | 5.12 | 2625 | 291.7318 |  | 2
85 | 80 | 67 | 51.5724 | 93700 | 63716 | 5.12 | 2625 | 291.7318 |  | 2
85 | 85 | 67 | 39.6049 | 93700 | 78708 | 5.12 | 2625 | 291.7318 |  | 2
85 | 75 | 67 | 66.7494 | 99000 | 60390 | 5.15 | 3600 | 427.1788 |  | 2
85 | 80 | 67 | 51.5724 | 99000 | 78210 | 5.15 | 3600 | 427.1788 |  | 2
85 | 85 | 67 | 39.6049 | 99000 | 96030 | 5.15 | 3600 | 427.1788 |  | 2
85 | 75 | 71 | 82.6659 | 91300 | 36520 | 5.11 | 1875 | 291.7318 |  | 2
85 | 80 | 71 | 65.0618 | 91300 | 45650 | 5.11 | 1875 | 291.7318 |  | 2
85 | 85 | 71 | 51.076 | 91300 | 54780 | 5.11 | 1875 | 291.7318 |  | 2
85 | 75 | 71 | 82.6659 | 98500 | 40385 | 5.14 | 2625 | 291.7318 |  | 2
85 | 80 | 71 | 65.0618 | 98500 | 53190 | 5.14 | 2625 | 291.7318 |  | 2
85 | 85 | 71 | 51.076 | 98500 | 65010 | 5.14 | 2625 | 291.7318 |  | 2
85 | 75 | 71 | 82.6659 | 104200 | 45848 | 5.17 | 3600 | 427.1788 |  | 2
85 | 80 | 71 | 65.0618 | 104200 | 62520 | 5.17 | 3600 | 427.1788 |  | 2
85 | 85 | 71 | 51.076 | 104200 | 80234 | 5.17 | 3600 | 427.1788 |  | 2
95 | 75 | 63 | 52.1129 | 78700 | 51942 | 5.76 | 1875 | 291.7318 |  | 2
95 | 80 | 63 | 39.1676 | 78700 | 62173 | 5.76 | 1875 | 291.7318 |  | 2
95 | 85 | 63 | 29.0563 | 78700 | 72404 | 5.76 | 1875 | 291.7318 |  | 2
95 | 75 | 63 | 52.1129 | 84600 | 61758 | 5.78 | 2625 | 291.7318 |  | 2
95 | 80 | 63 | 39.1676 | 84600 | 76140 | 5.78 | 2625 | 291.7318 |  | 2
95 | 85 | 63 | 29.0563 | 84600 | 84600 | 5.78 | 2625 | 291.7318 |  | 2
95 | 75 | 63 | 52.1129 | 90800 | 75364 | 5.82 | 3600 | 427.1788 |  | 2
95 | 80 | 63 | 39.1676 | 90800 | 90800 | 5.82 | 3600 | 427.1788 |  | 2
95 | 85 | 63 | 29.0563 | 90800 | 90800 | 5.82 | 3600 | 427.1788 |  | 2
95 | 75 | 67 | 66.7494 | 83000 | 43990 | 5.78 | 1875 | 291.7318 |  | 2
95 | 80 | 67 | 51.5724 | 83000 | 52290 | 5.78 | 1875 | 291.7318 |  | 2
95 | 85 | 67 | 39.6049 | 83000 | 61420 | 5.78 | 1875 | 291.7318 |  | 2
95 | 75 | 67 | 66.7494 | 89300 | 50901 | 5.81 | 2625 | 291.7318 |  | 2
95 | 80 | 67 | 51.5724 | 89300 | 62510 | 5.81 | 2625 | 291.7318 |  | 2
95 | 85 | 67 | 39.6049 | 89300 | 77691 | 5.81 | 2625 | 291.7318 |  | 2
95 | 75 | 67 | 66.7494 | 94100 | 57401 | 5.84 | 3600 | 427.1788 |  | 2
95 | 80 | 67 | 51.5724 | 94100 | 77162 | 5.84 | 3600 | 427.1788 |  | 2
95 | 85 | 67 | 39.6049 | 94100 | 94100 | 5.84 | 3600 | 427.1788 |  | 2
95 | 75 | 71 | 82.6659 | 87200 | 34880 | 5.81 | 1875 | 291.7318 |  | 2
95 | 80 | 71 | 65.0618 | 87200 | 44472 | 5.81 | 1875 | 291.7318 |  | 2
95 | 85 | 71 | 51.076 | 87200 | 52320 | 5.81 | 1875 | 291.7318 |  | 2
95 | 75 | 71 | 82.6659 | 93900 | 39438 | 5.84 | 2625 | 291.7318 |  | 2
95 | 80 | 71 | 65.0618 | 93900 | 51645 | 5.84 | 2625 | 291.7318 |  | 2
95 | 85 | 71 | 51.076 | 93900 | 62913 | 5.84 | 2625 | 291.7318 |  | 2
95 | 75 | 71 | 82.6659 | 99000 | 43560 | 5.86 | 3600 | 427.1788 |  | 2
95 | 80 | 71 | 65.0618 | 99000 | 60390 | 5.86 | 3600 | 427.1788 |  | 2
95 | 85 | 71 | 51.076 | 99000 | 78210 | 5.86 | 3600 | 427.1788 |  | 2
105 | 75 | 63 | 52.1129 | 74700 | 50049 | 6.54 | 1875 | 291.7318 |  | 2
105 | 80 | 63 | 39.1676 | 74700 | 60507 | 6.54 | 1875 | 291.7318 |  | 2
105 | 85 | 63 | 29.0563 | 74700 | 70965 | 6.54 | 1875 | 291.7318 |  | 2
105 | 75 | 63 | 52.1129 | 80300 | 60225 | 6.57 | 2625 | 291.7318 |  | 2
105 | 80 | 63 | 39.1676 | 80300 | 74679 | 6.57 | 2625 | 291.7318 |  | 2
105 | 85 | 63 | 29.0563 | 80300 | 80300 | 6.57 | 2625 | 291.7318 |  | 2
105 | 75 | 63 | 52.1129 | 86300 | 74218 | 6.6 | 3600 | 427.1788 |  | 2
105 | 80 | 63 | 39.1676 | 86300 | 86300 | 6.6 | 3600 | 427.1788 |  | 2
105 | 85 | 63 | 29.0563 | 86300 | 86300 | 6.6 | 3600 | 427.1788 |  | 2
105 | 75 | 67 | 66.7494 | 78700 | 41711 | 6.56 | 1875 | 291.7318 |  | 2
105 | 80 | 67 | 51.5724 | 78700 | 51155 | 6.56 | 1875 | 291.7318 |  | 2
105 | 85 | 67 | 39.6049 | 78700 | 60599 | 6.56 | 1875 | 291.7318 |  | 2
105 | 75 | 67 | 66.7494 | 84300 | 48051 | 6.59 | 2625 | 291.7318 |  | 2
105 | 80 | 67 | 51.5724 | 84300 | 60696 | 6.59 | 2625 | 291.7318 |  | 2
105 | 85 | 67 | 39.6049 | 84300 | 75870 | 6.59 | 2625 | 291.7318 |  | 2
105 | 75 | 67 | 66.7494 | 88500 | 55755 | 6.61 | 3600 | 427.1788 |  | 2
105 | 80 | 67 | 51.5724 | 88500 | 76110 | 6.61 | 3600 | 427.1788 |  | 2
105 | 85 | 67 | 39.6049 | 88500 | 88500 | 6.61 | 3600 | 427.1788 |  | 2
105 | 75 | 71 | 82.6659 | 82800 | 33120 | 6.59 | 1875 | 291.7318 |  | 2
105 | 80 | 71 | 65.0618 | 82800 | 43056 | 6.59 | 1875 | 291.7318 |  | 2
105 | 85 | 71 | 51.076 | 82800 | 52164 | 6.59 | 1875 | 291.7318 |  | 2
105 | 75 | 71 | 82.6659 | 88600 | 36326 | 6.62 | 2625 | 291.7318 |  | 2
105 | 80 | 71 | 65.0618 | 88600 | 49616 | 6.62 | 2625 | 291.7318 |  | 2
105 | 85 | 71 | 51.076 | 88600 | 62020 | 6.62 | 2625 | 291.7318 |  | 2
105 | 75 | 71 | 82.6659 | 93200 | 41940 | 6.64 | 3600 | 427.1788 |  | 2
105 | 80 | 71 | 65.0618 | 93200 | 58716 | 6.64 | 3600 | 427.1788 |  | 2
105 | 85 | 71 | 51.076 | 93200 | 78288 | 6.64 | 3600 | 427.1788 |  | 2
115 | 75 | 63 | 52.1129 | 69900 | 47532 | 7.43 | 1875 | 250.0559 |  | 2
115 | 80 | 63 | 39.1676 | 69900 | 59415 | 7.43 | 1875 | 250.0559 |  | 2
115 | 85 | 63 | 29.0563 | 69900 | 68502 | 7.43 | 1875 | 250.0559 |  | 2
115 | 75 | 63 | 52.1129 | 75400 | 59566 | 7.46 | 2625 | 291.7318 |  | 2
115 | 80 | 63 | 39.1676 | 75400 | 73138 | 7.46 | 2625 | 291.7318 |  | 2
115 | 85 | 63 | 29.0563 | 75400 | 75400 | 7.46 | 2625 | 291.7318 |  | 2
115 | 75 | 63 | 52.1129 | 81000 | 73710 | 7.49 | 3600 | 427.1788 |  | 2
115 | 80 | 63 | 39.1676 | 81000 | 81000 | 7.49 | 3600 | 427.1788 |  | 2
115 | 85 | 63 | 29.0563 | 81000 | 81000 | 7.49 | 3600 | 427.1788 |  | 2
115 | 75 | 67 | 66.7494 | 73800 | 39852 | 7.45 | 1875 | 291.7318 |  | 2
115 | 80 | 67 | 51.5724 | 73800 | 48708 | 7.45 | 1875 | 291.7318 |  | 2
115 | 85 | 67 | 39.6049 | 73800 | 59778 | 7.45 | 1875 | 291.7318 |  | 2
115 | 75 | 67 | 66.7494 | 78700 | 46433 | 7.48 | 2625 | 291.7318 |  | 2
115 | 80 | 67 | 51.5724 | 78700 | 59025 | 7.48 | 2625 | 291.7318 |  | 2
115 | 85 | 67 | 39.6049 | 78700 | 73978 | 7.48 | 2625 | 291.7318 |  | 2
115 | 75 | 67 | 66.7494 | 82400 | 53560 | 7.5 | 3600 | 427.1788 |  | 2
115 | 80 | 67 | 51.5724 | 82400 | 74160 | 7.5 | 3600 | 427.1788 |  | 2
115 | 85 | 67 | 39.6049 | 82400 | 82400 | 7.5 | 3600 | 427.1788 |  | 2
115 | 75 | 71 | 82.6659 | 77600 | 31816 | 7.48 | 1875 | 291.7318 |  | 2
115 | 80 | 71 | 65.0618 | 77600 | 41128 | 7.48 | 1875 | 291.7318 |  | 2
115 | 85 | 71 | 51.076 | 77600 | 49664 | 7.48 | 1875 | 291.7318 |  | 2
115 | 75 | 71 | 82.6659 | 82800 | 35604 | 7.5 | 2625 | 291.7318 |  | 2
115 | 80 | 71 | 65.0618 | 82800 | 48024 | 7.5 | 2625 | 291.7318 |  | 2
115 | 85 | 71 | 51.076 | 82800 | 59616 | 7.5 | 2625 | 291.7318 |  | 2
115 | 75 | 71 | 82.6659 | 86700 | 39882 | 7.52 | 3600 | 427.1788 |  | 2
115 | 80 | 71 | 65.0618 | 86700 | 57222 | 7.52 | 3600 | 427.1788 |  | 2
115 | 85 | 71 | 51.076 | 86700 | 74562 | 7.52 | 3600 | 427.1788 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 8
Degradation Coefficient (C_d)
IEER or SEER | 21
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 75 | 63 | 52.1129 | 70600 | 38124 | 4.03 | 800 | 291.7318 |  | 1
65 | 80 | 63 | 39.1676 | 70600 | 43066 | 4.03 | 800 | 291.7318 |  | 1
65 | 85 | 63 | 29.0563 | 70600 | 49420 | 4.03 | 800 | 291.7318 |  | 1
65 | 75 | 63 | 52.1129 | 89000 | 53400 | 4.05 | 1465 | 291.7318 |  | 1
65 | 80 | 63 | 39.1676 | 89000 | 61410 | 4.05 | 1465 | 291.7318 |  | 1
65 | 85 | 63 | 29.0563 | 89000 | 69420 | 4.05 | 1465 | 291.7318 |  | 1
65 | 75 | 63 | 52.1129 | 99300 | 62559 | 4.08 | 2125 | 291.7318 |  | 1
65 | 80 | 63 | 39.1676 | 99300 | 75468 | 4.08 | 2125 | 291.7318 |  | 1
65 | 85 | 63 | 29.0563 | 99300 | 87384 | 4.08 | 2125 | 291.7318 |  | 1
65 | 75 | 67 | 66.7494 | 74600 | 36554 | 4.02 | 800 | 291.7318 |  | 1
65 | 80 | 67 | 51.5724 | 74600 | 40284 | 4.02 | 800 | 291.7318 |  | 1
65 | 85 | 67 | 39.6049 | 74600 | 44014 | 4.02 | 800 | 291.7318 |  | 1
65 | 75 | 67 | 66.7494 | 93800 | 45962 | 4.06 | 1465 | 291.7318 |  | 1
65 | 80 | 67 | 51.5724 | 93800 | 53466 | 4.06 | 1465 | 291.7318 |  | 1
65 | 85 | 67 | 39.6049 | 93800 | 61908 | 4.06 | 1465 | 291.7318 |  | 1
65 | 75 | 67 | 66.7494 | 104900 | 53499 | 4.1 | 2125 | 291.7318 |  | 1
65 | 80 | 67 | 51.5724 | 104900 | 63989 | 4.1 | 2125 | 291.7318 |  | 1
65 | 85 | 67 | 39.6049 | 104900 | 75528 | 4.1 | 2125 | 291.7318 |  | 1
65 | 75 | 71 | 82.6659 | 78600 | 31440 | 4.02 | 800 | 291.7318 |  | 1
65 | 80 | 71 | 65.0618 | 78600 | 38514 | 4.02 | 800 | 291.7318 |  | 1
65 | 85 | 71 | 51.076 | 78600 | 41658 | 4.02 | 800 | 291.7318 |  | 1
65 | 75 | 71 | 82.6659 | 98600 | 39440 | 4.08 | 1465 | 291.7318 |  | 1
65 | 80 | 71 | 65.0618 | 98600 | 46342 | 4.08 | 1465 | 291.7318 |  | 1
65 | 85 | 71 | 51.076 | 98600 | 53244 | 4.08 | 1465 | 291.7318 |  | 1
65 | 75 | 71 | 82.6659 | 110400 | 44160 | 4.11 | 2125 | 333.4078 |  | 1
65 | 80 | 71 | 65.0618 | 110400 | 54096 | 4.11 | 2125 | 333.4078 |  | 1
65 | 85 | 71 | 51.076 | 110400 | 65136 | 4.11 | 2125 | 333.4078 |  | 1
75 | 75 | 63 | 52.1129 | 68600 | 37730 | 4.67 | 800 | 250.0559 |  | 1
75 | 80 | 63 | 39.1676 | 68600 | 43218 | 4.67 | 800 | 250.0559 |  | 1
75 | 85 | 63 | 29.0563 | 68600 | 48020 | 4.67 | 800 | 250.0559 |  | 1
75 | 75 | 63 | 52.1129 | 86100 | 51660 | 4.71 | 1465 | 291.7318 |  | 1
75 | 80 | 63 | 39.1676 | 86100 | 60270 | 4.71 | 1465 | 291.7318 |  | 1
75 | 85 | 63 | 29.0563 | 86100 | 68019 | 4.71 | 1465 | 291.7318 |  | 1
75 | 75 | 63 | 52.1129 | 95800 | 61312 | 4.74 | 2125 | 291.7318 |  | 1
75 | 80 | 63 | 39.1676 | 95800 | 73766 | 4.74 | 2125 | 291.7318 |  | 1
75 | 85 | 63 | 29.0563 | 95800 | 85262 | 4.74 | 2125 | 291.7318 |  | 1
75 | 75 | 67 | 66.7494 | 72200 | 34656 | 4.68 | 800 | 291.7318 |  | 1
75 | 80 | 67 | 51.5724 | 72200 | 38988 | 4.68 | 800 | 291.7318 |  | 1
75 | 85 | 67 | 39.6049 | 72200 | 42598 | 4.68 | 800 | 291.7318 |  | 1
75 | 75 | 67 | 66.7494 | 90800 | 45400 | 4.72 | 1465 | 291.7318 |  | 1
75 | 80 | 67 | 51.5724 | 90800 | 52664 | 4.72 | 1465 | 291.7318 |  | 1
75 | 85 | 67 | 39.6049 | 90800 | 59928 | 4.72 | 1465 | 291.7318 |  | 1
75 | 75 | 67 | 66.7494 | 101300 | 51663 | 4.75 | 2125 | 291.7318 |  | 1
75 | 80 | 67 | 51.5724 | 101300 | 62806 | 4.75 | 2125 | 291.7318 |  | 1
75 | 85 | 67 | 39.6049 | 101300 | 74962 | 4.75 | 2125 | 291.7318 |  | 1
75 | 75 | 71 | 82.6659 | 75900 | 32637 | 4.68 | 800 | 291.7318 |  | 1
75 | 80 | 71 | 65.0618 | 75900 | 36432 | 4.68 | 800 | 291.7318 |  | 1
75 | 85 | 71 | 51.076 | 75900 | 40227 | 4.68 | 800 | 291.7318 |  | 1
75 | 75 | 71 | 82.6659 | 95500 | 37245 | 4.74 | 1465 | 291.7318 |  | 1
75 | 80 | 71 | 65.0618 | 95500 | 45840 | 4.74 | 1465 | 291.7318 |  | 1
75 | 85 | 71 | 51.076 | 95500 | 52525 | 4.74 | 1465 | 291.7318 |  | 1
75 | 75 | 71 | 82.6659 | 106500 | 42600 | 4.77 | 2125 | 333.4078 |  | 1
75 | 80 | 71 | 65.0618 | 106500 | 53250 | 4.77 | 2125 | 333.4078 |  | 1
75 | 85 | 71 | 51.076 | 106500 | 62835 | 4.77 | 2125 | 333.4078 |  | 1
85 | 75 | 63 | 52.1129 | 66200 | 37734 | 5.34 | 800 | 250.0559 |  | 1
85 | 80 | 63 | 39.1676 | 66200 | 41706 | 5.34 | 800 | 250.0559 |  | 1
85 | 85 | 63 | 29.0563 | 66200 | 46340 | 5.34 | 800 | 250.0559 |  | 1
85 | 75 | 63 | 52.1129 | 83100 | 50691 | 5.39 | 1465 | 291.7318 |  | 1
85 | 80 | 63 | 39.1676 | 83100 | 58170 | 5.39 | 1465 | 291.7318 |  | 1
85 | 85 | 63 | 29.0563 | 83100 | 67311 | 5.39 | 1465 | 291.7318 |  | 1
85 | 75 | 63 | 52.1129 | 92100 | 59865 | 5.41 | 2125 | 291.7318 |  | 1
85 | 80 | 63 | 39.1676 | 92100 | 71838 | 5.41 | 2125 | 291.7318 |  | 1
85 | 85 | 63 | 29.0563 | 92100 | 82890 | 5.41 | 2125 | 291.7318 |  | 1
85 | 75 | 67 | 66.7494 | 69700 | 35547 | 5.35 | 800 | 250.0559 |  | 1
85 | 80 | 67 | 51.5724 | 69700 | 39032 | 5.35 | 800 | 250.0559 |  | 1
85 | 85 | 67 | 39.6049 | 69700 | 43214 | 5.35 | 800 | 250.0559 |  | 1
85 | 75 | 67 | 66.7494 | 87700 | 43850 | 5.4 | 1465 | 291.7318 |  | 1
85 | 80 | 67 | 51.5724 | 87700 | 50866 | 5.4 | 1465 | 291.7318 |  | 1
85 | 85 | 67 | 39.6049 | 87700 | 58759 | 5.4 | 1465 | 291.7318 |  | 1
85 | 75 | 67 | 66.7494 | 97300 | 50596 | 5.43 | 2125 | 291.7318 |  | 1
85 | 80 | 67 | 51.5724 | 97300 | 62272 | 5.43 | 2125 | 291.7318 |  | 1
85 | 85 | 67 | 39.6049 | 97300 | 72975 | 5.43 | 2125 | 291.7318 |  | 1
85 | 75 | 71 | 82.6659 | 72900 | 30618 | 5.35 | 800 | 291.7318 |  | 1
85 | 80 | 71 | 65.0618 | 72900 | 34263 | 5.35 | 800 | 291.7318 |  | 1
85 | 85 | 71 | 51.076 | 72900 | 37908 | 5.35 | 800 | 291.7318 |  | 1
85 | 75 | 71 | 82.6659 | 92100 | 36840 | 5.42 | 1465 | 291.7318 |  | 1
85 | 80 | 71 | 65.0618 | 92100 | 44208 | 5.42 | 1465 | 291.7318 |  | 1
85 | 85 | 71 | 51.076 | 92100 | 50655 | 5.42 | 1465 | 291.7318 |  | 1
85 | 75 | 71 | 82.6659 | 102300 | 40920 | 5.46 | 2125 | 291.7318 |  | 1
85 | 80 | 71 | 65.0618 | 102300 | 52173 | 5.46 | 2125 | 291.7318 |  | 1
85 | 85 | 71 | 51.076 | 102300 | 62403 | 5.46 | 2125 | 291.7318 |  | 1
95 | 75 | 63 | 52.1129 | 63900 | 35784 | 6.07 | 800 | 250.0559 |  | 1
95 | 80 | 63 | 39.1676 | 63900 | 40896 | 6.07 | 800 | 250.0559 |  | 1
95 | 85 | 63 | 29.0563 | 63900 | 45369 | 6.07 | 800 | 250.0559 |  | 1
95 | 75 | 63 | 52.1129 | 79600 | 49352 | 6.12 | 1465 | 291.7318 |  | 1
95 | 80 | 63 | 39.1676 | 79600 | 57312 | 6.12 | 1465 | 291.7318 |  | 1
95 | 85 | 63 | 29.0563 | 79600 | 65272 | 6.12 | 1465 | 291.7318 |  | 1
95 | 75 | 63 | 52.1129 | 88000 | 58080 | 6.15 | 2125 | 291.7318 |  | 1
95 | 80 | 63 | 39.1676 | 88000 | 71280 | 6.15 | 2125 | 291.7318 |  | 1
95 | 85 | 63 | 29.0563 | 88000 | 81840 | 6.15 | 2125 | 291.7318 |  | 1
95 | 75 | 67 | 66.7494 | 67400 | 33700 | 6.07 | 800 | 250.0559 |  | 1
95 | 80 | 67 | 51.5724 | 67400 | 37744 | 6.07 | 800 | 250.0559 |  | 1
95 | 85 | 67 | 39.6049 | 67400 | 41788 | 6.07 | 800 | 250.0559 |  | 1
95 | 75 | 67 | 66.7494 | 84100 | 42050 | 6.14 | 1465 | 291.7318 |  | 1
95 | 80 | 67 | 51.5724 | 84100 | 49619 | 6.14 | 1465 | 291.7318 |  | 1
95 | 85 | 67 | 39.6049 | 84100 | 57188 | 6.14 | 1465 | 291.7318 |  | 1
95 | 75 | 67 | 66.7494 | 92900 | 48308 | 6.17 | 2125 | 291.7318 |  | 1
95 | 80 | 67 | 51.5724 | 92900 | 59456 | 6.17 | 2125 | 291.7318 |  | 1
95 | 85 | 67 | 39.6049 | 92900 | 70604 | 6.17 | 2125 | 291.7318 |  | 1
95 | 75 | 71 | 82.6659 | 70400 | 28864 | 6.09 | 800 | 250.0559 |  | 1
95 | 80 | 71 | 65.0618 | 70400 | 33088 | 6.09 | 800 | 250.0559 |  | 1
95 | 85 | 71 | 51.076 | 70400 | 36608 | 6.09 | 800 | 250.0559 |  | 1
95 | 75 | 71 | 82.6659 | 88300 | 35320 | 6.16 | 1465 | 291.7318 |  | 1
95 | 80 | 71 | 65.0618 | 88300 | 41501 | 6.16 | 1465 | 291.7318 |  | 1
95 | 85 | 71 | 51.076 | 88300 | 49448 | 6.16 | 1465 | 291.7318 |  | 1
95 | 75 | 71 | 82.6659 | 97800 | 39120 | 6.2 | 2125 | 291.7318 |  | 1
95 | 80 | 71 | 65.0618 | 97800 | 49878 | 6.2 | 2125 | 291.7318 |  | 1
95 | 85 | 71 | 51.076 | 97800 | 59658 | 6.2 | 2125 | 291.7318 |  | 1
85 | 75 | 63 | 52.1129 | 92100 | 58944 | 5.41 | 2125 | 291.7318 |  | 2
85 | 80 | 63 | 39.1676 | 92100 | 70917 | 5.41 | 2125 | 291.7318 |  | 2
85 | 85 | 63 | 29.0563 | 92100 | 82890 | 5.41 | 2125 | 291.7318 |  | 2
85 | 75 | 63 | 52.1129 | 99200 | 71424 | 5.44 | 2975 | 333.4078 |  | 2
85 | 80 | 63 | 39.1676 | 99200 | 87296 | 5.44 | 2975 | 333.4078 |  | 2
85 | 85 | 63 | 29.0563 | 99200 | 99200 | 5.44 | 2975 | 333.4078 |  | 2
85 | 75 | 63 | 52.1129 | 106100 | 85941 | 5.46 | 4080 | 583.4637 |  | 2
85 | 80 | 63 | 39.1676 | 106100 | 106100 | 5.46 | 4080 | 583.4637 |  | 2
85 | 85 | 63 | 29.0563 | 106100 | 106100 | 5.46 | 4080 | 583.4637 |  | 2
85 | 75 | 67 | 66.7494 | 97300 | 50596 | 5.43 | 2125 | 291.7318 |  | 2
85 | 80 | 67 | 51.5724 | 97300 | 61299 | 5.43 | 2125 | 291.7318 |  | 2
85 | 85 | 67 | 39.6049 | 97300 | 72002 | 5.43 | 2125 | 291.7318 |  | 2
85 | 75 | 67 | 66.7494 | 104600 | 58576 | 5.46 | 2975 | 333.4078 |  | 2
85 | 80 | 67 | 51.5724 | 104600 | 72174 | 5.46 | 2975 | 333.4078 |  | 2
85 | 85 | 67 | 39.6049 | 104600 | 88910 | 5.46 | 2975 | 333.4078 |  | 2
85 | 75 | 67 | 66.7494 | 110400 | 67344 | 5.49 | 4080 | 583.4637 |  | 2
85 | 80 | 67 | 51.5724 | 110400 | 86112 | 5.49 | 4080 | 583.4637 |  | 2
85 | 85 | 67 | 39.6049 | 110400 | 108192 | 5.49 | 4080 | 583.4637 |  | 2
85 | 75 | 71 | 82.6659 | 102300 | 40920 | 5.46 | 2125 | 291.7318 |  | 2
85 | 80 | 71 | 65.0618 | 102300 | 52173 | 5.46 | 2125 | 291.7318 |  | 2
85 | 85 | 71 | 51.076 | 102300 | 61380 | 5.46 | 2125 | 291.7318 |  | 2
85 | 75 | 71 | 82.6659 | 110100 | 46242 | 5.49 | 2975 | 375.0838 |  | 2
85 | 80 | 71 | 65.0618 | 110100 | 60555 | 5.49 | 2975 | 375.0838 |  | 2
85 | 85 | 71 | 51.076 | 110100 | 73767 | 5.49 | 2975 | 375.0838 |  | 2
85 | 75 | 71 | 82.6659 | 116100 | 52245 | 5.51 | 4080 | 583.4637 |  | 2
85 | 80 | 71 | 65.0618 | 116100 | 68499 | 5.51 | 4080 | 583.4637 |  | 2
85 | 85 | 71 | 51.076 | 116100 | 91719 | 5.51 | 4080 | 583.4637 |  | 2
95 | 75 | 63 | 52.1129 | 88000 | 57200 | 6.15 | 2125 | 291.7318 |  | 2
95 | 80 | 63 | 39.1676 | 88000 | 69520 | 6.15 | 2125 | 291.7318 |  | 2
95 | 85 | 63 | 29.0563 | 88000 | 80960 | 6.15 | 2125 | 291.7318 |  | 2
95 | 75 | 63 | 52.1129 | 94800 | 70152 | 6.17 | 2975 | 333.4078 |  | 2
95 | 80 | 63 | 39.1676 | 94800 | 86268 | 6.17 | 2975 | 333.4078 |  | 2
95 | 85 | 63 | 29.0563 | 94800 | 94800 | 6.17 | 2975 | 333.4078 |  | 2
95 | 75 | 63 | 52.1129 | 101400 | 84162 | 6.21 | 4080 | 520.9497 |  | 2
95 | 80 | 63 | 39.1676 | 101400 | 101400 | 6.21 | 4080 | 520.9497 |  | 2
95 | 85 | 63 | 29.0563 | 101400 | 101400 | 6.21 | 4080 | 520.9497 |  | 2
95 | 75 | 67 | 66.7494 | 92900 | 48308 | 6.17 | 2125 | 291.7318 |  | 2
95 | 80 | 67 | 51.5724 | 92900 | 58527 | 6.17 | 2125 | 291.7318 |  | 2
95 | 85 | 67 | 39.6049 | 92900 | 69675 | 6.17 | 2125 | 291.7318 |  | 2
95 | 75 | 67 | 66.7494 | 99500 | 56715 | 6.2 | 2975 | 333.4078 |  | 2
95 | 80 | 67 | 51.5724 | 99500 | 69650 | 6.2 | 2975 | 333.4078 |  | 2
95 | 85 | 67 | 39.6049 | 99500 | 86565 | 6.2 | 2975 | 333.4078 |  | 2
95 | 75 | 67 | 66.7494 | 104600 | 64852 | 6.22 | 4080 | 520.9497 |  | 2
95 | 80 | 67 | 51.5724 | 104600 | 84726 | 6.22 | 4080 | 520.9497 |  | 2
95 | 85 | 67 | 39.6049 | 104600 | 104600 | 6.22 | 4080 | 520.9497 |  | 2
95 | 75 | 71 | 82.6659 | 97800 | 39120 | 6.2 | 2125 | 291.7318 |  | 2
95 | 80 | 71 | 65.0618 | 97800 | 49878 | 6.2 | 2125 | 291.7318 |  | 2
95 | 85 | 71 | 51.076 | 97800 | 59658 | 6.2 | 2125 | 291.7318 |  | 2
95 | 75 | 71 | 82.6659 | 104900 | 44058 | 6.22 | 2975 | 333.4078 |  | 2
95 | 80 | 71 | 65.0618 | 104900 | 57695 | 6.22 | 2975 | 333.4078 |  | 2
95 | 85 | 71 | 51.076 | 104900 | 71332 | 6.22 | 2975 | 333.4078 |  | 2
95 | 75 | 71 | 82.6659 | 110300 | 48532 | 6.25 | 4080 | 583.4637 |  | 2
95 | 80 | 71 | 65.0618 | 110300 | 67283 | 6.25 | 4080 | 583.4637 |  | 2
95 | 85 | 71 | 51.076 | 110300 | 87137 | 6.25 | 4080 | 583.4637 |  | 2
105 | 75 | 63 | 52.1129 | 83300 | 55811 | 6.98 | 2125 | 291.7318 |  | 2
105 | 80 | 63 | 39.1676 | 83300 | 68306 | 6.98 | 2125 | 291.7318 |  | 2
105 | 85 | 63 | 29.0563 | 83300 | 79135 | 6.98 | 2125 | 291.7318 |  | 2
105 | 75 | 63 | 52.1129 | 89800 | 69146 | 7.01 | 2975 | 333.4078 |  | 2
105 | 80 | 63 | 39.1676 | 89800 | 84412 | 7.01 | 2975 | 333.4078 |  | 2
105 | 85 | 63 | 29.0563 | 89800 | 89800 | 7.01 | 2975 | 333.4078 |  | 2
105 | 75 | 63 | 52.1129 | 96400 | 83868 | 7.04 | 4080 | 520.9497 |  | 2
105 | 80 | 63 | 39.1676 | 96400 | 96400 | 7.04 | 4080 | 520.9497 |  | 2
105 | 85 | 63 | 29.0563 | 96400 | 96400 | 7.04 | 4080 | 520.9497 |  | 2
105 | 75 | 67 | 66.7494 | 88000 | 46640 | 7.01 | 2125 | 291.7318 |  | 2
105 | 80 | 67 | 51.5724 | 88000 | 57200 | 7.01 | 2125 | 291.7318 |  | 2
105 | 85 | 67 | 39.6049 | 88000 | 68640 | 7.01 | 2125 | 291.7318 |  | 2
105 | 75 | 67 | 66.7494 | 94000 | 54520 | 7.03 | 2975 | 333.4078 |  | 2
105 | 80 | 67 | 51.5724 | 94000 | 68620 | 7.03 | 2975 | 333.4078 |  | 2
105 | 85 | 67 | 39.6049 | 94000 | 84600 | 7.03 | 2975 | 333.4078 |  | 2
105 | 75 | 67 | 66.7494 | 98500 | 63040 | 7.05 | 4080 | 520.9497 |  | 2
105 | 80 | 67 | 51.5724 | 98500 | 85695 | 7.05 | 4080 | 520.9497 |  | 2
105 | 85 | 67 | 39.6049 | 98500 | 98500 | 7.05 | 4080 | 520.9497 |  | 2
105 | 75 | 71 | 82.6659 | 92600 | 37040 | 7.03 | 2125 | 291.7318 |  | 2
105 | 80 | 71 | 65.0618 | 92600 | 48152 | 7.03 | 2125 | 291.7318 |  | 2
105 | 85 | 71 | 51.076 | 92600 | 58338 | 7.03 | 2125 | 291.7318 |  | 2
105 | 75 | 71 | 82.6659 | 99000 | 41580 | 7.06 | 2975 | 333.4078 |  | 2
105 | 80 | 71 | 65.0618 | 99000 | 56430 | 7.06 | 2975 | 333.4078 |  | 2
105 | 85 | 71 | 51.076 | 99000 | 69300 | 7.06 | 2975 | 333.4078 |  | 2
105 | 75 | 71 | 82.6659 | 103900 | 47794 | 7.08 | 4080 | 520.9497 |  | 2
105 | 80 | 71 | 65.0618 | 103900 | 64418 | 7.08 | 4080 | 520.9497 |  | 2
105 | 85 | 71 | 51.076 | 103900 | 88315 | 7.08 | 4080 | 520.9497 |  | 2
115 | 75 | 63 | 52.1129 | 78000 | 53820 | 7.93 | 2125 | 291.7318 |  | 2
115 | 80 | 63 | 39.1676 | 78000 | 65520 | 7.93 | 2125 | 291.7318 |  | 2
115 | 85 | 63 | 29.0563 | 78000 | 76440 | 7.93 | 2125 | 291.7318 |  | 2
115 | 75 | 63 | 52.1129 | 84100 | 65598 | 7.96 | 2975 | 333.4078 |  | 2
115 | 80 | 63 | 39.1676 | 84100 | 81577 | 7.96 | 2975 | 333.4078 |  | 2
115 | 85 | 63 | 29.0563 | 84100 | 84100 | 7.96 | 2975 | 333.4078 |  | 2
115 | 75 | 63 | 52.1129 | 90400 | 83168 | 7.99 | 4080 | 520.9497 |  | 2
115 | 80 | 63 | 39.1676 | 90400 | 90400 | 7.99 | 4080 | 520.9497 |  | 2
115 | 85 | 63 | 29.0563 | 90400 | 90400 | 7.99 | 4080 | 520.9497 |  | 2
115 | 75 | 67 | 66.7494 | 82400 | 44496 | 7.95 | 2125 | 291.7318 |  | 2
115 | 80 | 67 | 51.5724 | 82400 | 54384 | 7.95 | 2125 | 291.7318 |  | 2
115 | 85 | 67 | 39.6049 | 82400 | 65920 | 7.95 | 2125 | 291.7318 |  | 2
115 | 75 | 67 | 66.7494 | 87700 | 50866 | 7.99 | 2975 | 333.4078 |  | 2
115 | 80 | 67 | 51.5724 | 87700 | 67529 | 7.99 | 2975 | 333.4078 |  | 2
115 | 85 | 67 | 39.6049 | 87700 | 82438 | 7.99 | 2975 | 333.4078 |  | 2
115 | 75 | 67 | 66.7494 | 91600 | 60456 | 8 | 4080 | 520.9497 |  | 2
115 | 80 | 67 | 51.5724 | 91600 | 81524 | 8 | 4080 | 520.9497 |  | 2
115 | 85 | 67 | 39.6049 | 91600 | 91600 | 8 | 4080 | 520.9497 |  | 2
115 | 75 | 71 | 82.6659 | 86900 | 34760 | 7.98 | 2125 | 291.7318 |  | 2
115 | 80 | 71 | 65.0618 | 86900 | 46057 | 7.98 | 2125 | 291.7318 |  | 2
115 | 85 | 71 | 51.076 | 86900 | 55616 | 7.98 | 2125 | 291.7318 |  | 2
115 | 75 | 71 | 82.6659 | 92400 | 39732 | 8.01 | 2975 | 333.4078 |  | 2
115 | 80 | 71 | 65.0618 | 92400 | 53592 | 8.01 | 2975 | 333.4078 |  | 2
115 | 85 | 71 | 51.076 | 92400 | 68376 | 8.01 | 2975 | 333.4078 |  | 2
115 | 75 | 71 | 82.6659 | 96500 | 43425 | 8.03 | 4080 | 520.9497 |  | 2
115 | 80 | 71 | 65.0618 | 96500 | 61760 | 8.03 | 4080 | 520.9497 |  | 2
115 | 85 | 71 | 51.076 | 96500 | 83955 | 8.03 | 4080 | 520.9497 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 9
Degradation Coefficient (C_d)
IEER or SEER | 21
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 75 | 63 | 52.1129 | 80000 | 44000 | 5.13 | 875 | 291.7318 |  | 1
65 | 80 | 63 | 39.1676 | 80000 | 49600 | 5.13 | 875 | 291.7318 |  | 1
65 | 85 | 63 | 29.0563 | 80000 | 54400 | 5.13 | 875 | 291.7318 |  | 1
65 | 75 | 63 | 52.1129 | 103700 | 62220 | 5.21 | 1650 | 291.7318 |  | 1
65 | 80 | 63 | 39.1676 | 103700 | 71553 | 5.21 | 1650 | 291.7318 |  | 1
65 | 85 | 63 | 29.0563 | 103700 | 80886 | 5.21 | 1650 | 291.7318 |  | 1
65 | 75 | 63 | 52.1129 | 117800 | 75392 | 5.26 | 2500 | 333.4078 |  | 1
65 | 80 | 63 | 39.1676 | 117800 | 88350 | 5.26 | 2500 | 333.4078 |  | 1
65 | 85 | 63 | 29.0563 | 117800 | 101308 | 5.26 | 2500 | 333.4078 |  | 1
65 | 75 | 67 | 66.7494 | 84700 | 39809 | 5.13 | 875 | 291.7318 |  | 1
65 | 80 | 67 | 51.5724 | 84700 | 44891 | 5.13 | 875 | 291.7318 |  | 1
65 | 85 | 67 | 39.6049 | 84700 | 49126 | 5.13 | 875 | 291.7318 |  | 1
65 | 75 | 67 | 66.7494 | 109300 | 54650 | 5.23 | 1650 | 333.4078 |  | 1
65 | 80 | 67 | 51.5724 | 109300 | 62301 | 5.23 | 1650 | 333.4078 |  | 1
65 | 85 | 67 | 39.6049 | 109300 | 71045 | 5.23 | 1650 | 333.4078 |  | 1
65 | 75 | 67 | 66.7494 | 124500 | 63495 | 5.29 | 2500 | 333.4078 |  | 1
65 | 80 | 67 | 51.5724 | 124500 | 75945 | 5.29 | 2500 | 333.4078 |  | 1
65 | 85 | 67 | 39.6049 | 124500 | 88395 | 5.29 | 2500 | 333.4078 |  | 1
65 | 75 | 71 | 82.6659 | 89600 | 36736 | 5.15 | 875 | 291.7318 |  | 1
65 | 80 | 71 | 65.0618 | 89600 | 42112 | 5.15 | 875 | 291.7318 |  | 1
65 | 85 | 71 | 51.076 | 89600 | 46592 | 5.15 | 875 | 291.7318 |  | 1
65 | 75 | 71 | 82.6659 | 115000 | 46000 | 5.25 | 1650 | 333.4078 |  | 1
65 | 80 | 71 | 65.0618 | 115000 | 55200 | 5.25 | 1650 | 333.4078 |  | 1
65 | 85 | 71 | 51.076 | 115000 | 62100 | 5.25 | 1650 | 333.4078 |  | 1
65 | 75 | 71 | 82.6659 | 131000 | 52400 | 5.3 | 2500 | 333.4078 |  | 1
65 | 80 | 71 | 65.0618 | 131000 | 65500 | 5.3 | 2500 | 333.4078 |  | 1
65 | 85 | 71 | 51.076 | 131000 | 75980 | 5.3 | 2500 | 333.4078 |  | 1
75 | 75 | 63 | 52.1129 | 78100 | 43736 | 5.8 | 875 | 291.7318 |  | 1
75 | 80 | 63 | 39.1676 | 78100 | 48422 | 5.8 | 875 | 291.7318 |  | 1
75 | 85 | 63 | 29.0563 | 78100 | 53889 | 5.8 | 875 | 291.7318 |  | 1
75 | 75 | 63 | 52.1129 | 100600 | 60360 | 5.89 | 1650 | 291.7318 |  | 1
75 | 80 | 63 | 39.1676 | 100600 | 69414 | 5.89 | 1650 | 291.7318 |  | 1
75 | 85 | 63 | 29.0563 | 100600 | 78468 | 5.89 | 1650 | 291.7318 |  | 1
75 | 75 | 63 | 52.1129 | 114100 | 74165 | 5.94 | 2500 | 333.4078 |  | 1
75 | 80 | 63 | 39.1676 | 114100 | 87857 | 5.94 | 2500 | 333.4078 |  | 1
75 | 85 | 63 | 29.0563 | 114100 | 100408 | 5.94 | 2500 | 333.4078 |  | 1
75 | 75 | 67 | 66.7494 | 82700 | 38869 | 5.82 | 875 | 291.7318 |  | 1
75 | 80 | 67 | 51.5724 | 82700 | 43004 | 5.82 | 875 | 291.7318 |  | 1
75 | 85 | 67 | 39.6049 | 82700 | 49620 | 5.82 | 875 | 291.7318 |  | 1
75 | 75 | 67 | 66.7494 | 106200 | 53100 | 5.92 | 1650 | 333.4078 |  | 1
75 | 80 | 67 | 51.5724 | 106200 | 60534 | 5.92 | 1650 | 333.4078 |  | 1
75 | 85 | 67 | 39.6049 | 106200 | 70092 | 5.92 | 1650 | 333.4078 |  | 1
75 | 75 | 67 | 66.7494 | 120500 | 61455 | 5.98 | 2500 | 333.4078 |  | 1
75 | 80 | 67 | 51.5724 | 120500 | 74710 | 5.98 | 2500 | 333.4078 |  | 1
75 | 85 | 67 | 39.6049 | 120500 | 86760 | 5.98 | 2500 | 333.4078 |  | 1
75 | 75 | 71 | 82.6659 | 87600 | 35916 | 5.83 | 875 | 291.7318 |  | 1
75 | 80 | 71 | 65.0618 | 87600 | 40296 | 5.83 | 875 | 291.7318 |  | 1
75 | 85 | 71 | 51.076 | 87600 | 47304 | 5.83 | 875 | 291.7318 |  | 1
75 | 75 | 71 | 82.6659 | 111700 | 44680 | 5.94 | 1650 | 333.4078 |  | 1
75 | 80 | 71 | 65.0618 | 111700 | 52499 | 5.94 | 1650 | 333.4078 |  | 1
75 | 85 | 71 | 51.076 | 111700 | 61435 | 5.94 | 1650 | 333.4078 |  | 1
75 | 75 | 71 | 82.6659 | 126800 | 51988 | 6 | 2500 | 333.4078 |  | 1
75 | 80 | 71 | 65.0618 | 126800 | 62132 | 6 | 2500 | 333.4078 |  | 1
75 | 85 | 71 | 51.076 | 126800 | 74812 | 6 | 2500 | 333.4078 |  | 1
85 | 75 | 63 | 52.1129 | 76100 | 41855 | 6.59 | 875 | 291.7318 |  | 1
85 | 80 | 63 | 39.1676 | 76100 | 48704 | 6.59 | 875 | 291.7318 |  | 1
85 | 85 | 63 | 29.0563 | 76100 | 53270 | 6.59 | 875 | 291.7318 |  | 1
85 | 75 | 63 | 52.1129 | 97300 | 58380 | 6.69 | 1650 | 291.7318 |  | 1
85 | 80 | 63 | 39.1676 | 97300 | 68110 | 6.69 | 1650 | 291.7318 |  | 1
85 | 85 | 63 | 29.0563 | 97300 | 76867 | 6.69 | 1650 | 291.7318 |  | 1
85 | 75 | 63 | 52.1129 | 110000 | 72600 | 6.75 | 2500 | 333.4078 |  | 1
85 | 80 | 63 | 39.1676 | 110000 | 84700 | 6.75 | 2500 | 333.4078 |  | 1
85 | 85 | 63 | 29.0563 | 110000 | 97900 | 6.75 | 2500 | 333.4078 |  | 1
85 | 75 | 67 | 66.7494 | 80500 | 37030 | 6.61 | 875 | 291.7318 |  | 1
85 | 80 | 67 | 51.5724 | 80500 | 44275 | 6.61 | 875 | 291.7318 |  | 1
85 | 85 | 67 | 39.6049 | 80500 | 48300 | 6.61 | 875 | 291.7318 |  | 1
85 | 75 | 67 | 66.7494 | 102700 | 51350 | 6.7 | 1650 | 291.7318 |  | 1
85 | 80 | 67 | 51.5724 | 102700 | 59566 | 6.7 | 1650 | 291.7318 |  | 1
85 | 85 | 67 | 39.6049 | 102700 | 67782 | 6.7 | 1650 | 291.7318 |  | 1
85 | 75 | 67 | 66.7494 | 116200 | 60424 | 6.78 | 2500 | 333.4078 |  | 1
85 | 80 | 67 | 51.5724 | 116200 | 73206 | 6.78 | 2500 | 333.4078 |  | 1
85 | 85 | 67 | 39.6049 | 116200 | 85988 | 6.78 | 2500 | 333.4078 |  | 1
85 | 75 | 71 | 82.6659 | 84900 | 34809 | 6.63 | 875 | 291.7318 |  | 1
85 | 80 | 71 | 65.0618 | 84900 | 41601 | 6.63 | 875 | 291.7318 |  | 1
85 | 85 | 71 | 51.076 | 84900 | 44997 | 6.63 | 875 | 291.7318 |  | 1
85 | 75 | 71 | 82.6659 | 108100 | 43240 | 6.74 | 1650 | 333.4078 |  | 1
85 | 80 | 71 | 65.0618 | 108100 | 51888 | 6.74 | 1650 | 333.4078 |  | 1
85 | 85 | 71 | 51.076 | 108100 | 59455 | 6.74 | 1650 | 333.4078 |  | 1
85 | 75 | 71 | 82.6659 | 122400 | 48960 | 6.81 | 2500 | 333.4078 |  | 1
85 | 80 | 71 | 65.0618 | 122400 | 61200 | 6.81 | 2500 | 333.4078 |  | 1
85 | 85 | 71 | 51.076 | 122400 | 73440 | 6.81 | 2500 | 333.4078 |  | 1
95 | 75 | 63 | 52.1129 | 73500 | 41160 | 7.5 | 875 | 291.7318 |  | 1
95 | 80 | 63 | 39.1676 | 73500 | 47040 | 7.5 | 875 | 291.7318 |  | 1
95 | 85 | 63 | 29.0563 | 73500 | 52185 | 7.5 | 875 | 291.7318 |  | 1
95 | 75 | 63 | 52.1129 | 93700 | 57157 | 7.59 | 1650 | 291.7318 |  | 1
95 | 80 | 63 | 39.1676 | 93700 | 65590 | 7.59 | 1650 | 291.7318 |  | 1
95 | 85 | 63 | 29.0563 | 93700 | 74960 | 7.59 | 1650 | 291.7318 |  | 1
95 | 75 | 63 | 52.1129 | 105400 | 69564 | 7.66 | 2500 | 291.7318 |  | 1
95 | 80 | 63 | 39.1676 | 105400 | 83266 | 7.66 | 2500 | 291.7318 |  | 1
95 | 85 | 63 | 29.0563 | 105400 | 95914 | 7.66 | 2500 | 291.7318 |  | 1
95 | 75 | 67 | 66.7494 | 77600 | 38024 | 7.51 | 875 | 291.7318 |  | 1
95 | 80 | 67 | 51.5724 | 77600 | 41904 | 7.51 | 875 | 291.7318 |  | 1
95 | 85 | 67 | 39.6049 | 77600 | 46560 | 7.51 | 875 | 291.7318 |  | 1
95 | 75 | 67 | 66.7494 | 98900 | 49450 | 7.63 | 1650 | 291.7318 |  | 1
95 | 80 | 67 | 51.5724 | 98900 | 57362 | 7.63 | 1650 | 291.7318 |  | 1
95 | 85 | 67 | 39.6049 | 98900 | 66263 | 7.63 | 1650 | 291.7318 |  | 1
95 | 75 | 67 | 66.7494 | 111500 | 59095 | 7.7 | 2500 | 333.4078 |  | 1
95 | 80 | 67 | 51.5724 | 111500 | 71360 | 7.7 | 2500 | 333.4078 |  | 1
95 | 85 | 67 | 39.6049 | 111500 | 84740 | 7.7 | 2500 | 333.4078 |  | 1
95 | 75 | 71 | 82.6659 | 81700 | 35131 | 7.53 | 875 | 291.7318 |  | 1
95 | 80 | 71 | 65.0618 | 81700 | 39216 | 7.53 | 875 | 291.7318 |  | 1
95 | 85 | 71 | 51.076 | 81700 | 43301 | 7.53 | 875 | 291.7318 |  | 1
95 | 75 | 71 | 82.6659 | 104100 | 41640 | 7.65 | 1650 | 291.7318 |  | 1
95 | 80 | 71 | 65.0618 | 104100 | 49968 | 7.65 | 1650 | 291.7318 |  | 1
95 | 85 | 71 | 51.076 | 104100 | 57255 | 7.65 | 1650 | 291.7318 |  | 1
95 | 75 | 71 | 82.6659 | 117500 | 47000 | 7.74 | 2500 | 333.4078 |  | 1
95 | 80 | 71 | 65.0618 | 117500 | 59925 | 7.74 | 2500 | 333.4078 |  | 1
95 | 85 | 71 | 51.076 | 117500 | 71675 | 7.74 | 2500 | 333.4078 |  | 1
85 | 75 | 63 | 52.1129 | 109600 | 70144 | 6.56 | 2500 | 333.4078 |  | 2
85 | 80 | 63 | 39.1676 | 109600 | 83296 | 6.56 | 2500 | 333.4078 |  | 2
85 | 85 | 63 | 29.0563 | 109600 | 97544 | 6.56 | 2500 | 333.4078 |  | 2
85 | 75 | 63 | 52.1129 | 118100 | 83851 | 6.63 | 3500 | 479.2737 |  | 2
85 | 80 | 63 | 39.1676 | 118100 | 101566 | 6.63 | 3500 | 479.2737 |  | 2
85 | 85 | 63 | 29.0563 | 118100 | 118100 | 6.63 | 3500 | 479.2737 |  | 2
85 | 75 | 63 | 52.1129 | 125900 | 100720 | 6.68 | 4800 | 771.0056 |  | 2
85 | 80 | 63 | 39.1676 | 125900 | 124641 | 6.68 | 4800 | 771.0056 |  | 2
85 | 85 | 63 | 29.0563 | 125900 | 125900 | 6.68 | 4800 | 771.0056 |  | 2
85 | 75 | 67 | 66.7494 | 115800 | 60216 | 6.61 | 2500 | 333.4078 |  | 2
85 | 80 | 67 | 51.5724 | 115800 | 71796 | 6.61 | 2500 | 333.4078 |  | 2
85 | 85 | 67 | 39.6049 | 115800 | 84534 | 6.61 | 2500 | 333.4078 |  | 2
85 | 75 | 67 | 66.7494 | 124800 | 69888 | 6.68 | 3500 | 479.2737 |  | 2
85 | 80 | 67 | 51.5724 | 124800 | 84864 | 6.68 | 3500 | 479.2737 |  | 2
85 | 85 | 67 | 39.6049 | 124800 | 103584 | 6.68 | 3500 | 479.2737 |  | 2
85 | 75 | 67 | 66.7494 | 131800 | 77762 | 6.73 | 4800 | 771.0056 |  | 2
85 | 80 | 67 | 51.5724 | 131800 | 101486 | 6.73 | 4800 | 771.0056 |  | 2
85 | 85 | 67 | 39.6049 | 131800 | 126528 | 6.73 | 4800 | 771.0056 |  | 2
85 | 75 | 71 | 82.6659 | 121800 | 48720 | 6.66 | 2500 | 333.4078 |  | 2
85 | 80 | 71 | 65.0618 | 121800 | 60900 | 6.66 | 2500 | 333.4078 |  | 2
85 | 85 | 71 | 51.076 | 121800 | 73080 | 6.66 | 2500 | 333.4078 |  | 2
85 | 75 | 71 | 82.6659 | 131400 | 53874 | 6.73 | 3500 | 479.2737 |  | 2
85 | 80 | 71 | 65.0618 | 131400 | 70956 | 6.73 | 3500 | 479.2737 |  | 2
85 | 85 | 71 | 51.076 | 131400 | 86724 | 6.73 | 3500 | 479.2737 |  | 2
85 | 75 | 71 | 82.6659 | 138700 | 59641 | 6.77 | 4800 | 843.9385 |  | 2
85 | 80 | 71 | 65.0618 | 138700 | 81833 | 6.77 | 4800 | 843.9385 |  | 2
85 | 85 | 71 | 51.076 | 138700 | 105412 | 6.77 | 4800 | 843.9385 |  | 2
95 | 75 | 63 | 52.1129 | 105000 | 68250 | 7.43 | 2500 | 291.7318 |  | 2
95 | 80 | 63 | 39.1676 | 105000 | 81900 | 7.43 | 2500 | 291.7318 |  | 2
95 | 85 | 63 | 29.0563 | 105000 | 95550 | 7.43 | 2500 | 291.7318 |  | 2
95 | 75 | 63 | 52.1129 | 112900 | 82417 | 7.5 | 3500 | 479.2737 |  | 2
95 | 80 | 63 | 39.1676 | 112900 | 100481 | 7.5 | 3500 | 479.2737 |  | 2
95 | 85 | 63 | 29.0563 | 112900 | 112900 | 7.5 | 3500 | 479.2737 |  | 2
95 | 75 | 63 | 52.1129 | 120500 | 98810 | 7.57 | 4800 | 771.0056 |  | 2
95 | 80 | 63 | 39.1676 | 120500 | 120500 | 7.57 | 4800 | 771.0056 |  | 2
95 | 85 | 63 | 29.0563 | 120500 | 120500 | 7.57 | 4800 | 771.0056 |  | 2
95 | 75 | 67 | 66.7494 | 111000 | 58830 | 7.49 | 2500 | 333.4078 |  | 2
95 | 80 | 67 | 51.5724 | 111000 | 69930 | 7.49 | 2500 | 333.4078 |  | 2
95 | 85 | 67 | 39.6049 | 111000 | 83250 | 7.49 | 2500 | 333.4078 |  | 2
95 | 75 | 67 | 66.7494 | 119200 | 67944 | 7.55 | 3500 | 479.2737 |  | 2
95 | 80 | 67 | 51.5724 | 119200 | 82248 | 7.55 | 3500 | 479.2737 |  | 2
95 | 85 | 67 | 39.6049 | 119200 | 101320 | 7.55 | 3500 | 479.2737 |  | 2
95 | 75 | 67 | 66.7494 | 125700 | 77934 | 7.61 | 4800 | 771.0056 |  | 2
95 | 80 | 67 | 51.5724 | 125700 | 101817 | 7.61 | 4800 | 771.0056 |  | 2
95 | 85 | 67 | 39.6049 | 125700 | 124443 | 7.61 | 4800 | 771.0056 |  | 2
95 | 75 | 71 | 82.6659 | 116900 | 47929 | 7.55 | 2500 | 333.4078 |  | 2
95 | 80 | 71 | 65.0618 | 116900 | 59619 | 7.55 | 2500 | 333.4078 |  | 2
95 | 85 | 71 | 51.076 | 116900 | 71309 | 7.55 | 2500 | 333.4078 |  | 2
95 | 75 | 71 | 82.6659 | 125600 | 52752 | 7.61 | 3500 | 479.2737 |  | 2
95 | 80 | 71 | 65.0618 | 125600 | 69080 | 7.61 | 3500 | 479.2737 |  | 2
95 | 85 | 71 | 51.076 | 125600 | 85408 | 7.61 | 3500 | 479.2737 |  | 2
95 | 75 | 71 | 82.6659 | 132400 | 59580 | 7.66 | 4800 | 771.0056 |  | 2
95 | 80 | 71 | 65.0618 | 132400 | 79440 | 7.66 | 4800 | 771.0056 |  | 2
95 | 85 | 71 | 51.076 | 132400 | 101948 | 7.66 | 4800 | 771.0056 |  | 2
105 | 75 | 63 | 52.1129 | 100200 | 66132 | 8.4 | 2500 | 291.7318 |  | 2
105 | 80 | 63 | 39.1676 | 100200 | 80160 | 8.4 | 2500 | 291.7318 |  | 2
105 | 85 | 63 | 29.0563 | 100200 | 93186 | 8.4 | 2500 | 291.7318 |  | 2
105 | 75 | 63 | 52.1129 | 107700 | 80775 | 8.48 | 3500 | 479.2737 |  | 2
105 | 80 | 63 | 39.1676 | 107700 | 98007 | 8.48 | 3500 | 479.2737 |  | 2
105 | 85 | 63 | 29.0563 | 107700 | 107700 | 8.48 | 3500 | 479.2737 |  | 2
105 | 75 | 63 | 52.1129 | 115300 | 99158 | 8.54 | 4800 | 771.0056 |  | 2
105 | 80 | 63 | 39.1676 | 115300 | 115300 | 8.54 | 4800 | 771.0056 |  | 2
105 | 85 | 63 | 29.0563 | 115300 | 115300 | 8.54 | 4800 | 771.0056 |  | 2
105 | 75 | 67 | 66.7494 | 105700 | 56021 | 8.46 | 2500 | 333.4078 |  | 2
105 | 80 | 67 | 51.5724 | 105700 | 67648 | 8.46 | 2500 | 333.4078 |  | 2
105 | 85 | 67 | 39.6049 | 105700 | 80332 | 8.46 | 2500 | 333.4078 |  | 2
105 | 75 | 67 | 66.7494 | 113400 | 65772 | 8.53 | 3500 | 479.2737 |  | 2
105 | 80 | 67 | 51.5724 | 113400 | 80514 | 8.53 | 3500 | 479.2737 |  | 2
105 | 85 | 67 | 39.6049 | 113400 | 99792 | 8.53 | 3500 | 479.2737 |  | 2
105 | 75 | 67 | 66.7494 | 119200 | 75096 | 8.59 | 4800 | 771.0056 |  | 2
105 | 80 | 67 | 51.5724 | 119200 | 100128 | 8.59 | 4800 | 771.0056 |  | 2
105 | 85 | 67 | 39.6049 | 119200 | 119200 | 8.59 | 4800 | 771.0056 |  | 2
105 | 75 | 71 | 82.6659 | 111500 | 44600 | 8.52 | 2500 | 333.4078 |  | 2
105 | 80 | 71 | 65.0618 | 111500 | 57980 | 8.52 | 2500 | 333.4078 |  | 2
105 | 85 | 71 | 51.076 | 111500 | 69130 | 8.52 | 2500 | 333.4078 |  | 2
105 | 75 | 71 | 82.6659 | 119500 | 51385 | 8.6 | 3500 | 479.2737 |  | 2
105 | 80 | 71 | 65.0618 | 119500 | 66920 | 8.6 | 3500 | 479.2737 |  | 2
105 | 85 | 71 | 51.076 | 119500 | 81260 | 8.6 | 3500 | 479.2737 |  | 2
105 | 75 | 71 | 82.6659 | 125800 | 55352 | 8.65 | 4800 | 771.0056 |  | 2
105 | 80 | 71 | 65.0618 | 125800 | 76738 | 8.65 | 4800 | 771.0056 |  | 2
105 | 85 | 71 | 51.076 | 125800 | 101898 | 8.65 | 4800 | 771.0056 |  | 2
115 | 75 | 63 | 52.1129 | 94800 | 64464 | 9.47 | 2500 | 291.7318 |  | 2
115 | 80 | 63 | 39.1676 | 94800 | 78684 | 9.47 | 2500 | 291.7318 |  | 2
115 | 85 | 63 | 29.0563 | 94800 | 91008 | 9.47 | 2500 | 291.7318 |  | 2
115 | 75 | 63 | 52.1129 | 102100 | 78617 | 9.54 | 3500 | 427.1788 |  | 2
115 | 80 | 63 | 39.1676 | 102100 | 95974 | 9.54 | 3500 | 427.1788 |  | 2
115 | 85 | 63 | 29.0563 | 102100 | 102100 | 9.54 | 3500 | 427.1788 |  | 2
115 | 75 | 63 | 52.1129 | 109400 | 96272 | 9.63 | 4800 | 771.0056 |  | 2
115 | 80 | 63 | 39.1676 | 109400 | 109400 | 9.63 | 4800 | 771.0056 |  | 2
115 | 85 | 63 | 29.0563 | 109400 | 109400 | 9.63 | 4800 | 771.0056 |  | 2
115 | 75 | 67 | 66.7494 | 100300 | 54162 | 9.54 | 2500 | 291.7318 |  | 2
115 | 80 | 67 | 51.5724 | 100300 | 66198 | 9.54 | 2500 | 291.7318 |  | 2
115 | 85 | 67 | 39.6049 | 100300 | 79237 | 9.54 | 2500 | 291.7318 |  | 2
115 | 75 | 67 | 66.7494 | 107000 | 62060 | 9.61 | 3500 | 479.2737 |  | 2
115 | 80 | 67 | 51.5724 | 107000 | 79180 | 9.61 | 3500 | 479.2737 |  | 2
115 | 85 | 67 | 39.6049 | 107000 | 97370 | 9.61 | 3500 | 479.2737 |  | 2
115 | 75 | 67 | 66.7494 | 112200 | 72930 | 9.66 | 4800 | 771.0056 |  | 2
115 | 80 | 67 | 51.5724 | 112200 | 97614 | 9.66 | 4800 | 771.0056 |  | 2
115 | 85 | 67 | 39.6049 | 112200 | 112200 | 9.66 | 4800 | 771.0056 |  | 2
115 | 75 | 71 | 82.6659 | 105700 | 43337 | 9.59 | 2500 | 333.4078 |  | 2
115 | 80 | 71 | 65.0618 | 105700 | 54964 | 9.59 | 2500 | 333.4078 |  | 2
115 | 85 | 71 | 51.076 | 105700 | 66591 | 9.59 | 2500 | 333.4078 |  | 2
115 | 75 | 71 | 82.6659 | 112900 | 48547 | 9.67 | 3500 | 479.2737 |  | 2
115 | 80 | 71 | 65.0618 | 112900 | 63224 | 9.67 | 3500 | 479.2737 |  | 2
115 | 85 | 71 | 51.076 | 112900 | 80159 | 9.67 | 3500 | 479.2737 |  | 2
115 | 75 | 71 | 82.6659 | 118500 | 53325 | 9.73 | 4800 | 771.0056 |  | 2
115 | 80 | 71 | 65.0618 | 118500 | 74655 | 9.73 | 4800 | 771.0056 |  | 2
115 | 85 | 71 | 51.076 | 118500 | 97170 | 9.73 | 4800 | 771.0056 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions

## Table 10
Degradation Coefficient (C_d)
IEER or SEER | 20
Standby Power (W)
Crankcase Heater Power (W)
Outdoor Air Dry-Bulb (deg. F) | Entering Air Dry-Bulb (deg. F) | Entering Air Wet-Bulb (deg. F) | Relative Humidity (%) | Total Capacity (W or Btu/h) | Sensible Capacity (W or Btu/h) | Total Unit Power (kW) | Supply Fan Airflow (m3/s or cfm) | Supply Fan Power (W) | Outside Fan Power (W) | Compressor Stage
65 | 75 | 63 | 52.1129 | 99100 | 55496 | 7.01 | 1100 | 291.7318 |  | 1
65 | 80 | 63 | 39.1676 | 99100 | 61442 | 7.01 | 1100 | 291.7318 |  | 1
65 | 85 | 63 | 29.0563 | 99100 | 68379 | 7.01 | 1100 | 291.7318 |  | 1
65 | 75 | 63 | 52.1129 | 125200 | 75120 | 7.13 | 1965 | 333.4078 |  | 1
65 | 80 | 63 | 39.1676 | 125200 | 86388 | 7.13 | 1965 | 333.4078 |  | 1
65 | 85 | 63 | 29.0563 | 125200 | 96404 | 7.13 | 1965 | 333.4078 |  | 1
65 | 75 | 63 | 52.1129 | 144000 | 93600 | 7.24 | 3125 | 416.7598 |  | 1
65 | 80 | 63 | 39.1676 | 144000 | 109440 | 7.24 | 3125 | 416.7598 |  | 1
65 | 85 | 63 | 29.0563 | 144000 | 125280 | 7.24 | 3125 | 416.7598 |  | 1
65 | 75 | 67 | 66.7494 | 105000 | 49350 | 7.03 | 1100 | 291.7318 |  | 1
65 | 80 | 67 | 51.5724 | 105000 | 55650 | 7.03 | 1100 | 291.7318 |  | 1
65 | 85 | 67 | 39.6049 | 105000 | 61950 | 7.03 | 1100 | 291.7318 |  | 1
65 | 75 | 67 | 66.7494 | 131800 | 65900 | 7.17 | 1965 | 333.4078 |  | 1
65 | 80 | 67 | 51.5724 | 131800 | 75126 | 7.17 | 1965 | 333.4078 |  | 1
65 | 85 | 67 | 39.6049 | 131800 | 85670 | 7.17 | 1965 | 333.4078 |  | 1
65 | 75 | 67 | 66.7494 | 151900 | 78988 | 7.29 | 3125 | 416.7598 |  | 1
65 | 80 | 67 | 51.5724 | 151900 | 94178 | 7.29 | 3125 | 416.7598 |  | 1
65 | 85 | 67 | 39.6049 | 151900 | 110887 | 7.29 | 3125 | 416.7598 |  | 1
65 | 75 | 71 | 82.6659 | 111000 | 45510 | 7.06 | 1100 | 333.4078 |  | 1
65 | 80 | 71 | 65.0618 | 111000 | 52170 | 7.06 | 1100 | 333.4078 |  | 1
65 | 85 | 71 | 51.076 | 111000 | 57720 | 7.06 | 1100 | 333.4078 |  | 1
65 | 75 | 71 | 82.6659 | 138600 | 55440 | 7.21 | 1965 | 375.0838 |  | 1
65 | 80 | 71 | 65.0618 | 138600 | 65142 | 7.21 | 1965 | 375.0838 |  | 1
65 | 85 | 71 | 51.076 | 138600 | 76230 | 7.21 | 1965 | 375.0838 |  | 1
65 | 75 | 71 | 82.6659 | 159700 | 65477 | 7.33 | 3125 | 416.7598 |  | 1
65 | 80 | 71 | 65.0618 | 159700 | 79850 | 7.33 | 3125 | 416.7598 |  | 1
65 | 85 | 71 | 51.076 | 159700 | 95820 | 7.33 | 3125 | 416.7598 |  | 1
75 | 75 | 63 | 52.1129 | 96800 | 54208 | 7.84 | 1100 | 291.7318 |  | 1
75 | 80 | 63 | 39.1676 | 96800 | 60016 | 7.84 | 1100 | 291.7318 |  | 1
75 | 85 | 63 | 29.0563 | 96800 | 66792 | 7.84 | 1100 | 291.7318 |  | 1
75 | 75 | 63 | 52.1129 | 121500 | 72900 | 7.99 | 1965 | 333.4078 |  | 1
75 | 80 | 63 | 39.1676 | 121500 | 83835 | 7.99 | 1965 | 333.4078 |  | 1
75 | 85 | 63 | 29.0563 | 121500 | 94770 | 7.99 | 1965 | 333.4078 |  | 1
75 | 75 | 63 | 52.1129 | 139300 | 91938 | 8.11 | 3125 | 416.7598 |  | 1
75 | 80 | 63 | 39.1676 | 139300 | 107261 | 8.11 | 3125 | 416.7598 |  | 1
75 | 85 | 63 | 29.0563 | 139300 | 123977 | 8.11 | 3125 | 416.7598 |  | 1
75 | 75 | 67 | 66.7494 | 102500 | 48175 | 7.87 | 1100 | 291.7318 |  | 1
75 | 80 | 67 | 51.5724 | 102500 | 53300 | 7.87 | 1100 | 291.7318 |  | 1
75 | 85 | 67 | 39.6049 | 102500 | 62525 | 7.87 | 1100 | 291.7318 |  | 1
75 | 75 | 67 | 66.7494 | 128200 | 64100 | 8.03 | 1965 | 333.4078 |  | 1
75 | 80 | 67 | 51.5724 | 128200 | 74356 | 8.03 | 1965 | 333.4078 |  | 1
75 | 85 | 67 | 39.6049 | 128200 | 83330 | 8.03 | 1965 | 333.4078 |  | 1
75 | 75 | 67 | 66.7494 | 147100 | 76492 | 8.17 | 3125 | 416.7598 |  | 1
75 | 80 | 67 | 51.5724 | 147100 | 91202 | 8.17 | 3125 | 416.7598 |  | 1
75 | 85 | 67 | 39.6049 | 147100 | 108854 | 8.17 | 3125 | 416.7598 |  | 1
75 | 75 | 71 | 82.6659 | 108600 | 44526 | 7.91 | 1100 | 333.4078 |  | 1
75 | 80 | 71 | 65.0618 | 108600 | 49956 | 7.91 | 1100 | 333.4078 |  | 1
75 | 85 | 71 | 51.076 | 108600 | 58644 | 7.91 | 1100 | 333.4078 |  | 1
75 | 75 | 71 | 82.6659 | 134700 | 53880 | 8.08 | 1965 | 375.0838 |  | 1
75 | 80 | 71 | 65.0618 | 134700 | 64656 | 8.08 | 1965 | 375.0838 |  | 1
75 | 85 | 71 | 51.076 | 134700 | 74085 | 8.08 | 1965 | 375.0838 |  | 1
75 | 75 | 71 | 82.6659 | 154700 | 63427 | 8.24 | 3125 | 416.7598 |  | 1
75 | 80 | 71 | 65.0618 | 154700 | 78897 | 8.24 | 3125 | 416.7598 |  | 1
75 | 85 | 71 | 51.076 | 154700 | 92820 | 8.24 | 3125 | 416.7598 |  | 1
85 | 75 | 63 | 52.1129 | 94100 | 52696 | 8.84 | 1100 | 291.7318 |  | 1
85 | 80 | 63 | 39.1676 | 94100 | 59283 | 8.84 | 1100 | 291.7318 |  | 1
85 | 85 | 63 | 29.0563 | 94100 | 66811 | 8.84 | 1100 | 291.7318 |  | 1
85 | 75 | 63 | 52.1129 | 117500 | 71675 | 9 | 1965 | 333.4078 |  | 1
85 | 80 | 63 | 39.1676 | 117500 | 82250 | 9 | 1965 | 333.4078 |  | 1
85 | 85 | 63 | 29.0563 | 117500 | 92825 | 9 | 1965 | 333.4078 |  | 1
85 | 75 | 63 | 52.1129 | 134300 | 89981 | 9.13 | 3125 | 375.0838 |  | 1
85 | 80 | 63 | 39.1676 | 134300 | 106097 | 9.13 | 3125 | 375.0838 |  | 1
85 | 85 | 63 | 29.0563 | 134300 | 122213 | 9.13 | 3125 | 375.0838 |  | 1
85 | 75 | 67 | 66.7494 | 99900 | 48951 | 8.88 | 1100 | 291.7318 |  | 1
85 | 80 | 67 | 51.5724 | 99900 | 52947 | 8.88 | 1100 | 291.7318 |  | 1
85 | 85 | 67 | 39.6049 | 99900 | 60939 | 8.88 | 1100 | 291.7318 |  | 1
85 | 75 | 67 | 66.7494 | 124000 | 62000 | 9.05 | 1965 | 333.4078 |  | 1
85 | 80 | 67 | 51.5724 | 124000 | 71920 | 9.05 | 1965 | 333.4078 |  | 1
85 | 85 | 67 | 39.6049 | 124000 | 81840 | 9.05 | 1965 | 333.4078 |  | 1
85 | 75 | 67 | 66.7494 | 141800 | 75154 | 9.21 | 3125 | 416.7598 |  | 1
85 | 80 | 67 | 51.5724 | 141800 | 89334 | 9.21 | 3125 | 416.7598 |  | 1
85 | 85 | 67 | 39.6049 | 141800 | 106350 | 9.21 | 3125 | 416.7598 |  | 1
85 | 75 | 71 | 82.6659 | 105200 | 42080 | 8.92 | 1100 | 291.7318 |  | 1
85 | 80 | 71 | 65.0618 | 105200 | 51548 | 8.92 | 1100 | 291.7318 |  | 1
85 | 85 | 71 | 51.076 | 105200 | 56808 | 8.92 | 1100 | 291.7318 |  | 1
85 | 75 | 71 | 82.6659 | 130300 | 52120 | 9.09 | 1965 | 333.4078 |  | 1
85 | 80 | 71 | 65.0618 | 130300 | 62544 | 9.09 | 1965 | 333.4078 |  | 1
85 | 85 | 71 | 51.076 | 130300 | 72968 | 9.09 | 1965 | 333.4078 |  | 1
85 | 75 | 71 | 82.6659 | 149200 | 59680 | 9.26 | 3125 | 416.7598 |  | 1
85 | 80 | 71 | 65.0618 | 149200 | 76092 | 9.26 | 3125 | 416.7598 |  | 1
85 | 85 | 71 | 51.076 | 149200 | 91012 | 9.26 | 3125 | 416.7598 |  | 1
95 | 75 | 63 | 52.1129 | 91100 | 51016 | 9.97 | 1100 | 291.7318 |  | 1
95 | 80 | 63 | 39.1676 | 91100 | 58304 | 9.97 | 1100 | 291.7318 |  | 1
95 | 85 | 63 | 29.0563 | 91100 | 64681 | 9.97 | 1100 | 291.7318 |  | 1
95 | 75 | 63 | 52.1129 | 113100 | 68991 | 10.13 | 1965 | 333.4078 |  | 1
95 | 80 | 63 | 39.1676 | 113100 | 80301 | 10.13 | 1965 | 333.4078 |  | 1
95 | 85 | 63 | 29.0563 | 113100 | 90480 | 10.13 | 1965 | 333.4078 |  | 1
95 | 75 | 63 | 52.1129 | 128700 | 87516 | 10.25 | 3125 | 375.0838 |  | 1
95 | 80 | 63 | 39.1676 | 128700 | 102960 | 10.25 | 3125 | 375.0838 |  | 1
95 | 85 | 63 | 29.0563 | 128700 | 119691 | 10.25 | 3125 | 375.0838 |  | 1
95 | 75 | 67 | 66.7494 | 96300 | 47187 | 10 | 1100 | 291.7318 |  | 1
95 | 80 | 67 | 51.5724 | 96300 | 54891 | 10 | 1100 | 291.7318 |  | 1
95 | 85 | 67 | 39.6049 | 96300 | 57780 | 10 | 1100 | 291.7318 |  | 1
95 | 75 | 67 | 66.7494 | 119400 | 59700 | 10.19 | 1965 | 333.4078 |  | 1
95 | 80 | 67 | 51.5724 | 119400 | 70446 | 10.19 | 1965 | 333.4078 |  | 1
95 | 85 | 67 | 39.6049 | 119400 | 79998 | 10.19 | 1965 | 333.4078 |  | 1
95 | 75 | 67 | 66.7494 | 135900 | 72027 | 10.35 | 3125 | 416.7598 |  | 1
95 | 80 | 67 | 51.5724 | 135900 | 88335 | 10.35 | 3125 | 416.7598 |  | 1
95 | 85 | 67 | 39.6049 | 135900 | 104643 | 10.35 | 3125 | 416.7598 |  | 1
95 | 75 | 71 | 82.6659 | 100800 | 43344 | 10.03 | 1100 | 291.7318 |  | 1
95 | 80 | 71 | 65.0618 | 100800 | 48384 | 10.03 | 1100 | 291.7318 |  | 1
95 | 85 | 71 | 51.076 | 100800 | 53424 | 10.03 | 1100 | 291.7318 |  | 1
95 | 75 | 71 | 82.6659 | 125500 | 50200 | 10.25 | 1965 | 333.4078 |  | 1
95 | 80 | 71 | 65.0618 | 125500 | 60240 | 10.25 | 1965 | 333.4078 |  | 1
95 | 85 | 71 | 51.076 | 125500 | 70280 | 10.25 | 1965 | 333.4078 |  | 1
95 | 75 | 71 | 82.6659 | 143100 | 58671 | 10.43 | 3125 | 416.7598 |  | 1
95 | 80 | 71 | 65.0618 | 143100 | 74412 | 10.43 | 3125 | 416.7598 |  | 1
95 | 85 | 71 | 51.076 | 143100 | 88722 | 10.43 | 3125 | 416.7598 |  | 1
85 | 75 | 63 | 52.1129 | 134100 | 88506 | 8.99 | 3125 | 375.0838 |  | 2
85 | 80 | 63 | 39.1676 | 134100 | 103257 | 8.99 | 3125 | 375.0838 |  | 2
85 | 85 | 63 | 29.0563 | 134100 | 120690 | 8.99 | 3125 | 375.0838 |  | 2
85 | 75 | 63 | 52.1129 | 144100 | 103752 | 9.08 | 4375 | 687.6536 |  | 2
85 | 80 | 63 | 39.1676 | 144100 | 128249 | 9.08 | 4375 | 687.6536 |  | 2
85 | 85 | 63 | 29.0563 | 144100 | 144100 | 9.08 | 4375 | 687.6536 |  | 2
85 | 75 | 63 | 52.1129 | 152700 | 125214 | 9.16 | 6000 | 1364.8883 |  | 2
85 | 80 | 63 | 39.1676 | 152700 | 152700 | 9.16 | 6000 | 1364.8883 |  | 2
85 | 85 | 63 | 29.0563 | 152700 | 152700 | 9.16 | 6000 | 1364.8883 |  | 2
85 | 75 | 67 | 66.7494 | 141500 | 74995 | 9.06 | 3125 | 416.7598 |  | 2
85 | 80 | 67 | 51.5724 | 141500 | 89145 | 9.06 | 3125 | 416.7598 |  | 2
85 | 85 | 67 | 39.6049 | 141500 | 104710 | 9.06 | 3125 | 416.7598 |  | 2
85 | 75 | 67 | 66.7494 | 152100 | 85176 | 9.17 | 4375 | 687.6536 |  | 2
85 | 80 | 67 | 51.5724 | 152100 | 106470 | 9.17 | 4375 | 687.6536 |  | 2
85 | 85 | 67 | 39.6049 | 152100 | 129285 | 9.17 | 4375 | 687.6536 |  | 2
85 | 75 | 67 | 66.7494 | 160400 | 99448 | 9.23 | 6000 | 1364.8883 |  | 2
85 | 80 | 67 | 51.5724 | 160400 | 126716 | 9.23 | 6000 | 1364.8883 |  | 2
85 | 85 | 67 | 39.6049 | 160400 | 157192 | 9.23 | 6000 | 1364.8883 |  | 2
85 | 75 | 71 | 82.6659 | 148900 | 59560 | 9.14 | 3125 | 416.7598 |  | 2
85 | 80 | 71 | 65.0618 | 148900 | 75939 | 9.14 | 3125 | 416.7598 |  | 2
85 | 85 | 71 | 51.076 | 148900 | 89340 | 9.14 | 3125 | 416.7598 |  | 2
85 | 75 | 71 | 82.6659 | 160100 | 67242 | 9.24 | 4375 | 687.6536 |  | 2
85 | 80 | 71 | 65.0618 | 160100 | 86454 | 9.24 | 4375 | 687.6536 |  | 2
85 | 85 | 71 | 51.076 | 160100 | 107267 | 9.24 | 4375 | 687.6536 |  | 2
85 | 75 | 71 | 82.6659 | 168700 | 75915 | 9.32 | 6000 | 1364.8883 |  | 2
85 | 80 | 71 | 65.0618 | 168700 | 99533 | 9.32 | 6000 | 1364.8883 |  | 2
85 | 85 | 71 | 51.076 | 168700 | 131586 | 9.32 | 6000 | 1364.8883 |  | 2
95 | 75 | 63 | 52.1129 | 128400 | 86028 | 10.1 | 3125 | 375.0838 |  | 2
95 | 80 | 63 | 39.1676 | 128400 | 101436 | 10.1 | 3125 | 375.0838 |  | 2
95 | 85 | 63 | 29.0563 | 128400 | 118128 | 10.1 | 3125 | 375.0838 |  | 2
95 | 75 | 63 | 52.1129 | 137800 | 100594 | 10.2 | 4375 | 687.6536 |  | 2
95 | 80 | 63 | 39.1676 | 137800 | 124020 | 10.2 | 4375 | 687.6536 |  | 2
95 | 85 | 63 | 29.0563 | 137800 | 137800 | 10.2 | 4375 | 687.6536 |  | 2
95 | 75 | 63 | 52.1129 | 146500 | 123060 | 10.31 | 6000 | 1364.8883 |  | 2
95 | 80 | 63 | 39.1676 | 146500 | 146500 | 10.31 | 6000 | 1364.8883 |  | 2
95 | 85 | 63 | 29.0563 | 146500 | 146500 | 10.31 | 6000 | 1364.8883 |  | 2
95 | 75 | 67 | 66.7494 | 135600 | 71868 | 10.19 | 3125 | 416.7598 |  | 2
95 | 80 | 67 | 51.5724 | 135600 | 86784 | 10.19 | 3125 | 416.7598 |  | 2
95 | 85 | 67 | 39.6049 | 135600 | 101700 | 10.19 | 3125 | 416.7598 |  | 2
95 | 75 | 67 | 66.7494 | 145400 | 82878 | 10.29 | 4375 | 687.6536 |  | 2
95 | 80 | 67 | 51.5724 | 145400 | 103234 | 10.29 | 4375 | 687.6536 |  | 2
95 | 85 | 67 | 39.6049 | 145400 | 126498 | 10.29 | 4375 | 687.6536 |  | 2
95 | 75 | 67 | 66.7494 | 153300 | 96579 | 10.38 | 6000 | 1364.8883 |  | 2
95 | 80 | 67 | 51.5724 | 153300 | 124173 | 10.38 | 6000 | 1364.8883 |  | 2
95 | 85 | 67 | 39.6049 | 153300 | 153300 | 10.38 | 6000 | 1364.8883 |  | 2
95 | 75 | 71 | 82.6659 | 142700 | 58507 | 10.27 | 3125 | 416.7598 |  | 2
95 | 80 | 71 | 65.0618 | 142700 | 74204 | 10.27 | 3125 | 416.7598 |  | 2
95 | 85 | 71 | 51.076 | 142700 | 88474 | 10.27 | 3125 | 416.7598 |  | 2
95 | 75 | 71 | 82.6659 | 153200 | 64344 | 10.38 | 4375 | 687.6536 |  | 2
95 | 80 | 71 | 65.0618 | 153200 | 84260 | 10.38 | 4375 | 687.6536 |  | 2
95 | 85 | 71 | 51.076 | 153200 | 104176 | 10.38 | 4375 | 687.6536 |  | 2
95 | 75 | 71 | 82.6659 | 160900 | 72405 | 10.46 | 6000 | 1364.8883 |  | 2
95 | 80 | 71 | 65.0618 | 160900 | 99758 | 10.46 | 6000 | 1364.8883 |  | 2
95 | 85 | 71 | 51.076 | 160900 | 127111 | 10.46 | 6000 | 1364.8883 |  | 2
105 | 75 | 63 | 52.1129 | 122500 | 83300 | 11.34 | 3125 | 375.0838 |  | 2
105 | 80 | 63 | 39.1676 | 122500 | 100450 | 11.34 | 3125 | 375.0838 |  | 2
105 | 85 | 63 | 29.0563 | 122500 | 116375 | 11.34 | 3125 | 375.0838 |  | 2
105 | 75 | 63 | 52.1129 | 131200 | 98400 | 11.44 | 4375 | 625.1397 |  | 2
105 | 80 | 63 | 39.1676 | 131200 | 122016 | 11.44 | 4375 | 625.1397 |  | 2
105 | 85 | 63 | 29.0563 | 131200 | 131200 | 11.44 | 4375 | 625.1397 |  | 2
105 | 75 | 63 | 52.1129 | 140300 | 120658 | 11.56 | 6000 | 1364.8883 |  | 2
105 | 80 | 63 | 39.1676 | 140300 | 140300 | 11.56 | 6000 | 1364.8883 |  | 2
105 | 85 | 63 | 29.0563 | 140300 | 140300 | 11.56 | 6000 | 1364.8883 |  | 2
105 | 75 | 67 | 66.7494 | 129400 | 69876 | 11.42 | 3125 | 375.0838 |  | 2
105 | 80 | 67 | 51.5724 | 129400 | 85404 | 11.42 | 3125 | 375.0838 |  | 2
105 | 85 | 67 | 39.6049 | 129400 | 99638 | 11.42 | 3125 | 375.0838 |  | 2
105 | 75 | 67 | 66.7494 | 138500 | 80330 | 11.54 | 4375 | 687.6536 |  | 2
105 | 80 | 67 | 51.5724 | 138500 | 101105 | 11.54 | 4375 | 687.6536 |  | 2
105 | 85 | 67 | 39.6049 | 138500 | 123265 | 11.54 | 4375 | 687.6536 |  | 2
105 | 75 | 67 | 66.7494 | 145400 | 93056 | 11.63 | 6000 | 1364.8883 |  | 2
105 | 80 | 67 | 51.5724 | 145400 | 120682 | 11.63 | 6000 | 1364.8883 |  | 2
105 | 85 | 67 | 39.6049 | 145400 | 145400 | 11.63 | 6000 | 1364.8883 |  | 2
105 | 75 | 71 | 82.6659 | 136300 | 55883 | 11.53 | 3125 | 416.7598 |  | 2
105 | 80 | 71 | 65.0618 | 136300 | 70876 | 11.53 | 3125 | 416.7598 |  | 2
105 | 85 | 71 | 51.076 | 136300 | 85869 | 11.53 | 3125 | 416.7598 |  | 2
105 | 75 | 71 | 82.6659 | 145800 | 62694 | 11.63 | 4375 | 687.6536 |  | 2
105 | 80 | 71 | 65.0618 | 145800 | 83106 | 11.63 | 4375 | 687.6536 |  | 2
105 | 85 | 71 | 51.076 | 145800 | 102060 | 11.63 | 4375 | 687.6536 |  | 2
105 | 75 | 71 | 82.6659 | 153100 | 70426 | 11.71 | 6000 | 1364.8883 |  | 2
105 | 80 | 71 | 65.0618 | 153100 | 97984 | 11.71 | 6000 | 1364.8883 |  | 2
105 | 85 | 71 | 51.076 | 153100 | 127073 | 11.71 | 6000 | 1364.8883 |  | 2
115 | 75 | 63 | 52.1129 | 116200 | 80178 | 12.67 | 3125 | 375.0838 |  | 2
115 | 80 | 63 | 39.1676 | 116200 | 96446 | 12.67 | 3125 | 375.0838 |  | 2
115 | 85 | 63 | 29.0563 | 116200 | 113876 | 12.67 | 3125 | 375.0838 |  | 2
115 | 75 | 63 | 52.1129 | 124300 | 95711 | 12.78 | 4375 | 625.1397 |  | 2
115 | 80 | 63 | 39.1676 | 124300 | 119328 | 12.78 | 4375 | 625.1397 |  | 2
115 | 85 | 63 | 29.0563 | 124300 | 124300 | 12.78 | 4375 | 625.1397 |  | 2
115 | 75 | 63 | 52.1129 | 133400 | 117392 | 12.9 | 6000 | 1271.1173 |  | 2
115 | 80 | 63 | 39.1676 | 133400 | 133400 | 12.9 | 6000 | 1271.1173 |  | 2
115 | 85 | 63 | 29.0563 | 133400 | 133400 | 12.9 | 6000 | 1271.1173 |  | 2
115 | 75 | 67 | 66.7494 | 122800 | 67540 | 12.77 | 3125 | 375.0838 |  | 2
115 | 80 | 67 | 51.5724 | 122800 | 81048 | 12.77 | 3125 | 375.0838 |  | 2
115 | 85 | 67 | 39.6049 | 122800 | 98240 | 12.77 | 3125 | 375.0838 |  | 2
115 | 75 | 67 | 66.7494 | 131000 | 78600 | 12.87 | 4375 | 625.1397 |  | 2
115 | 80 | 67 | 51.5724 | 131000 | 98250 | 12.87 | 4375 | 625.1397 |  | 2
115 | 85 | 67 | 39.6049 | 131000 | 121830 | 12.87 | 4375 | 625.1397 |  | 2
115 | 75 | 67 | 66.7494 | 137300 | 89245 | 12.93 | 6000 | 1364.8883 |  | 2
115 | 80 | 67 | 51.5724 | 137300 | 119451 | 12.93 | 6000 | 1364.8883 |  | 2
115 | 85 | 67 | 39.6049 | 137300 | 137300 | 12.93 | 6000 | 1364.8883 |  | 2
115 | 75 | 71 | 82.6659 | 129300 | 54306 | 12.85 | 3125 | 375.0838 |  | 2
115 | 80 | 71 | 65.0618 | 129300 | 68529 | 12.85 | 3125 | 375.0838 |  | 2
115 | 85 | 71 | 51.076 | 129300 | 82752 | 12.85 | 3125 | 375.0838 |  | 2
115 | 75 | 71 | 82.6659 | 138000 | 57960 | 12.97 | 4375 | 687.6536 |  | 2
115 | 80 | 71 | 65.0618 | 138000 | 80040 | 12.97 | 4375 | 687.6536 |  | 2
115 | 85 | 71 | 51.076 | 138000 | 100740 | 12.97 | 4375 | 687.6536 |  | 2
115 | 75 | 71 | 82.6659 | 144600 | 67962 | 13.06 | 6000 | 1364.8883 |  | 2
115 | 80 | 71 | 65.0618 | 144600 | 93990 | 13.06 | 6000 | 1364.8883 |  | 2
115 | 85 | 71 | 51.076 | 144600 | 122910 | 13.06 | 6000 | 1364.8883 |  | 2
Note on B7: - Range: 50-130 deg. F - Include rated conditions
Note on C7: - Range: 50-130 deg. F - Include rated conditions