## page 1
Performance data (cont)
Cooling Capacities (cont)
48/50 030 (30 TON) STANDARD CAPACITY COIL — SUBCOOLING MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 6000 |  |  |  |  | 7500 |  |  |  |  | 9000 |  |  |  |  | 10500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 341 | 322 | 293 | 266 | 243 | 361 | 340 | 309 | 282 | 260 | 375 | 353 | 321 | 293 | 273 | 385 | 363 | 330 | 301 | 283
| SHC | 97 | 118 | 151 | 185 | 218 | 104 | 128 | 168 | 209 | 244 | 112 | 138 | 184 | 231 | 266 | 118 | 149 | 200 | 252 | 283
| kW | 23.7 | 23.2 | 22.4 | 21.8 | 21.3 | 24.3 | 23.7 | 22.9 | 22.2 | 21.6 | 24.8 | 24.2 | 23.2 | 22.5 | 21.9 | 25.1 | 24.5 | 23.5 | 22.7 | 22.2
| BF | 0 | 0.03 | 0.07 | 0.08 | 0.09 | 0.03 | 0.07 | 0.09 | 0.1 | 0.15 | 0.05 | 0.1 | 0.12 | 0.12 | 0.21 | 0.1 | 0.13 | 0.14 | 0.15 | 0.26
85 | TC | 320 | 301 | 274 | 249 | 227 | 335 | 316 | 288 | 262 | 244 | 346 | 327 | 298 | 271 | 256 | 355 | 335 | 305 | 279 | 264
| SHC | 78 | 100 | 135 | 170 | 205 | 83 | 108 | 150 | 192 | 229 | 89 | 117 | 164 | 213 | 249 | 94 | 125 | 179 | 232 | 264
| kW | 25.8 | 25.3 | 24.5 | 24 | 23.5 | 26.4 | 25.8 | 25 | 24.3 | 23.8 | 26.8 | 26.2 | 25.3 | 24.6 | 24.1 | 27.1 | 26.5 | 25.6 | 24.8 | 24.3
| BF | 0 | 0.03 | 0.07 | 0.08 | 0.1 | 0.03 | 0.07 | 0.09 | 0.1 | 0.16 | 0.06 | 0.1 | 0.12 | 0.12 | 0.22 | 0.1 | 0.13 | 0.14 | 0.15 | 0.28
95 | TC | 297 | 280 | 254 | 231 | 212 | 310 | 293 | 266 | 242 | 227 | 319 | 301 | 274 | 250 | 238 | 326 | 308 | 280 | 257 | 245
| SHC | 60 | 82 | 119 | 155 | 193 | 62 | 88 | 131 | 175 | 213 | 66 | 95 | 144 | 195 | 231 | 70 | 102 | 158 | 213 | 245
| kW | 28.2 | 27.7 | 27 | 26.5 | 26 | 28.7 | 28.1 | 27.4 | 26.7 | 26.3 | 29.1 | 28.5 | 27.6 | 27 | 26.6 | 29.4 | 28.7 | 27.9 | 27.1 | 26.8
| BF | 0 | 0.04 | 0.07 | 0.08 | 0.1 | 0.03 | 0.07 | 0.09 | 0.1 | 0.17 | 0.06 | 0.1 | 0.12 | 0.12 | 0.23 | 0.1 | 0.13 | 0.14 | 0.15 | 0.29
105 | TC | 274 | 258 | 234 | 212 | 198 | 284 | 268 | 244 | 222 | 211 | 291 | 275 | 250 | 229 | 220 | 296 | 280 | 254 | 234 | 225
| SHC | 42 | 65 | 102 | 140 | 179 | 42 | 68 | 113 | 158 | 197 | 43 | 73 | 125 | 177 | 214 | 46 | 80 | 137 | 194 | 225
| kW | 30.9 | 30.4 | 29.8 | 29.2 | 28.8 | 31.3 | 30.8 | 30.1 | 29.5 | 29.1 | 31.6 | 31 | 30.3 | 29.7 | 29.3 | 31.8 | 31.3 | 30.4 | 29.8 | 29.5
| BF | 0 | 0.04 | 0.07 | 0.08 | 0.13 | 0.04 | 0.07 | 0.09 | 0.1 | 0.18 | 0.06 | 0.1 | 0.12 | 0.13 | 0.24 | 0.1 | 0.13 | 0.14 | 0.16 | 0.3
115 | TC | 250 | 236 | 214 | 194 | 183 | 257 | 243 | 221 | 201 | 194 | 262 | 247 | 225 | 207 | 201 | 266 | 251 | 228 | 213 | 205
| SHC | 23 | 47 | 86 | 125 | 164 | 21 | 49 | 95 | 142 | 181 | 20 | 52 | 105 | 159 | 196 | 21 | 56 | 116 | 176 | 205
| kW | 33.9 | 33.4 | 32.8 | 32.3 | 32.1 | 34.2 | 33.7 | 33 | 32.5 | 32.2 | 34.4 | 33.9 | 33.2 | 32.7 | 32.4 | 34.6 | 34 | 33.3 | 32.8 | 32.6
| BF | 0.01 | 0.04 | 0.07 | 0.08 | 0.14 | 0.04 | 0.08 | 0.1 | 0.1 | 0.2 | 0.07 | 0.11 | 0.12 | 0.13 | 0.25 | 0.1 | 0.13 | 0.14 | 0.17 | 0.32
48/50 030 (30 TON) STANDARD CAPACITY COIL — SUBCOOLING MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 12000 |  |  |  |  | 13500 |  |  |  |  | 15000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 395 | 372 | 337 | 308 | 294 | 401 | 378 | 343 | 314 | 304 | 309 | 411 | 385 | 348 | 319
| SHC | 127 | 159 | 216 | 271 | 294 | 132 | 169 | 231 | 287 | 304 | 309 | 142 | 179 | 246 | 299
| kW | 25.5 | 24.8 | 23.8 | 22.9 | 22.5 | 25.7 | 25 | 24 | 23.1 | 22.8 | 22.9 | 26.1 | 25.2 | 24.1 | 23.2
| BF | 0.12 | 0.15 | 0.15 | 0.18 | 0.33 | 0.15 | 0.16 | 0.17 | 0.21 | 0.39 | 0.4 | 0.17 | 0.18 | 0.19 | 0.25
85 | TC | 363 | 342 | 311 | 274 | 285 | 368 | 348 | 316 | 290 | 282 | 374 | 352 | 321 | 296 | 290
| SHC | 100 | 134 | 193 | 274 | 255 | 105 | 143 | 208 | 263 | 282 | 112 | 152 | 222 | 276 | 290
| kW | 27.4 | 26.7 | 25.8 | 24.6 | 24.9 | 27.6 | 27 | 26 | 25.1 | 24.9 | 27.9 | 27.1 | 26.1 | 25.3 | 25.1
| BF | 0.13 | 0.15 | 0.15 | 0.34 | 0.19 | 0.15 | 0.17 | 0.17 | 0.22 | 0.4 | 0.17 | 0.18 | 0.19 | 0.26 | 0.45
95 | TC | 331 | 313 | 285 | 262 | 253 | 336 | 318 | 289 | 268 | 261 | 340 | 321 | 292 | 272 | 267
| SHC | 74 | 110 | 171 | 230 | 253 | 79 | 119 | 185 | 241 | 261 | 84 | 126 | 198 | 253 | 267
| kW | 29.6 | 29 | 28 | 27.3 | 27 | 29.8 | 29.2 | 28.2 | 27.5 | 27.2 | 30 | 29.3 | 28.3 | 27.6 | 27.5
| BF | 0.13 | 0.15 | 0.15 | 0.19 | 0.35 | 0.15 | 0.17 | 0.17 | 0.23 | 0.41 | 0.17 | 0.18 | 0.19 | 0.27 | 0.45
105 | TC | 301 | 284 | 258 | 241 | 233 | 304 | 287 | 261 | 245 | 239 | 307 | 289 | 263 | 249 | 244
| SHC | 49 | 86 | 149 | 208 | 233 | 53 | 93 | 161 | 219 | 239 | 57 | 100 | 174 | 230 | 244
| kW | 32 | 31.4 | 30.6 | 30 | 29.7 | 32.2 | 31.6 | 30.7 | 30.1 | 29.9 | 32.4 | 31.7 | 30.8 | 30.2 | 30.1
| BF | 0.13 | 0.15 | 0.16 | 0.21 | 0.37 | 0.15 | 0.17 | 0.17 | 0.24 | 0.42 | 0.17 | 0.18 | 0.19 | 0.28 | 0.46
115 | TC | 268 | 253 | 231 | 218 | 211 | 271 | 255 | 233 | 222 | 216 | 273 | 257 | 234 | 224 | 221
| SHC | 24 | 62 | 127 | 186 | 211 | 26 | 68 | 139 | 197 | 216 | 29 | 74 | 150 | 207 | 221
| kW | 34.7 | 34.1 | 33.4 | 32.9 | 32.7 | 34.8 | 34.3 | 33.5 | 33 | 32.9 | 34.9 | 34.3 | 33.6 | 33.1 | 33
| BF | 0.13 | 0.15 | 0.16 | 0.22 | 0.38 | 0.15 | 0.17 | 0.17 | 0.26 | 0.43 | 0.17 | 0.19 | 0.19 | 0.29 | 0.48
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
70

## page 2
Performance data (cont)
Cooling Capacities (cont)
48/50 030 (30 TON) HIGH-CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 6000 |  |  |  |  | 7500 |  |  |  |  | 9000 |  |  |  |  | 10500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 353 | 332 | 300 | 272 | 249 | 374 | 351 | 318 | 288 | 268 | 389 | 365 | 330 | 300 | 282 | 398 | 377 | 340 | 309 | 292
| SHC | 98 | 119 | 153 | 188 | 225 | 106 | 131 | 171 | 214 | 252 | 114 | 142 | 190 | 239 | 275 | 121 | 155 | 208 | 262 | 292
| kW | 24.1 | 23.5 | 22.6 | 22 | 21.4 | 24.8 | 24.1 | 23.2 | 22.4 | 21.8 | 25.3 | 24.6 | 23.6 | 22.7 | 22.2 | 25.6 | 25 | 23.9 | 23 | 22.5
| BF | 0 | 0.01 | 0.03 | 0.03 | 0.05 | 0.01 | 0.03 | 0.04 | 0.05 | 0.11 | 0.02 | 0.04 | 0.05 | 0.06 | 0.16 | 0.04 | 0.06 | 0.07 | 0.08 | 0.22
85 | TC | 329 | 310 | 280 | 254 | 233 | 346 | 326 | 294 | 267 | 251 | 359 | 337 | 305 | 277 | 263 | 369 | 346 | 313 | 285 | 272
| SHC | 78 | 100 | 136 | 172 | 211 | 83 | 109 | 151 | 196 | 236 | 90 | 119 | 168 | 219 | 257 | 97 | 129 | 185 | 241 | 272
| kW | 26.2 | 25.6 | 24.8 | 24.2 | 23.7 | 26.8 | 26.2 | 25.2 | 24.5 | 24 | 27.3 | 26.6 | 25.6 | 24.8 | 24.3 | 27.6 | 26.9 | 25.9 | 25 | 24.6
| BF | 0 | 0.01 | 0.03 | 0.03 | 0.05 | 0.01 | 0.03 | 0.04 | 0.05 | 0.12 | 0.02 | 0.04 | 0.05 | 0.06 | 0.17 | 0.04 | 0.06 | 0.07 | 0.09 | 0.23
95 | TC | 306 | 287 | 259 | 234 | 219 | 319 | 300 | 271 | 246 | 234 | 329 | 309 | 279 | 254 | 244 | 337 | 317 | 286 | 261 | 251
| SHC | 59 | 81 | 118 | 155 | 198 | 61 | 87 | 131 | 177 | 219 | 65 | 95 | 146 | 199 | 238 | 70 | 104 | 162 | 220 | 251
| kW | 28.6 | 28 | 27.3 | 26.7 | 26.3 | 29.1 | 28.5 | 27.6 | 27 | 26.6 | 29.5 | 28.8 | 27.9 | 27.2 | 26.8 | 29.8 | 29.1 | 28.1 | 27.4 | 27.1
| BF | 0 | 0.01 | 0.03 | 0.03 | 0.07 | 0.01 | 0.03 | 0.04 | 0.05 | 0.13 | 0.02 | 0.04 | 0.05 | 0.07 | 0.18 | 0.04 | 0.06 | 0.07 | 0.09 | 0.25
105 | TC | 281 | 264 | 238 | 215 | 204 | 291 | 273 | 247 | 224 | 216 | 299 | 280 | 253 | 231 | 225 | 305 | 286 | 257 | 239 | 229
| SHC | 39 | 62 | 101 | 140 | 183 | 38 | 65 | 112 | 160 | 202 | 40 | 71 | 124 | 180 | 219 | 44 | 79 | 138 | 200 | 229
| kW | 31.2 | 30.7 | 30.1 | 29.5 | 29.2 | 31.7 | 31.1 | 30.3 | 29.7 | 29.4 | 32 | 31.4 | 30.5 | 29.9 | 29.6 | 32.3 | 31.6 | 30.7 | 30.1 | 29.8
| BF | 0 | 0.01 | 0.03 | 0.03 | 0.09 | 0.01 | 0.03 | 0.04 | 0.05 | 0.14 | 0.03 | 0.05 | 0.06 | 0.07 | 0.19 | 0.04 | 0.06 | 0.07 | 0.11 | 0.26
115 | TC | 256 | 240 | 216 | 195 | 188 | 263 | 246 | 222 | 202 | 198 | 267 | 251 | 226 | 208 | 205 | 271 | 254 | 229 | 216 | 207
| SHC | 19 | 43 | 84 | 124 | 168 | 15 | 44 | 92 | 142 | 185 | 15 | 47 | 103 | 162 | 200 | 17 | 53 | 115 | 177 | 207
| kW | 34.2 | 33.8 | 33.2 | 32.9 | 32.8 | 34.5 | 34 | 33.3 | 32.9 | 32.7 | 34.7 | 34.2 | 33.4 | 32.9 | 32.8 | 34.9 | 34.3 | 33.6 | 33.1 | 32.9
| BF | 0 | 0.02 | 0.03 | 0.03 | 0.1 | 0.01 | 0.03 | 0.04 | 0.05 | 0.16 | 0.03 | 0.05 | 0.06 | 0.08 | 0.21 | 0.04 | 0.06 | 0.07 | 0.13 | 0.28
48/50 030 (30 TON) HIGH-CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 12000 |  |  |  |  | 13500 |  |  |  |  | 15000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 396 | 386 | 348 | 316 | 305 | 405 | 388 | 355 | 324 | 316 | 409 | 401 | 361 | 331 | 326
| SHC | 123 | 167 | 226 | 282 | 305 | 130 | 174 | 245 | 298 | 316 | 132 | 192 | 263 | 314 | 326
| kW | 25.5 | 25.3 | 24.2 | 23.2 | 22.9 | 25.6 | 25.4 | 24.4 | 23.4 | 23.2 | 25.8 | 25.8 | 24.6 | 23.7 | 23.5
| BF | 0.06 | 0.07 | 0.08 | 0.12 | 0.3 | 0.07 | 0.09 | 0.09 | 0.16 | 0.36 | 0.09 | 0.1 | 0.11 | 0.19 | 0.41
85 | TC | 375 | 354 | 319 | 293 | 282 | 383 | 359 | 325 | 300 | 292 | 389 | 365 | 329 | 306 | 300
| SHC | 102 | 140 | 202 | 258 | 282 | 111 | 151 | 219 | 273 | 292 | 114 | 162 | 235 | 289 | 300
| kW | 27.9 | 27.2 | 26.1 | 25.2 | 24.9 | 28.2 | 27.4 | 26.3 | 25.5 | 25.2 | 28.4 | 27.6 | 26.5 | 25.7 | 25.5
| BF | 0.06 | 0.07 | 0.08 | 0.13 | 0.3 | 0.07 | 0.09 | 0.09 | 0.17 | 0.36 | 0.08 | 0.1 | 0.11 | 0.2 | 0.41
95 | TC | 343 | 322 | 291 | 269 | 260 | 348 | 327 | 295 | 275 | 268 | 352 | 331 | 298 | 279 | 275
| SHC | 76 | 114 | 177 | 235 | 260 | 82 | 123 | 193 | 249 | 268 | 88 | 133 | 208 | 263 | 275
| kW | 30.1 | 29.4 | 28.3 | 27.6 | 27.3 | 30.3 | 29.6 | 28.5 | 27.8 | 27.6 | 30.5 | 29.7 | 28.6 | 27.9 | 27.8
| BF | 0.06 | 0.07 | 0.08 | 0.14 | 0.31 | 0.08 | 0.09 | 0.1 | 0.18 | 0.37 | 0.09 | 0.1 | 0.11 | 0.21 | 0.42
105 | TC | 310 | 290 | 261 | 245 | 237 | 313 | 293 | 264 | 250 | 243 | 317 | 297 | 267 | 253 | 249
| SHC | 48 | 87 | 153 | 212 | 237 | 53 | 95 | 167 | 225 | 243 | 59 | 105 | 181 | 238 | 249
| kW | 32.5 | 31.8 | 30.8 | 30.2 | 30 | 32.7 | 32 | 31 | 30.4 | 30.2 | 32.8 | 32.1 | 31.1 | 30.5 | 30.4
| BF | 0.06 | 0.07 | 0.08 | 0.16 | 0.33 | 0.08 | 0.09 | 0.1 | 0.19 | 0.38 | 0.09 | 0.1 | 0.11 | 0.22 | 0.43
115 | TC | 275 | 257 | 231 | 221 | 213 | 277 | 259 | 234 | 224 | 218 | 279 | 261 | 235 | 227 | 223
| SHC | 20 | 59 | 129 | 189 | 213 | 23 | 67 | 142 | 201 | 218 | 28 | 75 | 156 | 212 | 223
| kW | 35.1 | 34.5 | 33.7 | 33.2 | 33 | 35.2 | 34.6 | 33.7 | 33.3 | 33.2 | 35.4 | 34.7 | 33.8 | 33.4 | 33.3
| BF | 0.06 | 0.08 | 0.08 | 0.17 | 0.34 | 0.08 | 0.09 | 0.1 | 0.21 | 0.4 | 0.09 | 0.1 | 0.12 | 0.24 | 0.44
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
73

## page 3
Performance data (cont)
Cooling Capacities (cont)
48/50 035 (35 TON) STANDARD CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 7000 |  |  |  |  | 8750 |  |  |  |  | 9625 |  |  |  |  | 10500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 388 | 364 | 328 | 297 | 270 | 410 | 385 | 346 | 313 | 290 | 413 | 393 | 354 | 319 | 297 | 419 | 401 | 360 | 325 | 304
| SHC | 112 | 134 | 172 | 211 | 249 | 123 | 149 | 194 | 241 | 281 | 124 | 157 | 206 | 255 | 294 | 127 | 165 | 217 | 270 | 304
| kW | 26.3 | 25.6 | 24.5 | 23.7 | 23 | 27 | 26.2 | 25.1 | 24.2 | 23.5 | 27.2 | 26.5 | 25.3 | 24.3 | 23.7 | 27.3 | 26.8 | 25.6 | 24.5 | 23.9
| BF | 0 | 0.01 | 0.04 | 0.04 | 0.05 | 0.01 | 0.04 | 0.05 | 0.06 | 0.12 | 0.02 | 0.05 | 0.06 | 0.07 | 0.15 | 0.03 | 0.06 | 0.07 | 0.08 | 0.19
85 | TC | 360 | 337 | 304 | 275 | 251 | 378 | 355 | 319 | 289 | 270 | 386 | 362 | 325 | 294 | 276 | 392 | 368 | 330 | 299 | 282
| SHC | 88 | 112 | 151 | 192 | 233 | 97 | 125 | 171 | 220 | 261 | 102 | 131 | 181 | 234 | 273 | 106 | 138 | 192 | 247 | 282
| kW | 28.4 | 27.7 | 26.7 | 25.9 | 25.3 | 29.1 | 28.3 | 27.2 | 26.3 | 25.7 | 29.4 | 28.6 | 27.4 | 26.5 | 25.9 | 29.6 | 28.8 | 27.6 | 26.6 | 26.1
| BF | 0 | 0.02 | 0.04 | 0.04 | 0.06 | 0.01 | 0.04 | 0.05 | 0.06 | 0.13 | 0.02 | 0.05 | 0.06 | 0.07 | 0.16 | 0.04 | 0.06 | 0.07 | 0.08 | 0.2
95 | TC | 331 | 311 | 280 | 253 | 235 | 346 | 324 | 292 | 265 | 250 | 352 | 330 | 297 | 269 | 255 | 357 | 335 | 302 | 273 | 259
| SHC | 65 | 89 | 130 | 173 | 218 | 71 | 99 | 148 | 199 | 242 | 74 | 105 | 157 | 212 | 253 | 78 | 111 | 167 | 224 | 259
| kW | 30.8 | 30.1 | 29.1 | 28.4 | 27.9 | 31.4 | 30.7 | 29.6 | 28.8 | 28.3 | 31.7 | 30.9 | 29.8 | 28.9 | 28.4 | 31.9 | 31.1 | 30 | 29.1 | 28.6
| BF | 0 | 0.02 | 0.04 | 0.04 | 0.08 | 0.02 | 0.04 | 0.05 | 0.06 | 0.14 | 0.02 | 0.05 | 0.06 | 0.07 | 0.17 | 0.04 | 0.06 | 0.07 | 0.08 | 0.22
105 | TC | 303 | 284 | 256 | 230 | 217 | 314 | 294 | 265 | 240 | 229 | 318 | 298 | 269 | 244 | 225 | 322 | 301 | 272 | 247 | 236
| SHC | 42 | 67 | 110 | 154 | 200 | 44 | 74 | 125 | 178 | 222 | 47 | 78 | 133 | 190 | 223 | 49 | 83 | 142 | 202 | 236
| kW | 33.5 | 32.8 | 32 | 31.3 | 30.9 | 34 | 33.3 | 32.3 | 31.6 | 31.2 | 34.2 | 33.5 | 32.5 | 31.7 | 31.2 | 34.4 | 33.7 | 32.6 | 31.8 | 31.5
| BF | 0 | 0.02 | 0.04 | 0.04 | 0.09 | 0.02 | 0.04 | 0.05 | 0.06 | 0.16 | 0.03 | 0.05 | 0.06 | 0.07 | 0.19 | 0.04 | 0.06 | 0.07 | 0.08 | 0.23
115 | TC | 274 | 256 | 230 | 207 | 188 | 281 | 263 | 237 | 216 | 198 | 284 | 266 | 239 | 207 | 199 | 287 | 269 | 237 | 210 | 200
| SHC | 18 | 45 | 90 | 135 | 172 | 18 | 49 | 103 | 153 | 192 | 19 | 52 | 110 | 160 | 199 | 20 | 56 | 112 | 169 | 200
| kW | 36.5 | 35.9 | 35.2 | 34.6 | 34 | 36.9 | 36.3 | 35.4 | 34.8 | 34.3 | 37.1 | 36.4 | 35.5 | 34.7 | 34.4 | 37.2 | 36.5 | 35.5 | 34.8 | 34.5
| BF | 0 | 0.02 | 0.04 | 0.04 | 0.11 | 0.02 | 0.04 | 0.05 | 0.06 | 0.17 | 0.03 | 0.05 | 0.06 | 0.08 | 0.2 | 0.04 | 0.06 | 0.07 | 0.09 | 0.25
48/50 035 (35 TON) STANDARD CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 12225 |  |  |  |  | 14000 |  |  |  |  | 15000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 435 | 407 | 372 | 335 | 320 | 451 | 413 | 377 | 343 | 334 | 441 | 427 | 381 | 349 | 342
| SHC | 142 | 175 | 239 | 297 | 320 | 159 | 186 | 258 | 322 | 334 | 150 | 204 | 269 | 331 | 342
| kW | 27.9 | 27 | 25.9 | 24.8 | 24.4 | 28.4 | 27.2 | 26.1 | 25.1 | 24.8 | 28 | 27.6 | 26.2 | 25.3 | 25.1
| BF | 0.06 | 0.07 | 0.08 | 0.1 | 0.28 | 0.08 | 0.09 | 0.1 | 0.13 | 0.35 | 0.09 | 0.1 | 0.1 | 0.16 | 0.38
85 | TC | 402 | 378 | 340 | 307 | 296 | 404 | 386 | 347 | 315 | 307 | 420 | 391 | 350 | 320 | 314
| SHC | 114 | 152 | 213 | 272 | 296 | 118 | 165 | 233 | 291 | 307 | 134 | 174 | 244 | 302 | 314
| kW | 30 | 29.2 | 27.9 | 26.9 | 26.5 | 30 | 29.5 | 28.2 | 27.2 | 26.9 | 30.6 | 29.7 | 28.3 | 27.3 | 27.1
| BF | 0.06 | 0.07 | 0.08 | 0.11 | 0.29 | 0.08 | 0.09 | 0.1 | 0.15 | 0.36 | 0.09 | 0.1 | 0.1 | 0.17 | 0.39
95 | TC | 366 | 343 | 308 | 277 | 271 | 373 | 349 | 313 | 288 | 281 | 376 | 353 | 316 | 292 | 287
| SHC | 85 | 122 | 186 | 247 | 271 | 93 | 135 | 205 | 265 | 281 | 97 | 142 | 216 | 275 | 287
| kW | 32.3 | 31.4 | 30.2 | 29.2 | 29 | 32.5 | 31.7 | 30.5 | 29.5 | 29.3 | 32.7 | 31.9 | 30.6 | 29.7 | 29.5
| BF | 0.06 | 0.08 | 0.08 | 0.11 | 0.3 | 0.08 | 0.09 | 0.1 | 0.16 | 0.37 | 0.09 | 0.1 | 0.11 | 0.18 | 0.4
105 | TC | 328 | 307 | 277 | 255 | 246 | 334 | 312 | 281 | 261 | 255 | 337 | 314 | 283 | 264 | 259
| SHC | 55 | 93 | 159 | 223 | 246 | 62 | 104 | 177 | 239 | 255 | 66 | 110 | 187 | 248 | 259
| kW | 34.7 | 33.9 | 32.8 | 32 | 31.8 | 35 | 34.2 | 33 | 32.3 | 32.1 | 35.1 | 34.3 | 33.1 | 32.4 | 32.2
| BF | 0.06 | 0.08 | 0.08 | 0.13 | 0.31 | 0.08 | 0.09 | 0.1 | 0.17 | 0.38 | 0.09 | 0.1 | 0.11 | 0.2 | 0.41
115 | TC | 291 | 272 | 240 | 219 | 208 | 295 | 275 | 243 | 223 | 215 | 296 | 276 | 245 | 224 | 219
| SHC | 24 | 64 | 128 | 187 | 208 | 29 | 74 | 145 | 202 | 215 | 33 | 78 | 155 | 209 | 219
| kW | 37.5 | 36.7 | 35.6 | 35 | 34.8 | 37.7 | 36.9 | 35.8 | 35.2 | 35.1 | 37.8 | 37 | 35.9 | 35.3 | 35.2
| BF | 0.06 | 0.08 | 0.08 | 0.15 | 0.33 | 0.08 | 0.09 | 0.1 | 0.19 | 0.39 | 0.09 | 0.1 | 0.11 | 0.21 | 0.42
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
76

## page 4
Performance data (cont)
Cooling Capacities (cont)
48/50 040 (40 TON) STANDARD CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 8000 |  |  |  |  | 10000 |  |  |  |  | 12000 |  |  |  |  | 14000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 453 | 431 | 395 | 358 | 329 | 479 | 450 | 418 | 379 | 340 | 498 | 473 | 433 | 393 | 363 | 513 | 486 | 455 | 406 | 377
| SHC | 162 | 177 | 207 | 247 | 288 | 175 | 185 | 233 | 275 | 313 | 178 | 201 | 252 | 300 | 342 | 183 | 212 | 281 | 326 | 362
| kW | 24.6 | 24.2 | 23.5 | 22.9 | 23.5 | 25.1 | 24.5 | 23.9 | 23.3 | 22.7 | 25.5 | 25 | 24.2 | 23.5 | 23.1 | 25.8 | 25.3 | 25.6 | 23.8 | 23.3
| BF | 0 | 0 | 0 | 0.12 | 0.3 | 0 | 0 | 0.14 | 0.37 | 0.34 | 0 | 0 | 0.14 | 0.36 | 0.37 | 0 | 0.18 | 0.43 | 0.36 | 0.42
85 | TC | 434 | 413 | 379 | 344 | 308 | 460 | 437 | 401 | 363 | 329 | 478 | 453 | 416 | 377 | 349 | 490 | 465 | 426 | 388 | 361
| SHC | 148 | 161 | 193 | 235 | 269 | 156 | 177 | 220 | 263 | 302 | 157 | 186 | 239 | 288 | 329 | 167 | 197 | 255 | 311 | 347
| kW | 27.1 | 26.7 | 26.1 | 25.5 | 25.1 | 27.6 | 27.1 | 26.5 | 25.8 | 25.4 | 28 | 27.5 | 26.7 | 26.1 | 25.6 | 28.2 | 27.7 | 26.9 | 26.3 | 25.8
| BF | 0 | 0 | 0.19 | 0.12 | 0.31 | 0 | 0 | 0.14 | 0.37 | 0.34 | 0 | 0.2 | 0.14 | 0.36 | 0.38 | 0 | 0.17 | 0.42 | 0.37 | 0.43
95 | TC | 416 | 396 | 362 | 325 | 294 | 439 | 418 | 384 | 357 | 316 | 456 | 445 | 397 | 373 | 332 | 467 | 459 | 406 | 360 | 345
| SHC | 134 | 146 | 180 | 220 | 257 | 141 | 163 | 206 | 261 | 290 | 142 | 177 | 224 | 289 | 312 | 151 | 197 | 241 | 287 | 330
| kW | 29.9 | 29.6 | 29 | 28.4 | 28.1 | 30.4 | 30 | 29.4 | 29.9 | 28.4 | 30.8 | 30.9 | 29.6 | 30 | 28.6 | 31 | 31.5 | 29.8 | 29 | 28.8
| BF | 0 | 0 | 0.16 | 0.12 | 0.31 | 0 | 0 | 0.13 | 0.36 | 0.34 | 0 | 0.18 | 0.14 | 0.35 | 0.4 | 0 | 0.17 | 0.42 | 0.37 | 0.44
105 | TC | 391 | 377 | 346 | 322 | 287 | 418 | 397 | 364 | 340 | 300 | 434 | 414 | 376 | 353 | 316 | 444 | 422 | 385 | 345 | 328
| SHC | 114 | 133 | 164 | 221 | 254 | 126 | 148 | 192 | 249 | 275 | 126 | 153 | 209 | 273 | 296 | 134 | 166 | 225 | 277 | 314
| kW | 33.3 | 32.9 | 32.4 | 33 | 32.7 | 33.7 | 33.3 | 32.7 | 33.6 | 31.8 | 34 | 33.6 | 33 | 34 | 32 | 34.3 | 33.8 | 33.1 | 33.1 | 32.2
| BF | 0 | 0 | 0.15 | 0.11 | 0.32 | 0 | 0 | 0.13 | 0.36 | 0.36 | 0 | 0.17 | 0.14 | 0.36 | 0.41 | 0 | 0.16 | 0.41 | 0.36 | 0.45
115 | TC | 374 | 360 | 325 | 305 | 261 | 395 | 374 | 342 | 309 | 283 | 409 | 389 | 354 | 320 | 299 | 418 | 398 | 362 | 329 | 309
| SHC | 103 | 123 | 154 | 209 | 226 | 108 | 132 | 176 | 222 | 259 | 110 | 136 | 194 | 245 | 280 | 117 | 149 | 209 | 266 | 296
| kW | 37 | 36.8 | 36.2 | 37 | 35.2 | 37.4 | 37 | 36.5 | 36 | 35.6 | 37.7 | 37.3 | 36.8 | 36.2 | 35.9 | 37.9 | 37.5 | 36.9 | 36.4 | 36.1
| BF | 0 | 0 | 0.13 | 0.11 | 0.37 | 0 | 0.18 | 0.12 | 0.35 | 0.37 | 0 | 0.16 | 0.13 | 0.35 | 0.42 | 0.2 | 0.15 | 0.41 | 0.37 | 0.46
48/50 040 (40 TON) STANDARD CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 16000 |  |  |  |  | 18000 |  |  |  |  | 20000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 523 | 496 | 452 | 414 | 393 | 532 | 504 | 460 | 420 | 405 | 540 | 511 | 466 | 427 | 404
| SHC | 192 | 225 | 285 | 346 | 380 | 196 | 236 | 301 | 364 | 405 | 199 | 246 | 316 | 376 | 385
| kW | 26 | 25.5 | 24.6 | 23.9 | 24.6 | 26.2 | 25.6 | 24.8 | 24 | 24.9 | 26.4 | 25.8 | 24.9 | 24.2 | 23.8
| BF | 0 | 0.18 | 0.42 | 0.38 | 0.45 | 0.23 | 0.18 | 0.42 | 0.41 | 0.49 | 0.21 | 0.5 | 0.42 | 0.44 | 0.57
85 | TC | 500 | 474 | 434 | 397 | 368 | 508 | 482 | 442 | 416 | 378 | 515 | 489 | 434 | 419 | 388
| SHC | 175 | 209 | 271 | 332 | 368 | 179 | 220 | 278 | 356 | 378 | 182 | 230 | 288 | 377 | 388
| kW | 28.4 | 27.9 | 27.1 | 26.4 | 25.9 | 28.6 | 28.1 | 27.3 | 27.8 | 26.1 | 28.8 | 28.2 | 27.2 | 27.4 | 26.3
| BF | 0.25 | 0.17 | 0.41 | 0.38 | 0.45 | 0.21 | 0.17 | 0.42 | 0.4 | 0.47 | 0.2 | 0.49 | 0.42 | 0.43 | 0.51
95 | TC | 476 | 453 | 414 | 377 | 351 | 484 | 476 | 421 | 381 | 363 | 491 | 466 | 441 | 390 | 373
| SHC | 158 | 193 | 256 | 316 | 351 | 161 | 219 | 271 | 333 | 363 | 165 | 214 | 300 | 348 | 373
| kW | 31.2 | 30.7 | 30 | 29.3 | 28.9 | 31.4 | 31.9 | 30.1 | 29.4 | 29.1 | 31.6 | 31 | 31.6 | 29.6 | 29.3
| BF | 0.22 | 0.17 | 0.41 | 0.39 | 0.46 | 0.2 | 0.17 | 0.41 | 0.41 | 0.5 | 0.19 | 0.48 | 0.42 | 0.44 | 0.54
105 | TC | 452 | 430 | 392 | 358 | 335 | 459 | 437 | 389 | 362 | 346 | 466 | 459 | 395 | 369 | 356
| SHC | 141 | 177 | 240 | 301 | 335 | 144 | 187 | 245 | 315 | 346 | 148 | 213 | 260 | 323 | 356
| kW | 34.5 | 34 | 33.3 | 32.7 | 32.3 | 34.6 | 34.1 | 33.2 | 32.8 | 32.5 | 34.8 | 35.3 | 33.4 | 32.9 | 32.7
| BF | 0.2 | 0.16 | 0.41 | 0.4 | 0.46 | 0.19 | 0.16 | 0.41 | 0.42 | 0.51 | 0.19 | 0.47 | 0.42 | 0.44 | 0.55
115 | TC | 427 | 405 | 369 | 335 | 316 | 450 | 411 | 375 | 344 | 327 | 441 | 416 | 380 | 351 | 336
| SHC | 119 | 159 | 224 | 284 | 316 | 143 | 169 | 239 | 298 | 327 | 132 | 178 | 252 | 310 | 336
| kW | 38.1 | 37.7 | 37.1 | 36.5 | 36.2 | 39.2 | 37.8 | 37.2 | 36.7 | 36.4 | 38.5 | 38 | 37.3 | 36.8 | 36.5
| BF | 0.18 | 0.16 | 0.41 | 0.41 | 0.48 | 0.18 | 0.16 | 0.41 | 0.44 | 0.52 | 0.18 | 0.47 | 0.42 | 0.46 | 0.56
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
79

## page 5
Performance data (cont)
Cooling Capacities (cont)
48/50 040 (40 TON) HIGH-CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 8000 |  |  |  |  | 10000 |  |  |  |  | 12000 |  |  |  |  | 14000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 445 | 418 | 373 | 335 | 300 | 479 | 451 | 403 | 363 | 337 | 495 | 467 | 424 | 385 | 358 | 518 | 486 | 440 | 401 | 382
| SHC | 133 | 154 | 191 | 234 | 273 | 148 | 174 | 224 | 275 | 322 | 152 | 190 | 252 | 314 | 352 | 170 | 211 | 279 | 348 | 381
| kW | 24.9 | 24.4 | 23.5 | 22.8 | 22.3 | 25.6 | 25 | 24 | 23.3 | 22.8 | 25.8 | 25.3 | 24.4 | 23.7 | 23.2 | 26.4 | 25.7 | 24.7 | 23.9 | 23.6
| BF | 0 | 0 | 0.06 | 0.13 | 0.12 | 0 | 0.08 | 0.17 | 0.13 | 0.17 | 0.12 | 0.08 | 0.16 | 0.14 | 0.24 | 0.1 | 0.22 | 0.17 | 0.16 | 0.3
85 | TC | 414 | 389 | 347 | 313 | 279 | 443 | 416 | 377 | 340 | 318 | 466 | 437 | 398 | 362 | 339 | 482 | 453 | 414 | 378 | 362
| SHC | 106 | 129 | 167 | 213 | 254 | 117 | 143 | 200 | 254 | 304 | 128 | 165 | 229 | 293 | 332 | 139 | 183 | 256 | 328 | 361
| kW | 27.2 | 26.6 | 25.8 | 25.2 | 24.7 | 27.7 | 27.2 | 26.4 | 25.7 | 25.2 | 28.2 | 27.6 | 26.7 | 26 | 25.6 | 28.5 | 27.9 | 27 | 26.3 | 26
| BF | 0 | 0.13 | 0.06 | 0.13 | 0.12 | 0 | 0.07 | 0.17 | 0.13 | 0.18 | 0.11 | 0.07 | 0.16 | 0.14 | 0.25 | 0.1 | 0.22 | 0.17 | 0.16 | 0.31
95 | TC | 384 | 361 | 322 | 290 | 261 | 412 | 387 | 351 | 317 | 299 | 433 | 407 | 372 | 338 | 318 | 449 | 424 | 388 | 354 | 339
| SHC | 80 | 104 | 144 | 193 | 236 | 90 | 118 | 177 | 234 | 285 | 99 | 138 | 206 | 273 | 311 | 111 | 158 | 234 | 307 | 339
| kW | 29.7 | 29.2 | 28.5 | 28 | 27.5 | 30.3 | 29.8 | 29.1 | 28.5 | 28.2 | 30.8 | 30.2 | 29.5 | 28.9 | 28.5 | 31.1 | 30.5 | 29.8 | 29.1 | 28.8
| BF | 0 | 0.1 | 0.05 | 0.13 | 0.14 | 0 | 0.07 | 0.17 | 0.13 | 0.19 | 0.1 | 0.07 | 0.16 | 0.14 | 0.26 | 0.09 | 0.22 | 0.17 | 0.17 | 0.3
105 | TC | 355 | 333 | 295 | 265 | 239 | 380 | 356 | 323 | 292 | 279 | 401 | 376 | 343 | 312 | 300 | 416 | 393 | 358 | 331 | 318
| SHC | 53 | 80 | 121 | 172 | 217 | 63 | 92 | 154 | 213 | 266 | 72 | 112 | 183 | 251 | 293 | 84 | 132 | 210 | 284 | 317
| kW | 32.7 | 32.3 | 31.7 | 31.3 | 31 | 33.3 | 32.8 | 32.3 | 31.8 | 31.6 | 33.8 | 33.3 | 32.7 | 32.2 | 31.9 | 34.1 | 33.6 | 33 | 32.4 | 32.2
| BF | 0 | 0.09 | 0.05 | 0.13 | 0.13 | 0.15 | 0.07 | 0.16 | 0.13 | 0.2 | 0.09 | 0.07 | 0.16 | 0.14 | 0.25 | 0.09 | 0.21 | 0.17 | 0.18 | 0.31
115 | TC | 324 | 303 | 266 | 239 | 220 | 346 | 323 | 294 | 264 | 259 | 365 | 343 | 313 | 284 | 276 | 381 | 358 | 329 | 300 | 295
| SHC | 27 | 56 | 99 | 151 | 199 | 35 | 65 | 131 | 192 | 248 | 44 | 85 | 159 | 229 | 269 | 56 | 105 | 187 | 255 | 295
| kW | 36.2 | 35.9 | 35.4 | 35.4 | 35.5 | 36.8 | 36.4 | 36 | 36 | 35.9 | 37.3 | 36.9 | 36.5 | 36.3 | 36.1 | 37.7 | 37.3 | 36.8 | 36.4 | 36.3
| BF | 0 | 0.08 | 0.05 | 0.12 | 0.15 | 0.11 | 0.06 | 0.16 | 0.13 | 0.21 | 0.09 | 0.07 | 0.16 | 0.15 | 0.27 | 0.08 | 0.21 | 0.17 | 0.18 | 0.34
48/50 040 (40 TON) HIGH-CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 16000 |  |  |  |  | 18000 |  |  |  |  | 20000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 523 | 498 | 452 | 414 | 399 | 540 | 508 | 462 | 426 | 413 | 549 | 516 | 471 | 428 | 419
| SHC | 176 | 227 | 304 | 377 | 399 | 194 | 243 | 327 | 394 | 413 | 205 | 257 | 350 | 406 | 419
| kW | 26.4 | 25.9 | 24.9 | 24.2 | 23.9 | 26.8 | 26.1 | 25.1 | 24.4 | 24.2 | 27 | 26.3 | 25.3 | 24.5 | 24.3
| BF | 0.1 | 0.21 | 0.18 | 0.19 | 0.36 | 0.28 | 0.22 | 0.19 | 0.23 | 0.4 | 0.26 | 0.22 | 0.2 | 0.26 | 0.46
85 | TC | 493 | 466 | 426 | 393 | 378 | 504 | 477 | 435 | 407 | 396 | 513 | 485 | 444 | 419 | 405
| SHC | 152 | 200 | 281 | 356 | 378 | 164 | 217 | 304 | 379 | 396 | 174 | 232 | 327 | 400 | 405
| kW | 28.7 | 28.1 | 27.3 | 26.6 | 26.3 | 29 | 28.3 | 27.5 | 26.8 | 26.6 | 29.1 | 28.5 | 27.6 | 27.1 | 26.8
| BF | 0.09 | 0.21 | 0.18 | 0.2 | 0.37 | 0.27 | 0.22 | 0.19 | 0.24 | 0.42 | 0.26 | 0.22 | 0.2 | 0.28 | 0.45
95 | TC | 462 | 439 | 400 | 370 | 357 | 473 | 449 | 409 | 384 | 370 | 480 | 454 | 417 | 398 | 382
| SHC | 125 | 177 | 259 | 333 | 357 | 138 | 192 | 282 | 357 | 370 | 146 | 205 | 305 | 380 | 382
| kW | 31.4 | 30.8 | 30 | 29.4 | 29.1 | 31.6 | 31 | 30.2 | 29.7 | 29.4 | 31.7 | 31.2 | 30.4 | 29.9 | 29.6
| BF | 0.09 | 0.21 | 0.18 | 0.21 | 0.38 | 0.27 | 0.22 | 0.19 | 0.25 | 0.43 | 0.26 | 0.22 | 0.2 | 0.28 | 0.46
105 | TC | 428 | 408 | 371 | 346 | 335 | 439 | 417 | 380 | 361 | 348 | 449 | 422 | 388 | 377 | 361
| SHC | 97 | 151 | 235 | 311 | 335 | 110 | 167 | 259 | 335 | 348 | 122 | 179 | 281 | 360 | 361
| kW | 34.4 | 34 | 33.3 | 32.7 | 32.5 | 34.7 | 34.2 | 33.5 | 33 | 32.8 | 34.9 | 34.3 | 33.6 | 33.4 | 33
| BF | 0.09 | 0.21 | 0.18 | 0.22 | 0.39 | 0.26 | 0.21 | 0.19 | 0.26 | 0.44 | 0.26 | 0.22 | 0.2 | 0.29 | 0.48
115 | TC | 393 | 374 | 338 | 322 | 310 | 403 | 385 | 347 | 335 | 324 | 412 | 390 | 354 | 347 | 334
| SHC | 70 | 126 | 210 | 288 | 310 | 82 | 142 | 233 | 310 | 324 | 93 | 155 | 255 | 327 | 334
| kW | 38.1 | 37.6 | 37 | 36.7 | 36.5 | 38.4 | 37.9 | 37.3 | 36.9 | 36.7 | 38.6 | 38.1 | 37.5 | 37.2 | 36.9
| BF | 0.08 | 0.21 | 0.18 | 0.23 | 0.4 | 0.27 | 0.21 | 0.19 | 0.27 | 0.45 | 0.25 | 0.22 | 0.2 | 0.29 | 0.49
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
82

## page 6
Performance data (cont)
Cooling Capacities (cont)
48/50 050 (50 TON) STANDARD CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 10000 |  |  |  |  | 12500 |  |  |  |  | 15000 |  |  |  |  | 17500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 590 | 563 | 519 | 472 | 450 | 625 | 598 | 549 | 502 | 465 | 652 | 619 | 571 | 524 | 491 | 671 | 638 | 588 | 551 | 513
| SHC | 206 | 233 | 275 | 329 | 413 | 219 | 248 | 308 | 370 | 450 | 228 | 256 | 336 | 406 | 480 | 235 | 281 | 362 | 473 | 513
| kW | 33.2 | 32.7 | 32.1 | 31.5 | 31.8 | 33.8 | 33.3 | 32.5 | 31.9 | 31.4 | 34.2 | 33.7 | 32.9 | 32.3 | 31.6 | 34.5 | 34 | 33.2 | 32.5 | 32
| BF | 0.02 | 0 | 0.13 | 0.08 | 0.13 | 0 | 0 | 0.11 | 0.28 | 0.18 | 0 | 0.16 | 0.35 | 0.28 | 0.25 | 0 | 0.14 | 0.33 | 0.2 | 0.32
85 | TC | 565 | 538 | 493 | 450 | 429 | 598 | 572 | 525 | 479 | 445 | 620 | 590 | 545 | 500 | 467 | 638 | 610 | 562 | 513 | 492
| SHC | 184 | 213 | 256 | 312 | 397 | 194 | 228 | 290 | 353 | 431 | 206 | 234 | 317 | 388 | 467 | 212 | 260 | 343 | 420 | 492
| kW | 36.7 | 36.2 | 35.6 | 35.2 | 35.5 | 37.3 | 36.8 | 36.1 | 35.6 | 35 | 37.7 | 37.2 | 36.5 | 35.9 | 35.4 | 38 | 37.5 | 36.8 | 36.2 | 35.8
| BF | 0 | 0 | 0.11 | 0.08 | 0.14 | 0 | 0 | 0.1 | 0.27 | 0.19 | 0 | 0.15 | 0.34 | 0.28 | 0.26 | 0 | 0.13 | 0.32 | 0.29 | 0.34
95 | TC | 538 | 513 | 466 | 424 | 407 | 568 | 544 | 498 | 451 | 436 | 593 | 563 | 517 | 473 | 444 | 607 | 581 | 533 | 487 | 467
| SHC | 163 | 195 | 236 | 293 | 380 | 172 | 208 | 270 | 332 | 424 | 177 | 215 | 296 | 369 | 444 | 189 | 238 | 322 | 402 | 467
| kW | 40.8 | 40.4 | 39.9 | 39.5 | 40.4 | 41.4 | 41 | 40.4 | 39.9 | 40.6 | 41.9 | 41.4 | 40.8 | 40.3 | 39.9 | 42.2 | 41.7 | 41.1 | 40.5 | 40.1
| BF | 0 | 0 | 0.1 | 0.28 | 0.14 | 0 | 0 | 0.1 | 0.26 | 0.21 | 0 | 0.13 | 0.33 | 0.27 | 0.27 | 0 | 0.13 | 0.32 | 0.29 | 0.35
105 | TC | 507 | 483 | 439 | 398 | 383 | 537 | 511 | 469 | 423 | 398 | 559 | 533 | 486 | 445 | 420 | 572 | 547 | 502 | 458 | 442
| SHC | 140 | 174 | 216 | 274 | 360 | 148 | 177 | 250 | 311 | 388 | 154 | 196 | 275 | 350 | 420 | 164 | 215 | 301 | 382 | 442
| kW | 45.6 | 45.3 | 44.9 | 45 | 46.4 | 46.2 | 45.9 | 45.4 | 45.3 | 45.3 | 46.7 | 46.3 | 45.8 | 45.5 | 45.5 | 46.9 | 46.6 | 46.1 | 45.8 | 45.6
| BF | 0 | 0 | 0.09 | 0.26 | 0.15 | 0 | 0.15 | 0.09 | 0.26 | 0.22 | 0 | 0.13 | 0.33 | 0.27 | 0.29 | 0.17 | 0.12 | 0.31 | 0.29 | 0.36
115 | TC | 474 | 454 | 429 | 399 | 343 | 501 | 477 | 454 | 408 | 375 | 521 | 497 | 470 | 424 | 394 | 534 | 510 | 483 | 434 | 415
| SHC | 116 | 145 | 224 | 294 | 321 | 124 | 155 | 253 | 320 | 366 | 129 | 173 | 280 | 357 | 394 | 138 | 191 | 305 | 388 | 415
| kW | 51.1 | 51 | 51.3 | 52.7 | 52.2 | 51.7 | 51.5 | 51.6 | 52.1 | 52.3 | 52.1 | 51.9 | 51.9 | 52.1 | 52.3 | 52.4 | 52.2 | 52 | 52.1 | 52.2
| BF | 0 | 0 | 0.15 | 0.13 | 0.18 | 0 | 0.13 | 0.17 | 0.16 | 0.24 | 0 | 0.12 | 0.19 | 0.18 | 0.31 | 0.15 | 0.12 | 0.21 | 0.21 | 0.38
48/50 050 (50 TON) STANDARD CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
20000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57
75 | TC | 684 | 650 | 599 | 562 | 531
| SHC | 241 | 296 | 383 | 503 | 531
| kW | 34.8 | 34.2 | 33.4 | 32.7 | 32.3
| BF | 0.22 | 0.14 | 0.33 | 0.22 | 0.37
85 | TC | 650 | 621 | 573 | 536 | 508
| SHC | 217 | 274 | 363 | 483 | 508
| kW | 38.3 | 37.7 | 36.9 | 36.3 | 36
| BF | 0.18 | 0.13 | 0.32 | 0.22 | 0.39
95 | TC | 618 | 591 | 543 | 497 | 484
| SHC | 194 | 251 | 342 | 427 | 484
| kW | 42.4 | 41.9 | 41.3 | 40.7 | 40.4
| BF | 0.17 | 0.13 | 0.32 | 0.3 | 0.4
105 | TC | 583 | 557 | 511 | 492 | 458
| SHC | 169 | 228 | 320 | 447 | 458
| kW | 47.2 | 46.8 | 46.2 | 46.2 | 45.6
| BF | 0.16 | 0.12 | 0.32 | 0.25 | 0.41
115 | TC | 544 | 519 | 492 | 448 | 430
| SHC | 142 | 203 | 326 | 406 | 430
| kW | 52.6 | 52.3 | 52.1 | 51.9 | 52.1
| BF | 0.14 | 0.12 | 0.22 | 0.26 | 0.43
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
85

## page 7
Performance data (cont)
Cooling Capacities (cont)
48/50 050 (50 TON) HIGH-CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 10000 |  |  |  |  | 12500 | [5 empty] | 15000 |  |  |  |  | 17500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 |  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 589 | 555 | 500 | 454 | 407 | 633 | 597 | 538 | 489 | 452 |  | 673 | 619 | 563 | 515 | 482 | 697 | 653 | 583 | 534 | 509
| SHC | 191 | 216 | 261 | 316 | 365 | 209 | 238 | 301 | 366 | 427 |  | 241 | 260 | 335 | 411 | 468 | 251 | 297 | 367 | 452 | 509
| kW | 33.4 | 32.8 | 32 | 31.2 | 30.5 | 34.2 | 33.6 | 32.5 | 31.7 | 31.1 |  | 35.1 | 33.9 | 33 | 32.1 | 31.5 | 35.4 | 34.6 | 33.3 | 32.4 | 32
| BF | 0 | 0 | 0.07 | 0.16 | 0.13 | 0 | 0.11 | 0.24 | 0.16 | 0.18 |  | 0 | 0.1 | 0.21 | 0.18 | 0.24 | 0.14 | 0.3 | 0.21 | 0.19 | 0.28
85 | TC | 552 | 523 | 468 | 445 | 408 | 592 | 557 | 506 | 470 | 436 |  | 618 | 581 | 531 | 488 | 460 | 640 | 601 | 550 | 502 | 483
| SHC | 160 | 190 | 233 | 300 | 371 | 175 | 205 | 275 | 345 | 424 |  | 192 | 228 | 309 | 390 | 460 | 201 | 252 | 340 | 432 | 483
| kW | 36.7 | 36.1 | 35.2 | 34.7 | 34.3 | 37.4 | 36.8 | 35.8 | 35.1 | 34.6 |  | 37.9 | 37.2 | 36.3 | 35.5 | 35 | 38.3 | 37.6 | 36.6 | 35.8 | 35.4
| BF | 0 | 0 | 0.07 | 0.07 | 0.08 | 0 | 0.1 | 0.23 | 0.09 | 0.13 |  | 0 | 0.09 | 0.21 | 0.1 | 0.2 | 0.13 | 0.29 | 0.21 | 0.12 | 0.29
95 | TC | 514 | 485 | 436 | 418 | 382 | 551 | 510 | 475 | 441 | 417 |  | 575 | 543 | 499 | 457 | 435 | 597 | 564 | 518 | 470 | 453
| SHC | 128 | 159 | 206 | 279 | 350 | 142 | 162 | 249 | 323 | 406 |  | 158 | 198 | 282 | 365 | 435 | 166 | 221 | 314 | 405 | 453
| kW | 40.5 | 39.9 | 39.1 | 38.9 | 38.5 | 41.2 | 40.5 | 39.8 | 39.3 | 38.9 |  | 41.7 | 41.1 | 40.3 | 39.7 | 39.2 | 42.2 | 41.5 | 40.7 | 39.9 | 39.5
| BF | 0 | 0 | 0.07 | 0.07 | 0.08 | 0 | 0.09 | 0.22 | 0.08 | 0.14 |  | 0.15 | 0.09 | 0.2 | 0.1 | 0.22 | 0.12 | 0.28 | 0.21 | 0.13 | 0.3
105 | TC | 477 | 450 | 402 | 387 | 365 | 511 | 473 | 440 | 408 | 363 |  | 537 | 504 | 464 | 423 | 405 | 555 | 525 | 482 | 436 | 425
| SHC | 97 | 130 | 179 | 255 | 334 | 110 | 131 | 222 | 298 | 354 |  | 121 | 166 | 255 | 339 | 405 | 133 | 191 | 286 | 378 | 425
| kW | 44.9 | 44.5 | 43.9 | 43.9 | 43.6 | 45.7 | 45.1 | 44.6 | 44.3 | 43.8 |  | 46.3 | 45.7 | 45.1 | 44.7 | 44.2 | 46.7 | 46.2 | 45.5 | 44.8 | 44.5
| BF | 0 | 0 | 0.06 | 0.07 | 0.11 | 0 | 0.09 | 0.21 | 0.08 | 0.16 |  | 0.13 | 0.08 | 0.2 | 0.1 | 0.24 | 0.11 | 0.27 | 0.2 | 0.13 | 0.31
115 | TC | 438 | 412 | 365 | 353 | 340 | 469 | 430 | 402 | 372 | 333 |  | 493 | 461 | 424 | 387 | 381 | 511 | 482 | 441 | 400 | 398
| SHC | 64 | 100 | 151 | 230 | 314 | 77 | 99 | 194 | 271 | 326 |  | 87 | 134 | 226 | 312 | 381 | 99 | 159 | 256 | 345 | 398
| kW | 50.1 | 49.9 | 49.6 | 50.5 | 51.4 | 50.9 | 50.4 | 50.3 | 50.9 | 50.6 |  | 51.5 | 51.1 | 50.8 | 51 | 50.7 | 52 | 51.5 | 51.1 | 50.2 | 50.7
| BF | 0 | 0.1 | 0.06 | 0.07 | 0.11 | 0 | 0.08 | 0.21 | 0.08 | 0.18 |  | 0.11 | 0.08 | 0.2 | 0.11 | 0.26 | 0.1 | 0.26 | 0.2 | 0.15 | 0.33
48/50 050 (50 TON) HIGH- CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
20000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57
75 | TC | 707 | 650 | 597 | 548 | 527
| SHC | 262 | 298 | 395 | 487 | 527
| kW | 35.6 | 34.3 | 33.5 | 32.7 | 32.3
| BF | 0.12 | 0.26 | 0.22 | 0.22 | 0.35
85 | TC | 650 | 616 | 564 | 517 | 506
| SHC | 211 | 271 | 369 | 473 | 506
| kW | 38.5 | 37.9 | 36.9 | 36.1 | 35.8
| BF | 0.12 | 0.26 | 0.21 | 0.15 | 0.35
95 | TC | 611 | 579 | 532 | 500 | 471
| SHC | 181 | 242 | 342 | 458 | 471
| kW | 42.5 | 41.8 | 40.9 | 40.2 | 39.8
| BF | 0.11 | 0.25 | 0.21 | 0.16 | 0.36
105 | TC | 570 | 539 | 496 | 446 | 442
| SHC | 148 | 211 | 315 | 411 | 442
| kW | 47.1 | 46.5 | 45.8 | 44.9 | 44.8
| BF | 0.11 | 0.25 | 0.21 | 0.16 | 0.38
115 | TC | 524 | 495 | 454 | 411 | 403
| SHC | 115 | 178 | 285 | 378 | 403
| kW | 52.4 | 51.8 | 51.4 | 50.6 | 50.6
| BF | 0.1 | 0.25 | 0.21 | 0.18 | 0.39
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC. | [11 empty] | 2. Interpolation is permissible. 3. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat. 5. SHC values provided are in subcooling mode with the gas bypass valve closed and reflect the maximum SHC in subcooling mode. The P Series innovative modulating valve system can reduce SHC as needed to meet the supply air set point requirement with mini- mal change in latent capacity. This will provide variable SHC to meet the space load.
88

## page 8
Performance data (cont)
Cooling Capacities (cont)
48/50 055 (55 TON) STANDARD CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 11000 |  |  |  |  | 13750 |  |  |  |  | 16500 |  |  |  |  | 19250
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 648 | 613 | 562 | 501 | 464 | 681 | 647 | 598 | 541 | 494 | 704 | 668 | 615 | 561 | 523 | 719 | 684 | 630 | 578 | 549
| SHC | 206 | 244 | 311 | 364 | 434 | 221 | 269 | 354 | 424 | 487 | 236 | 290 | 383 | 471 | 523 | 248 | 310 | 415 | 515 | 549
| kW | 41.9 | 41.3 | 40.5 | 39.7 | 39.2 | 42.5 | 41.9 | 41.2 | 40.2 | 39.6 | 43 | 42.3 | 41.4 | 40.5 | 40 | 43.3 | 42.6 | 41.6 | 40.8 | 40.3
| BF | 0.03 | 0.08 | 0.08 | 0.07 | 0.08 | 0.12 | 0.1 | 0.09 | 0.09 | 0.14 | 0.14 | 0.12 | 0.12 | 0.11 | 0.23 | 0.16 | 0.15 | 0.14 | 0.14 | 0.31
85 | TC | 573 | 588 | 536 | 488 | 443 | 652 | 619 | 567 | 516 | 472 | 672 | 639 | 586 | 537 | 500 | 687 | 654 | 602 | 551 | 525
| SHC | 139 | 226 | 292 | 357 | 416 | 200 | 249 | 329 | 407 | 466 | 213 | 269 | 361 | 453 | 500 | 225 | 289 | 394 | 495 | 525
| kW | 44.8 | 45.1 | 44.3 | 43.7 | 43 | 46.2 | 45.6 | 44.8 | 44.1 | 43.4 | 46.6 | 46 | 45.1 | 44.3 | 43.8 | 46.9 | 46.3 | 45.3 | 44.5 | 44.2
| BF | 0.04 | 0.08 | 0.08 | 0.07 | 0.09 | 0.12 | 0.1 | 0.09 | 0.09 | 0.15 | 0.14 | 0.13 | 0.12 | 0.12 | 0.24 | 0.16 | 0.15 | 0.14 | 0.14 | 0.32
95 | TC | 591 | 560 | 510 | 463 | 422 | 621 | 515 | 538 | 490 | 455 | 640 | 533 | 558 | 509 | 476 | 652 | 623 | 572 | 522 | 500
| SHC | 165 | 206 | 273 | 338 | 403 | 178 | 154 | 309 | 388 | 455 | 191 | 172 | 342 | 433 | 476 | 200 | 267 | 373 | 473 | 500
| kW | 50 | 49.5 | 48.8 | 48.1 | 47.7 | 50.5 | 48.6 | 49.2 | 48.5 | 48.4 | 50.9 | 48.9 | 49.4 | 48.7 | 48.2 | 51.1 | 50.6 | 49.7 | 48.9 | 48.6
| BF | 0.05 | 0.08 | 0.08 | 0.07 | 0.1 | 0.12 | 0.1 | 0.09 | 0.09 | 0.16 | 0.14 | 0.13 | 0.12 | 0.12 | 0.26 | 0.16 | 0.15 | 0.14 | 0.14 | 0.33
105 | TC | 560 | 529 | 481 | 436 | 395 | 588 | 557 | 508 | 462 | 424 | 606 | 576 | 526 | 479 | 451 | 623 | 589 | 539 | 491 | 474
| SHC | 143 | 185 | 253 | 319 | 374 | 156 | 205 | 288 | 368 | 424 | 167 | 225 | 320 | 411 | 451 | 183 | 243 | 351 | 450 | 474
| kW | 55 | 54.5 | 53.8 | 53.6 | 53.3 | 55.5 | 54.9 | 54.1 | 53.6 | 53.3 | 55.8 | 55.2 | 54.4 | 53.7 | 53.5 | 56.2 | 55.5 | 54.6 | 53.8 | 53.6
| BF | 0.05 | 0.08 | 0.08 | 0.08 | 0.12 | 0.12 | 0.1 | 0.1 | 0.09 | 0.18 | 0.14 | 0.13 | 0.12 | 0.12 | 0.27 | 0.16 | 0.15 | 0.14 | 0.15 | 0.35
115 | TC | 526 | 497 | 451 | 408 | 371 | 552 | 523 | 476 | 432 | 398 | 569 | 540 | 493 | 448 | 424 | 584 | 552 | 505 | 460 | 457
| SHC | 121 | 163 | 232 | 299 | 352 | 132 | 183 | 266 | 347 | 398 | 143 | 201 | 298 | 389 | 424 | 157 | 219 | 328 | 422 | 457
| kW | 60.7 | 60.3 | 60 | 60.1 | 60 | 61 | 60.5 | 60 | 59.8 | 59.8 | 61.4 | 60.8 | 60.1 | 59.8 | 59.7 | 61.7 | 61 | 60.2 | 59.7 | 60.4
| BF | 0.05 | 0.08 | 0.08 | 0.08 | 0.14 | 0.12 | 0.1 | 0.1 | 0.1 | 0.2 | 0.14 | 0.13 | 0.12 | 0.12 | 0.29 | 0.16 | 0.15 | 0.14 | 0.17 | 0.37
48/50 055 (55 TON) STANDARD CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 22000 |  |  |  |  | 24750
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 732 | 699 | 641 | 589 | 571 | 742 | 709 | 651 | 598 | 597
| SHC | 260 | 332 | 445 | 553 | 571 | 272 | 350 | 474 | 584 | 597
| kW | 43.5 | 43 | 41.9 | 41 | 40.7 | 43.8 | 43.2 | 42.1 | 41.1 | 41.3
| BF | 0.18 | 0.16 | 0.15 | 0.17 | 0.37 | 0.2 | 0.18 | 0.17 | 0.2 | 0.43
85 | TC | 698 | 666 | 554 | 561 | 555 | 707 | 677 | 621 | 571 | 564
| SHC | 237 | 307 | 366 | 531 | 555 | 248 | 327 | 453 | 560 | 564
| kW | 47.2 | 46.5 | 44.5 | 44.7 | 44.9 | 47.4 | 46.8 | 45.7 | 44.8 | 44.8
| BF | 0.18 | 0.17 | 0.15 | 0.17 | 0.39 | 0.2 | 0.18 | 0.17 | 0.21 | 0.44
95 | TC | 665 | 634 | 582 | 532 | 530 | 674 | 642 | 591 | 543 | 545
| SHC | 214 | 285 | 403 | 508 | 530 | 224 | 302 | 431 | 531 | 545
| kW | 51.4 | 50.8 | 49.8 | 49 | 49.4 | 51.6 | 51 | 50 | 49.2 | 49.5
| BF | 0.18 | 0.17 | 0.15 | 0.18 | 0.4 | 0.2 | 0.18 | 0.17 | 0.23 | 0.45
105 | TC | 633 | 599 | 549 | 503 | 502 | 638 | 607 | 557 | 514 | 518
| SHC | 193 | 261 | 380 | 476 | 502 | 200 | 278 | 408 | 504 | 518
| kW | 56.4 | 55.7 | 54.8 | 54 | 54.4 | 56.4 | 55.8 | 54.9 | 54.1 | 54.6
| BF | 0.18 | 0.17 | 0.16 | 0.2 | 0.41 | 0.2 | 0.18 | 0.17 | 0.24 | 0.46
115 | TC | 591 | 562 | 514 | 473 | 463 | 599 | 569 | 522 | 482 | 488
| SHC | 164 | 237 | 357 | 449 | 463 | 174 | 253 | 384 | 475 | 488
| kW | 61.8 | 61.2 | 60.3 | 59.7 | 59.7 | 62 | 61.3 | 60.4 | 59.8 | 60.3
| BF | 0.18 | 0.17 | 0.16 | 0.22 | 0.43 | 0.2 | 0.18 | 0.17 | 0.26 | 0.48
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
91

## page 9
Performance data (cont)
Cooling Capacities (cont)
48/50 055 (55 TON) HIGH-CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 11000 |  |  |  |  | 13750 |  |  |  |  | 16500 |  |  |  |  | 19250
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 639 | 598 | 533 | 481 | 441 | 678 | 632 | 569 | 510 | 476 | 704 | 658 | 588 | 535 | 500 | 721 | 671 | 618 | 550 | 524
| SHC | 174 | 211 | 270 | 338 | 411 | 194 | 237 | 316 | 392 | 467 | 213 | 263 | 350 | 448 | 500 | 227 | 282 | 403 | 496 | 524
| kW | 42 | 41.3 | 40.2 | 39.3 | 38.7 | 42.8 | 42 | 40.9 | 39.9 | 39.2 | 43.3 | 42.5 | 41.2 | 40.3 | 39.7 | 43.6 | 42.7 | 41.7 | 40.6 | 40.2
| BF | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.05 | 0.03 | 0.02 | 0.03 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.17 | 0.08 | 0.06 | 0.05 | 0.06 | 0.26
85 | TC | 591 | 553 | 497 | 449 | 415 | 618 | 577 | 534 | 473 | 446 | 663 | 616 | 552 | 491 | 467 | 676 | 629 | 566 | 502 | 490
| SHC | 133 | 172 | 241 | 311 | 387 | 143 | 189 | 286 | 360 | 438 | 182 | 231 | 322 | 410 | 467 | 192 | 251 | 358 | 453 | 490
| kW | 45.4 | 44.7 | 43.7 | 43 | 42.5 | 46 | 45.2 | 44.3 | 43.3 | 42.8 | 46.7 | 45.9 | 44.7 | 43.7 | 43.2 | 47 | 46.2 | 45 | 43.9 | 43.6
| BF | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.05 | 0.03 | 0.02 | 0.03 | 0.1 | 0.06 | 0.04 | 0.04 | 0.04 | 0.18 | 0.07 | 0.06 | 0.05 | 0.06 | 0.27
95 | TC | 563 | 525 | 469 | 415 | 395 | 595 | 552 | 493 | 436 | 416 | 618 | 573 | 510 | 452 | 433 | 621 | 568 | 523 | 467 | 455
| SHC | 113 | 151 | 219 | 283 | 371 | 128 | 172 | 253 | 330 | 410 | 144 | 195 | 288 | 378 | 433 | 144 | 197 | 323 | 424 | 455
| kW | 49.6 | 48.9 | 47.9 | 47.3 | 46.9 | 50.2 | 49.4 | 48.3 | 47.5 | 47.2 | 50.7 | 49.8 | 48.6 | 47.7 | 47.4 | 50.9 | 49.9 | 48.9 | 47.9 | 47.7
| BF | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.05 | 0.03 | 0.02 | 0.03 | 0.11 | 0.06 | 0.04 | 0.04 | 0.04 | 0.2 | 0.07 | 0.05 | 0.05 | 0.06 | 0.28
105 | TC | 511 | 476 | 423 | 380 | 364 | 554 | 512 | 454 | 407 | 389 | 577 | 514 | 457 | 413 | 399 | 572 | 529 | 468 | 433 | 417
| SHC | 70 | 111 | 181 | 256 | 339 | 97 | 141 | 222 | 310 | 384 | 114 | 145 | 243 | 346 | 399 | 106 | 167 | 276 | 388 | 417
| kW | 54.3 | 53.6 | 52.7 | 52.5 | 52.6 | 55 | 54.1 | 53.1 | 52.4 | 52.3 | 55.5 | 54.3 | 53.2 | 52.5 | 52.3 | 55.6 | 54.6 | 53.4 | 52.7 | 52.5
| BF | 0.02 | 0.02 | 0.02 | 0.02 | 0.06 | 0.05 | 0.03 | 0.03 | 0.03 | 0.12 | 0.06 | 0.04 | 0.04 | 0.04 | 0.21 | 0.07 | 0.05 | 0.05 | 0.09 | 0.29
115 | TC | 469 | 434 | 383 | 343 | 334 | 490 | 453 | 399 | 358 | 350 | 507 | 467 | 411 | 374 | 363 | 520 | 477 | 420 | 393 | 378
| SHC | 39 | 80 | 151 | 228 | 311 | 44 | 93 | 178 | 270 | 347 | 56 | 110 | 208 | 316 | 363 | 68 | 128 | 240 | 351 | 378
| kW | 60 | 59.3 | 58.9 | 59.4 | 59.9 | 60.4 | 59.5 | 58.7 | 58.7 | 59 | 60.8 | 59.7 | 58.7 | 58.4 | 58.5 | 61.2 | 59.9 | 58.7 | 58.3 | 58.3
| BF | 0.02 | 0.02 | 0.02 | 0.02 | 0.08 | 0.05 | 0.03 | 0.03 | 0.03 | 0.14 | 0.06 | 0.04 | 0.04 | 0.05 | 0.23 | 0.07 | 0.05 | 0.05 | 0.11 | 0.31
48/50 055 (55 TON) HIGH-CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 22000 |  |  |  |  | 24750
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 739 | 686 | 746 | 568 | 555 | 752 | 697 | 750 | 582 | 576
| SHC | 246 | 307 | 653 | 537 | 555 | 263 | 329 | 668 | 569 | 576
| kW | 43.9 | 43 | 44.1 | 40.9 | 40.7 | 44.1 | 43.2 | 44.2 | 41.2 | 41.1
| BF | 0.09 | 0.07 | 0.36 | 0.1 | 0.33 | 0.1 | 0.08 | 0.37 | 0.14 | 0.39
85 | TC | 692 | 643 | 573 | 521 | 518 | 704 | 653 | 584 | 531 | 537
| SHC | 210 | 274 | 389 | 491 | 518 | 226 | 297 | 426 | 520 | 537
| kW | 47.3 | 46.5 | 45.2 | 44.2 | 44.1 | 47.6 | 46.7 | 45.4 | 44.5 | 44.5
| BF | 0.09 | 0.07 | 0.06 | 0.11 | 0.34 | 0.1 | 0.08 | 0.07 | 0.15 | 0.4
95 | TC | 636 | 579 | 535 | 484 | 473 | 666 | 612 | 543 | 495 | 489
| SHC | 161 | 218 | 359 | 456 | 473 | 197 | 264 | 393 | 486 | 489
| kW | 51.3 | 50.1 | 49.1 | 48.2 | 48.1 | 51.7 | 50.6 | 49.3 | 48.4 | 48.4
| BF | 0.08 | 0.07 | 0.06 | 0.12 | 0.35 | 0.1 | 0.08 | 0.07 | 0.16 | 0.4
105 | TC | 586 | 539 | 475 | 445 | 434 | 593 | 545 | 484 | 454 | 448
| SHC | 122 | 188 | 308 | 419 | 434 | 134 | 207 | 343 | 446 | 448
| kW | 56 | 54.8 | 53.5 | 52.9 | 52.8 | 56.2 | 55 | 53.7 | 53.1 | 53
| BF | 0.09 | 0.07 | 0.06 | 0.13 | 0.36 | 0.1 | 0.08 | 0.07 | 0.17 | 0.42
115 | TC | 532 | 486 | 427 | 404 | 393 | 543 | 494 | 434 | 410 | 405
| SHC | 82 | 148 | 272 | 380 | 393 | 98 | 169 | 304 | 405 | 405
| kW | 61.6 | 60.1 | 58.8 | 58.4 | 58.3 | 62 | 60.3 | 58.9 | 58.4 | 58.4
| BF | 0.09 | 0.07 | 0.06 | 0.15 | 0.38 | 0.1 | 0.08 | 0.08 | 0.19 | 0.43
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
94

## page 10
Performance data (cont)
Cooling Capacities (cont)
48/50 060 (60 TON) STANDARD CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 12000 |  |  |  |  | 15000 |  |  |  |  | 18000 |  |  |  |  | 21000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 711 | 674 | 615 | 560 | 508 | 754 | 710 | 650 | 600 | 539 | 771 | 734 | 674 | 626 | 570 | 789 | 758 | 692 | 634 | 599
| SHC | 224 | 268 | 339 | 408 | 473 | 247 | 293 | 379 | 469 | 530 | 255 | 315 | 415 | 522 | 570 | 269 | 344 | 450 | 559 | 599
| kW | 48.5 | 47.7 | 46.6 | 45.7 | 44.8 | 49.5 | 48.5 | 47.2 | 46.5 | 45.2 | 49.9 | 49 | 47.7 | 47.1 | 45.8 | 50.3 | 49.7 | 48.1 | 47 | 46.3
| BF | 0.02 | 0.08 | 0.08 | 0.08 | 0.09 | 0.13 | 0.11 | 0.1 | 0.1 | 0.14 | 0.15 | 0.13 | 0.13 | 0.12 | 0.23 | 0.17 | 0.16 | 0.15 | 0.15 | 0.31
85 | TC | 681 | 646 | 589 | 536 | 482 | 723 | 688 | 622 | 567 | 518 | 746 | 702 | 645 | 589 | 546 | 755 | 717 | 661 | 605 | 586
| SHC | 202 | 246 | 318 | 389 | 446 | 226 | 279 | 357 | 442 | 508 | 239 | 292 | 393 | 492 | 546 | 244 | 311 | 427 | 537 | 586
| kW | 52.8 | 52 | 51 | 50 | 49.2 | 53.8 | 53.1 | 51.6 | 50.6 | 49.6 | 54.3 | 53.2 | 52 | 51 | 50.2 | 54.4 | 53.5 | 52.4 | 51.3 | 51.6
| BF | 0.04 | 0.08 | 0.08 | 0.08 | 0.08 | 0.13 | 0.11 | 0.1 | 0.1 | 0.16 | 0.15 | 0.13 | 0.13 | 0.12 | 0.24 | 0.17 | 0.16 | 0.15 | 0.15 | 0.32
95 | TC | 649 | 615 | 561 | 510 | 462 | 681 | 647 | 592 | 539 | 494 | 703 | 668 | 613 | 560 | 521 | 727 | 684 | 629 | 575 | 548
| SHC | 179 | 224 | 298 | 370 | 435 | 193 | 247 | 335 | 422 | 485 | 206 | 268 | 370 | 470 | 521 | 227 | 288 | 404 | 513 | 548
| kW | 57.7 | 57 | 55.9 | 55.2 | 54.8 | 58.4 | 57.6 | 56.5 | 55.5 | 54.8 | 58.9 | 58.1 | 56.9 | 55.9 | 55.2 | 59.6 | 58.4 | 57.3 | 56.2 | 55.7
| BF | 0.05 | 0.08 | 0.08 | 0.08 | 0.1 | 0.13 | 0.11 | 0.1 | 0.1 | 0.17 | 0.15 | 0.14 | 0.13 | 0.13 | 0.25 | 0.17 | 0.16 | 0.15 | 0.15 | 0.33
105 | TC | 614 | 582 | 531 | 482 | 433 | 644 | 611 | 559 | 509 | 468 | 664 | 631 | 579 | 528 | 495 | 679 | 646 | 593 | 542 | 519
| SHC | 155 | 201 | 276 | 349 | 408 | 168 | 222 | 312 | 400 | 461 | 180 | 243 | 346 | 447 | 495 | 192 | 262 | 379 | 489 | 519
| kW | 63.3 | 62.6 | 61.8 | 61.4 | 61.3 | 63.9 | 63.2 | 62.1 | 61.5 | 61 | 64.4 | 63.6 | 62.5 | 61.7 | 61.3 | 64.7 | 64 | 62.8 | 61.8 | 61.5
| BF | 0.05 | 0.08 | 0.08 | 0.08 | 0.09 | 0.13 | 0.11 | 0.1 | 0.1 | 0.18 | 0.15 | 0.14 | 0.13 | 0.13 | 0.27 | 0.17 | 0.16 | 0.15 | 0.16 | 0.34
115 | TC | 577 | 547 | 498 | 451 | 408 | 604 | 573 | 524 | 477 | 439 | 631 | 592 | 542 | 494 | 465 | 644 | 605 | 555 | 506 | 489
| SHC | 130 | 177 | 253 | 327 | 381 | 142 | 197 | 288 | 376 | 433 | 162 | 216 | 321 | 422 | 465 | 173 | 235 | 353 | 462 | 489
| kW | 69.8 | 69.3 | 68.8 | 68.7 | 69 | 70.2 | 69.6 | 68.9 | 68.6 | 68.2 | 71 | 69.9 | 69 | 68.5 | 68.4 | 71.2 | 70.1 | 69.2 | 68.5 | 68.4
| BF | 0.05 | 0.08 | 0.08 | 0.08 | 0.12 | 0.13 | 0.11 | 0.1 | 0.1 | 0.2 | 0.15 | 0.14 | 0.13 | 0.13 | 0.29 | 0.17 | 0.16 | 0.15 | 0.16 | 0.36
48/50 060 (60 TON) STANDARD CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 24000 |  |  |  |  | 27000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 793 | 765 | 795 | 775 | 771 | 804 | 774 | 715 | 780 | 778
| SHC | 276 | 357 | 681 | 740 | 771 | 288 | 375 | 514 | 758 | 778
| kW | 50.4 | 49.8 | 50.9 | 50.6 | 50.6 | 50.6 | 50 | 48.7 | 50.7 | 50.7
| BF | 0.2 | 0.18 | 0.39 | 0.48 | 0.63 | 0.22 | 0.2 | 0.18 | 0.49 | 0.65
85 | TC | 776 | 732 | 674 | 617 | 597 | 767 | 742 | 694 | 637 | 617
| SHC | 264 | 333 | 459 | 577 | 597 | 262 | 352 | 495 | 624 | 617
| kW | 55.1 | 53.9 | 52.6 | 51.5 | 51.1 | 54.7 | 54.2 | 53.3 | 52.3 | 51.5
| BF | 0.19 | 0.18 | 0.16 | 0.18 | 0.38 | 0.22 | 0.19 | 0.18 | 0.21 | 0.43
95 | TC | 730 | 696 | 640 | 586 | 582 | 754 | 704 | 658 | 596 | 601
| SHC | 230 | 307 | 436 | 551 | 582 | 262 | 326 | 475 | 578 | 601
| kW | 59.5 | 58.7 | 57.5 | 56.4 | 57 | 61.1 | 58.8 | 58.1 | 56.6 | 57.3
| BF | 0.19 | 0.18 | 0.17 | 0.18 | 0.39 | 0.22 | 0.2 | 0.18 | 0.23 | 0.45
105 | TC | 698 | 657 | 604 | 553 | 540 | 699 | 666 | 621 | 577 | 570
| SHC | 212 | 281 | 410 | 518 | 540 | 214 | 299 | 449 | 562 | 570
| kW | 65.4 | 64.2 | 63 | 61.9 | 61.7 | 65.2 | 64.4 | 63.6 | 63 | 62.9
| BF | 0.19 | 0.18 | 0.17 | 0.2 | 0.41 | 0.21 | 0.19 | 0.18 | 0.24 | 0.46
115 | TC | 654 | 615 | 574 | 519 | 522 | 654 | 623 | 573 | 530 | 524
| SHC | 184 | 254 | 394 | 487 | 522 | 186 | 271 | 414 | 516 | 524
| kW | 71.5 | 70.3 | 69.7 | 68.5 | 69.5 | 71.3 | 70.5 | 69.4 | 68.6 | 68.6
| BF | 0.19 | 0.18 | 0.17 | 0.22 | 0.42 | 0.21 | 0.2 | 0.18 | 0.26 | 0.47
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
97

## page 11
Performance data (cont)
Cooling Capacities (cont)
48/50 060 (60 TON) HIGH-CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 12000 |  |  |  |  | 15000 |  |  |  |  | 18000 |  |  |  |  | 21000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 703 | 654 | 591 | 539 | 494 | 787 | 718 | 647 | 570 | 533 | 812 | 750 | 672 | 588 | 558 | 829 | 752 | 683 | 620 | 588
| SHC | 188 | 224 | 299 | 378 | 457 | 254 | 280 | 364 | 435 | 520 | 270 | 312 | 406 | 486 | 558 | 285 | 318 | 439 | 554 | 588
| kW | 48.9 | 47.7 | 46.4 | 45.3 | 44.4 | 50.2 | 48.9 | 47.3 | 45.9 | 45.1 | 50.8 | 49.8 | 48 | 46.4 | 45.7 | 51.3 | 49.9 | 48.5 | 47 | 46.4
| BF | 0 | 0.02 | 0.02 | 0.02 | 0.03 | 0.05 | 0.04 | 0.03 | 0.03 | 0.08 | 0.07 | 0.05 | 0.04 | 0.04 | 0.16 | 0.09 | 0.06 | 0.05 | 0.06 | 0.25
85 | TC | 661 | 621 | 559 | 506 | 462 | 691 | 658 | 592 | 534 | 504 | 739 | 692 | 606 | 555 | 526 | 759 | 710 | 639 | 568 | 553
| SHC | 152 | 198 | 273 | 351 | 424 | 163 | 226 | 314 | 405 | 492 | 203 | 261 | 346 | 458 | 526 | 221 | 286 | 402 | 507 | 553
| kW | 52.7 | 51.8 | 50.5 | 49.5 | 48.7 | 53.5 | 52.7 | 51.2 | 50 | 49.3 | 54.4 | 53.4 | 51.6 | 50.4 | 49.8 | 54.9 | 53.8 | 52.2 | 50.8 | 50.4
| BF | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.06 | 0.03 | 0.03 | 0.03 | 0.09 | 0.07 | 0.05 | 0.04 | 0.04 | 0.17 | 0.08 | 0.06 | 0.05 | 0.06 | 0.26
95 | TC | 621 | 581 | 522 | 472 | 443 | 672 | 611 | 548 | 497 | 473 | 670 | 625 | 583 | 516 | 492 | 689 | 668 | 581 | 546 | 516
| SHC | 120 | 165 | 242 | 323 | 413 | 154 | 187 | 278 | 375 | 462 | 142 | 203 | 331 | 426 | 492 | 159 | 254 | 352 | 490 | 516
| kW | 57.4 | 56.5 | 55.3 | 54.4 | 54.1 | 58.4 | 57.2 | 55.8 | 54.8 | 54.2 | 58.7 | 57.6 | 56.4 | 55.2 | 54.7 | 59.2 | 58.4 | 56.6 | 55.6 | 55.1
| BF | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.11 | 0.07 | 0.05 | 0.04 | 0.04 | 0.19 | 0.08 | 0.06 | 0.05 | 0.07 | 0.27
105 | TC | 576 | 538 | 483 | 436 | 410 | 628 | 564 | 505 | 458 | 441 | 625 | 586 | 521 | 474 | 457 | 644 | 597 | 534 | 493 | 478
| SHC | 87 | 132 | 212 | 294 | 378 | 122 | 151 | 244 | 344 | 432 | 110 | 174 | 280 | 393 | 457 | 127 | 193 | 315 | 440 | 478
| kW | 62.9 | 62 | 61 | 60.8 | 61 | 64 | 62.6 | 61.2 | 60.6 | 60.4 | 64.2 | 63.1 | 61.6 | 60.6 | 60.5 | 64.7 | 63.4 | 61.8 | 60.9 | 60.6
| BF | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.05 | 0.03 | 0.03 | 0.03 | 0.12 | 0.07 | 0.05 | 0.04 | 0.05 | 0.2 | 0.08 | 0.06 | 0.05 | 0.09 | 0.28
115 | TC | 529 | 493 | 440 | 396 | 379 | 553 | 514 | 459 | 415 | 400 | 573 | 530 | 473 | 432 | 420 | 587 | 544 | 482 | 451 | 438
| SHC | 52 | 99 | 180 | 265 | 349 | 60 | 113 | 210 | 312 | 387 | 74 | 133 | 243 | 361 | 420 | 86 | 155 | 276 | 400 | 438
| kW | 69.6 | 68.7 | 68.2 | 68.7 | 69 | 70.1 | 69 | 68 | 68 | 68.4 | 70.7 | 69.3 | 68 | 67.7 | 67.8 | 71.2 | 69.6 | 68.1 | 67.5 | 67.6
| BF | 0.02 | 0.02 | 0.02 | 0.02 | 0.07 | 0.05 | 0.03 | 0.03 | 0.03 | 0.13 | 0.07 | 0.05 | 0.04 | 0.05 | 0.22 | 0.08 | 0.06 | 0.05 | 0.11 | 0.3
48/50 060 (60 TON) HIGH-CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 24000 |  |  |  |  | 27000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 847 | 805 | 691 | 637 | 607 | 859 | 791 | 720 | 662 | 654
| SHC | 301 | 384 | 471 | 599 | 607 | 321 | 379 | 526 | 638 | 654
| kW | 51.7 | 50.8 | 48.6 | 47.4 | 46.9 | 52.1 | 50.7 | 49.1 | 47.8 | 47.6
| BF | 0.1 | 0.08 | 0.07 | 0.1 | 0.32 | 0.11 | 0.09 | 0.08 | 0.14 | 0.38
85 | TC | 776 | 725 | 651 | 591 | 574 | 795 | 737 | 662 | 601 | 599
| SHC | 239 | 312 | 440 | 552 | 574 | 261 | 337 | 478 | 584 | 599
| kW | 55.3 | 54.2 | 52.5 | 51.2 | 50.9 | 55.9 | 54.5 | 52.8 | 51.5 | 51.5
| BF | 0.1 | 0.08 | 0.07 | 0.11 | 0.33 | 0.11 | 0.09 | 0.08 | 0.15 | 0.39
95 | TC | 701 | 683 | 609 | 550 | 535 | 747 | 694 | 619 | 561 | 554
| SHC | 173 | 279 | 407 | 513 | 535 | 225 | 304 | 443 | 546 | 554
| kW | 59.6 | 58.8 | 57.1 | 55.8 | 55.5 | 60.3 | 59.1 | 57.3 | 56.1 | 56
| BF | 0.09 | 0.08 | 0.07 | 0.12 | 0.34 | 0.11 | 0.09 | 0.08 | 0.16 | 0.4
105 | TC | 656 | 610 | 544 | 509 | 495 | 667 | 618 | 550 | 519 | 512
| SHC | 141 | 218 | 351 | 474 | 495 | 156 | 238 | 385 | 505 | 512
| kW | 65.1 | 63.7 | 62.1 | 61.2 | 61 | 65.4 | 64 | 62.3 | 61.4 | 61.3
| BF | 0.09 | 0.07 | 0.07 | 0.13 | 0.35 | 0.11 | 0.09 | 0.08 | 0.17 | 0.41
115 | TC | 599 | 553 | 491 | 465 | 453 | 609 | 561 | 498 | 471 | 466
| SHC | 100 | 175 | 311 | 432 | 453 | 115 | 197 | 346 | 460 | 466
| kW | 71.7 | 69.9 | 68.2 | 67.6 | 67.5 | 72.1 | 70.1 | 68.3 | 67.7 | 67.6
| BF | 0.09 | 0.07 | 0.07 | 0.15 | 0.37 | 0.11 | 0.09 | 0.08 | 0.19 | 0.42
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
100

## page 12
Performance data (cont)
Cooling Capacities (cont)
48/50 070 (70 TON) STANDARD CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 14000 |  |  |  |  | 17500 | [5 empty] | 21000 |  |  |  |  | 24500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 |  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 791 | 754 | 683 | 644 | 576 | 812 | 787 | 726 | 676 | 627 |  | 855 | 813 | 749 | 671 | 663 | 875 | 813 | 767 | 703 | 681
| SHC | 255 | 309 | 393 | 488 | 552 | 257 | 336 | 440 | 549 | 627 |  | 292 | 363 | 483 | 580 | 663 | 308 | 369 | 525 | 648 | 681
| kW | 52.2 | 51.2 | 49.8 | 48.8 | 47.5 | 53 | 52.1 | 50.6 | 49.5 | 48.6 |  | 54.3 | 53.1 | 51.2 | 49.6 | 49.3 | 54.8 | 53.1 | 51.7 | 50.4 | 49.6
| BF | 0 | 0.07 | 0.07 | 0.06 | 0.08 | 0.13 | 0.1 | 0.09 | 0.09 | 0.16 |  | 0.14 | 0.12 | 0.11 | 0.11 | 0.26 | 0.16 | 0.14 | 0.13 | 0.14 | 0.34
85 | TC | 738 | 724 | 665 | 618 | 551 | 774 | 738 | 695 | 637 | 588 |  | 815 | 776 | 716 | 668 | 623 | 833 | 793 | 731 | 672 | 675
| SHC | 209 | 286 | 374 | 467 | 529 | 229 | 295 | 416 | 517 | 588 |  | 264 | 337 | 458 | 584 | 623 | 279 | 361 | 497 | 624 | 675
| kW | 56.1 | 55.5 | 54.1 | 53.2 | 51.8 | 57.2 | 56.2 | 54.9 | 53.6 | 52.5 |  | 58.4 | 57.3 | 55.4 | 54.3 | 53.3 | 59 | 57.8 | 56.1 | 54.7 | 55.7
| BF | 0 | 0.07 | 0.07 | 0.07 | 0.09 | 0.13 | 0.1 | 0.09 | 0.09 | 0.17 |  | 0.14 | 0.12 | 0.11 | 0.11 | 0.27 | 0.15 | 0.14 | 0.13 | 0.14 | 0.35
95 | TC | 723 | 687 | 627 | 595 | 543 | 754 | 718 | 660 | 579 | 577 |  | 775 | 739 | 681 | 646 | 616 | 791 | 753 | 696 | 639 | 621
| SHC | 205 | 258 | 344 | 453 | 522 | 221 | 285 | 390 | 467 | 577 |  | 236 | 310 | 431 | 571 | 616 | 250 | 333 | 472 | 597 | 621
| kW | 61.7 | 60.7 | 59.2 | 59.7 | 59.3 | 62.6 | 61.6 | 60.1 | 58.3 | 59.8 |  | 63.3 | 62.2 | 60.6 | 60.7 | 60.4 | 63.8 | 62.7 | 61.1 | 59.6 | 59.2
| BF | 0.05 | 0.07 | 0.07 | 0.07 | 0.11 | 0.13 | 0.1 | 0.09 | 0.09 | 0.17 |  | 0.14 | 0.12 | 0.11 | 0.11 | 0.28 | 0.15 | 0.14 | 0.13 | 0.15 | 0.36
105 | TC | 685 | 650 | 605 | 565 | 517 | 714 | 679 | 624 | 593 | 552 |  | 733 | 699 | 643 | 613 | 586 | 747 | 713 | 657 | 604 | 589
| SHC | 178 | 232 | 333 | 431 | 498 | 193 | 257 | 364 | 491 | 552 |  | 207 | 282 | 405 | 547 | 586 | 221 | 305 | 444 | 560 | 589
| kW | 67.3 | 66.4 | 65.9 | 65.7 | 65.5 | 68.2 | 67.2 | 65.8 | 66.2 | 65.9 |  | 68.8 | 67.8 | 66.3 | 66.7 | 66.6 | 69.3 | 68.2 | 66.7 | 65.3 | 64.9
| BF | 0.05 | 0.07 | 0.07 | 0.07 | 0.12 | 0.13 | 0.1 | 0.09 | 0.09 | 0.2 |  | 0.14 | 0.12 | 0.11 | 0.12 | 0.3 | 0.15 | 0.14 | 0.13 | 0.17 | 0.37
115 | TC | 643 | 610 | 583 | 532 | 483 | 670 | 637 | 584 | 558 | 522 |  | 705 | 655 | 602 | 576 | 555 | 718 | 668 | 615 | 567 | 554
| SHC | 150 | 205 | 321 | 408 | 471 | 163 | 229 | 337 | 467 | 522 |  | 195 | 253 | 377 | 522 | 555 | 209 | 275 | 416 | 526 | 554
| kW | 73.7 | 72.8 | 73.4 | 72.9 | 72.7 | 74.5 | 73.6 | 72.2 | 73.1 | 73.1 |  | 75.9 | 74.1 | 72.7 | 73.5 | 73.5 | 76.3 | 74.5 | 73 | 71.7 | 71.4
| BF | 0.04 | 0.07 | 0.07 | 0.07 | 0.15 | 0.12 | 0.1 | 0.09 | 0.09 | 0.22 |  | 0.14 | 0.12 | 0.11 | 0.12 | 0.32 | 0.15 | 0.14 | 0.13 | 0.19 | 0.39
48/50 070 (70 TON) STANDARD CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 28000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 703 | 888 | 847 | 777 | 717 | 897 | 854 | 783 | 696 | 728
| SHC | 648 | 332 | 414 | 561 | 717 | 333 | 428 | 582 | 681 | 728
| kW | 50.4 | 55.2 | 54.1 | 52.3 | 50.5 | 55.5 | 54.3 | 52.5 | 50.4 | 50.8
| BF | 0.17 | 0.15 | 0.14 | 0.17 | 0.4 | 0.18 | 0.16 | 0.15 | 0.2 | 0.43
85 | TC | 847 | 806 | 744 | 683 | 675 | 853 | 812 | 750 | 715 | 709
| SHC | 294 | 385 | 536 | 657 | 675 | 303 | 399 | 558 | 700 | 709
| kW | 59.4 | 58.2 | 56.5 | 54.9 | 54.7 | 59.6 | 58.4 | 56.7 | 56.9 | 56.3
| BF | 0.17 | 0.15 | 0.14 | 0.19 | 0.41 | 0.18 | 0.16 | 0.15 | 0.22 | 0.44
95 | TC | 802 | 766 | 707 | 677 | 669 | 808 | 771 | 713 | 685 | 608
| SHC | 265 | 357 | 510 | 654 | 669 | 273 | 370 | 531 | 674 | 608
| kW | 64.2 | 63.1 | 61.4 | 61.5 | 61.3 | 64.4 | 63.3 | 61.6 | 61.8 | 59.2
| BF | 0.17 | 0.15 | 0.14 | 0.2 | 0.42 | 0.18 | 0.16 | 0.15 | 0.23 | 0.45
105 | TC | 758 | 724 | 668 | 643 | 635 | 763 | 729 | 672 | 652 | 646
| SHC | 235 | 328 | 482 | 623 | 635 | 242 | 341 | 503 | 643 | 646
| kW | 69.7 | 68.6 | 67 | 67.5 | 67.4 | 69.8 | 68.8 | 67.2 | 67.8 | 67.6
| BF | 0.17 | 0.15 | 0.14 | 0.22 | 0.43 | 0.18 | 0.16 | 0.15 | 0.24 | 0.46
115 | TC | 711 | 697 | 624 | 581 | 573 | 738 | 701 | 629 | 587 | 610
| SHC | 204 | 318 | 453 | 561 | 573 | 235 | 331 | 474 | 580 | 610
| kW | 75.9 | 75.7 | 73.3 | 72.1 | 71.9 | 77 | 75.9 | 73.5 | 72.3 | 74.3
| BF | 0.17 | 0.15 | 0.14 | 0.23 | 0.45 | 0.18 | 0.16 | 0.15 | 0.26 | 0.48
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC. | [11 empty] | 2. Interpolation is permissible. 3. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat. 5. SHC values provided are in subcooling mode with the gas bypass valve closed and reflect the maximum SHC in subcooling mode. The P Series innovative modulating valve system can reduce SHC as needed to meet the supply air set point requirement with mini- mal change in latent capacity. This will provide variable SHC to meet the space load.
103

## page 13
Performance data (cont)
Cooling Capacities (cont)
48/50 070 (70 TON) HIGH-CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 14000 |  |  |  |  | 17500 | [5 empty] | 21000 |  |  |  |  | 24500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 |  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 798 | 759 | 699 | 643 | 604 | 835 | 793 | 732 | 675 | 635 |  | 861 | 817 | 754 | 698 | 669 | 879 | 836 | 769 | 716 | 700
| SHC | 236 | 292 | 386 | 478 | 578 | 253 | 320 | 433 | 544 | 631 |  | 271 | 348 | 478 | 607 | 669 | 288 | 375 | 522 | 664 | 700
| kW | 52.9 | 51.8 | 50.3 | 49 | 48.1 | 53.9 | 52.8 | 51.1 | 49.7 | 48.8 |  | 54.7 | 53.5 | 51.8 | 50.3 | 49.6 | 55.3 | 54.1 | 52.2 | 50.8 | 50.3
| BF | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.06 | 0.04 | 0.03 | 0.04 | 0.11 |  | 0.07 | 0.05 | 0.05 | 0.05 | 0.21 | 0.08 | 0.06 | 0.06 | 0.08 | 0.29
85 | TC | 762 | 725 | 668 | 610 | 586 | 795 | 757 | 697 | 644 | 600 |  | 817 | 778 | 718 | 664 | 638 | 833 | 793 | 733 | 683 | 667
| SHC | 207 | 264 | 361 | 451 | 558 | 222 | 290 | 405 | 519 | 598 |  | 237 | 316 | 449 | 579 | 638 | 253 | 342 | 493 | 636 | 667
| kW | 57 | 56 | 54.6 | 53.3 | 52.7 | 58 | 57 | 55.3 | 54 | 53.1 |  | 58.7 | 57.6 | 55.9 | 54.5 | 53.9 | 59.3 | 58.1 | 56.4 | 55 | 54.6
| BF | 0.03 | 0.02 | 0.02 | 0.02 | 0.06 | 0.06 | 0.04 | 0.03 | 0.04 | 0.12 |  | 0.07 | 0.05 | 0.05 | 0.05 | 0.22 | 0.08 | 0.06 | 0.06 | 0.08 | 0.3
95 | TC | 723 | 687 | 632 | 578 | 560 | 752 | 716 | 661 | 610 | 568 |  | 773 | 735 | 679 | 631 | 607 | 787 | 749 | 693 | 649 | 634
| SHC | 176 | 235 | 333 | 427 | 534 | 189 | 259 | 377 | 492 | 562 |  | 203 | 284 | 419 | 553 | 607 | 218 | 308 | 462 | 600 | 634
| kW | 62 | 61 | 59.6 | 58.4 | 58.2 | 62.8 | 61.8 | 60.3 | 59.1 | 58.1 |  | 63.5 | 62.4 | 60.9 | 59.6 | 59 | 64 | 62.9 | 61.3 | 60 | 59.7
| BF | 0.03 | 0.02 | 0.02 | 0.02 | 0.07 | 0.06 | 0.04 | 0.03 | 0.04 | 0.12 |  | 0.07 | 0.05 | 0.05 | 0.06 | 0.23 | 0.08 | 0.06 | 0.06 | 0.1 | 0.31
105 | TC | 680 | 646 | 594 | 548 | 533 | 706 | 671 | 618 | 570 | 528 |  | 724 | 688 | 636 | 592 | 569 | 737 | 701 | 648 | 610 | 598
| SHC | 145 | 205 | 305 | 405 | 508 | 155 | 226 | 346 | 463 | 528 |  | 167 | 249 | 387 | 523 | 569 | 181 | 273 | 429 | 563 | 598
| kW | 67.7 | 66.7 | 65.6 | 65.2 | 65.1 | 68.5 | 67.5 | 66.1 | 65.3 | 64.7 |  | 69.1 | 68 | 66.5 | 65.6 | 65.2 | 69.5 | 68.4 | 66.9 | 65.8 | 65.7
| BF | 0.02 | 0.02 | 0.02 | 0.02 | 0.09 | 0.06 | 0.04 | 0.03 | 0.04 | 0.15 |  | 0.07 | 0.05 | 0.05 | 0.06 | 0.25 | 0.08 | 0.06 | 0.06 | 0.12 | 0.33
115 | TC | 633 | 601 | 553 | 504 | 502 | 656 | 624 | 575 | 532 | 507 |  | 671 | 638 | 590 | 559 | 536 | 683 | 649 | 601 | 572 | 556
| SHC | 111 | 173 | 276 | 373 | 479 | 120 | 193 | 316 | 442 | 507 |  | 130 | 214 | 355 | 494 | 536 | 143 | 236 | 396 | 527 | 556
| kW | 74.5 | 73.8 | 73.2 | 73.1 | 73.5 | 75.1 | 74.2 | 73.4 | 73 | 72.9 |  | 75.5 | 74.6 | 73.6 | 73.1 | 72.9 | 75.9 | 74.9 | 73.7 | 73.1 | 73
| BF | 0.02 | 0.02 | 0.02 | 0.02 | 0.1 | 0.06 | 0.04 | 0.03 | 0.04 | 0.17 |  | 0.07 | 0.05 | 0.05 | 0.08 | 0.27 | 0.08 | 0.06 | 0.06 | 0.13 | 0.34
48/50 070 (70 TON) HIGH-CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 28000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 894 | 849 | 783 | 733 | 723 | 901 | 851 | 788 | 741 | 736
| SHC | 305 | 403 | 567 | 705 | 723 | 314 | 414 | 590 | 728 | 736
| kW | 55.7 | 54.5 | 52.7 | 51.2 | 51 | 56 | 54.4 | 52.8 | 51.5 | 51.3
| BF | 0.09 | 0.08 | 0.07 | 0.12 | 0.36 | 0.1 | 0.08 | 0.08 | 0.15 | 0.4
85 | TC | 845 | 805 | 745 | 701 | 692 | 852 | 810 | 750 | 709 | 703
| SHC | 269 | 368 | 536 | 675 | 692 | 278 | 383 | 560 | 696 | 703
| kW | 59.7 | 58.5 | 56.8 | 55.5 | 55.3 | 59.9 | 58.7 | 56.9 | 55.7 | 55.6
| BF | 0.09 | 0.08 | 0.07 | 0.13 | 0.37 | 0.1 | 0.08 | 0.08 | 0.16 | 0.4
95 | TC | 798 | 760 | 703 | 666 | 659 | 804 | 765 | 708 | 673 | 664
| SHC | 233 | 334 | 503 | 641 | 659 | 241 | 348 | 527 | 662 | 664
| kW | 64.4 | 63.3 | 61.6 | 60.5 | 60.3 | 64.6 | 63.4 | 61.8 | 60.7 | 60.5
| BF | 0.09 | 0.08 | 0.07 | 0.15 | 0.38 | 0.1 | 0.08 | 0.08 | 0.17 | 0.41
105 | TC | 747 | 710 | 657 | 626 | 619 | 752 | 715 | 661 | 633 | 628
| SHC | 195 | 297 | 470 | 603 | 619 | 203 | 311 | 492 | 624 | 628
| kW | 69.9 | 68.8 | 67.2 | 66.3 | 66.1 | 70 | 68.9 | 67.4 | 66.5 | 66.4
| BF | 0.09 | 0.08 | 0.07 | 0.16 | 0.39 | 0.1 | 0.08 | 0.08 | 0.18 | 0.42
115 | TC | 691 | 657 | 609 | 583 | 573 | 696 | 660 | 613 | 589 | 582
| SHC | 156 | 260 | 436 | 563 | 573 | 164 | 273 | 458 | 583 | 582
| kW | 76.2 | 75.2 | 73.9 | 73.3 | 73.2 | 76.4 | 75.3 | 74 | 73.4 | 73.3
| BF | 0.09 | 0.08 | 0.07 | 0.18 | 0.41 | 0.1 | 0.08 | 0.08 | 0.2 | 0.44
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC. | [11 empty] | 2. Interpolation is permissible. 3. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat. 5. SHC values provided are in subcooling mode with the gas bypass valve closed and reflect the maximum SHC in subcooling mode. The P Series innovative modulating valve system can reduce SHC as needed to meet the supply air set point requirement with mini- mal change in latent capacity. This will provide variable SHC to meet the space load.
106

## page 14
Performance data (cont)
Cooling Capacities (cont)
48/50 075 (75 TON) STANDARD CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 14000 |  |  |  |  | 17500 | [5 empty] | 21000 |  |  |  |  | 24500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 |  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 847 | 771 | 745 | 681 | 619 | 871 | 829 | 760 | 720 | 659 |  | 900 | 856 | 789 | 725 | 674 | 914 | 868 | 809 | 743 | 709
| SHC | 281 | 299 | 432 | 507 | 582 | 284 | 347 | 447 | 572 | 649 |  | 301 | 373 | 494 | 610 | 674 | 310 | 391 | 530 | 665 | 709
| kW | 56.6 | 54.6 | 54.8 | 53.8 | 53 | 57.3 | 56.2 | 54.5 | 54.5 | 53.9 |  | 58.2 | 57 | 55.2 | 53.7 | 52.5 | 58.7 | 57.4 | 55.8 | 54.1 | 53.3
| BF | 0 | 0.07 | 0.07 | 0.06 | 0.07 | 0.06 | 0.1 | 0.09 | 0.09 | 0.14 |  | 0.14 | 0.12 | 0.11 | 0.11 | 0.22 | 0.16 | 0.14 | 0.12 | 0.13 | 0.31
85 | TC | 803 | 756 | 715 | 653 | 593 | 832 | 817 | 713 | 668 | 632 |  | 860 | 819 | 755 | 681 | 670 | 878 | 838 | 773 | 710 | 680
| SHC | 246 | 293 | 403 | 486 | 562 | 254 | 344 | 410 | 527 | 623 |  | 272 | 346 | 468 | 576 | 670 | 287 | 371 | 508 | 639 | 680
| kW | 61.1 | 59.9 | 59.9 | 59.1 | 58.1 | 61.9 | 62.1 | 58.9 | 57.8 | 58.4 |  | 62.8 | 61.7 | 59.9 | 58.3 | 59.6 | 63.4 | 62.2 | 60.4 | 58.8 | 58.1
| BF | 0 | 0.07 | 0.07 | 0.06 | 0.08 | 0.16 | 0.1 | 0.09 | 0.09 | 0.15 |  | 0.14 | 0.12 | 0.11 | 0.11 | 0.24 | 0.16 | 0.14 | 0.13 | 0.13 | 0.32
95 | TC | 759 | 720 | 681 | 623 | 566 | 794 | 755 | 694 | 603 | 606 |  | 818 | 779 | 717 | 682 | 641 | 859 | 797 | 734 | 674 | 648
| SHC | 212 | 266 | 378 | 464 | 540 | 227 | 292 | 399 | 471 | 599 |  | 242 | 317 | 441 | 585 | 641 | 282 | 341 | 480 | 611 | 648
| kW | 66.4 | 65.4 | 65.6 | 64.8 | 64.5 | 67.4 | 66.4 | 64.7 | 62.6 | 64.9 |  | 68.2 | 67.1 | 65.4 | 66 | 65.6 | 69.9 | 67.6 | 65.9 | 64.3 | 63.7
| BF | 0 | 0.07 | 0.07 | 0.06 | 0.09 | 0.14 | 0.1 | 0.09 | 0.09 | 0.16 |  | 0.14 | 0.12 | 0.11 | 0.11 | 0.25 | 0.16 | 0.14 | 0.13 | 0.14 | 0.33
105 | TC | 718 | 681 | 647 | 590 | 533 | 751 | 714 | 654 | 621 | 576 |  | 773 | 736 | 677 | 645 | 610 | 789 | 752 | 692 | 634 | 613
| SHC | 183 | 238 | 354 | 440 | 508 | 198 | 263 | 371 | 501 | 576 |  | 212 | 287 | 412 | 559 | 610 | 226 | 311 | 451 | 582 | 613
| kW | 72.6 | 71.6 | 72.3 | 71.5 | 71.1 | 73.6 | 72.6 | 71 | 71.9 | 72.1 |  | 74.3 | 73.2 | 71.6 | 72.6 | 72.3 | 74.9 | 73.7 | 72.1 | 70.5 | 70
| BF | 0.06 | 0.07 | 0.07 | 0.06 | 0.11 | 0.14 | 0.1 | 0.09 | 0.09 | 0.17 |  | 0.14 | 0.12 | 0.11 | 0.11 | 0.27 | 0.15 | 0.13 | 0.13 | 0.14 | 0.34
115 | TC | 674 | 639 | 611 | 555 | 510 | 704 | 669 | 613 | 581 | 509 |  | 724 | 689 | 633 | 607 | 576 | 764 | 704 | 647 | 622 | 577
| SHC | 154 | 209 | 330 | 415 | 486 | 167 | 233 | 342 | 472 | 485 |  | 180 | 256 | 382 | 533 | 576 | 219 | 279 | 421 | 570 | 577
| kW | 79.6 | 78.7 | 80.2 | 79.6 | 80.4 | 80.5 | 79.5 | 78.1 | 79.8 | 80 |  | 81.2 | 80.1 | 78.6 | 80.3 | 80.2 | 83.1 | 80.6 | 79 | 80.7 | 77.3
| BF | 0.05 | 0.07 | 0.07 | 0.07 | 0.13 | 0.13 | 0.1 | 0.09 | 0.09 | 0.013 |  | 0.14 | 0.12 | 0.11 | 0.12 | 0.29 | 0.15 | 0.13 | 0.13 | 0.17 | 0.36
48/50 075 (75 TON) STANDARD CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 28000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 939 | 893 | 823 | 780 | 736 | 947 | 900 | 830 | 764 | 773
| SHC | 329 | 424 | 575 | 736 | 736 | 338 | 437 | 596 | 741 | 773
| kW | 59.3 | 58.1 | 56.2 | 55.8 | 54 | 59.6 | 58.3 | 56.4 | 54.7 | 55.8
| BF | 0.17 | 0.15 | 0.14 | 0.16 | 0.37 | 0.18 | 0.16 | 0.15 | 0.17 | 0.4
85 | TC | 893 | 852 | 787 | 724 | 706 | 900 | 884 | 817 | 731 | 719
| SHC | 302 | 394 | 547 | 685 | 706 | 310 | 433 | 593 | 703 | 719
| kW | 63.9 | 62.7 | 60.9 | 59.2 | 58.8 | 64.1 | 64 | 62.2 | 59.4 | 59.1
| BF | 0.17 | 0.15 | 0.14 | 0.16 | 0.38 | 0.18 | 0.16 | 0.15 | 0.19 | 0.41
95 | TC | 849 | 810 | 747 | 687 | 673 | 854 | 817 | 753 | 696 | 685
| SHC | 271 | 365 | 519 | 649 | 673 | 283 | 373 | 540 | 670 | 685
| kW | 69.2 | 68 | 66.3 | 64.6 | 64.3 | 69.4 | 68.3 | 66.5 | 64.9 | 64.6
| BF | 0.17 | 0.15 | 0.14 | 0.18 | 0.39 | 0.18 | 0.16 | 0.15 | 0.21 | 0.42
105 | TC | 802 | 764 | 705 | 650 | 637 | 830 | 770 | 710 | 658 | 649
| SHC | 235 | 334 | 489 | 614 | 637 | 280 | 346 | 510 | 634 | 649
| kW | 75.3 | 74.1 | 72.4 | 70.9 | 70.6 | 76.7 | 74.3 | 72.6 | 71.1 | 70.9
| BF | 0.17 | 0.15 | 0.14 | 0.2 | 0.41 | 0.18 | 0.16 | 0.15 | 0.22 | 0.44
115 | TC | 750 | 715 | 658 | 635 | 599 | 787 | 720 | 663 | 617 | 609
| SHC | 206 | 301 | 458 | 605 | 599 | 236 | 314 | 479 | 596 | 609
| kW | 82.1 | 81 | 79.3 | 80.9 | 77.8 | 83.9 | 81.2 | 79.5 | 78.2 | 78
| BF | 0.17 | 0.15 | 0.14 | 0.21 | 0.42 | 0.18 | 0.16 | 0.15 | 0.24 | 0.45
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC. | [11 empty] | 2. Interpolation is permissible. 3. Correction Factor = 1.10 x (1 – BF) x (edb – 80). 4. Cooling capacities are gross and do not include deduction for indoor fan motor heat. 5. SHC values provided are in subcooling mode with the gas bypass valve closed and reflect the maximum SHC in subcooling mode. The P Series innovative modulating valve system can reduce SHC as needed to meet the supply air set point requirement with mini- mal change in latent capacity. This will provide variable SHC to meet the space load.
109

## page 15
Performance data (cont)
Cooling Capacities (cont)
48/50 075 (75 TON) HIGH-CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 14000 |  |  |  |  | 17500 |  |  |  |  | 21000 |  |  |  |  | 24500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 871 | 825 | 758 | 693 | 647 | 913 | 869 | 799 | 726 | 674 | 946 | 896 | 837 | 761 | 717 | 966 | 919 | 847 | 773 | 753
| SHC | 277 | 330 | 421 | 508 | 606 | 296 | 363 | 472 | 572 | 660 | 317 | 391 | 530 | 644 | 717 | 333 | 421 | 561 | 697 | 753
| kW | 57.3 | 56.1 | 54.4 | 53 | 52.4 | 58.6 | 57.3 | 55.5 | 53.5 | 52.5 | 59.5 | 58.1 | 56.5 | 54.5 | 53.5 | 60.2 | 58.8 | 56.8 | 54.8 | 54.4
| BF | 0 | 0.02 | 0.02 | 0.02 | 0.03 | 0.07 | 0.04 | 0.03 | 0.03 | 0.09 | 0.07 | 0.05 | 0.04 | 0.05 | 0.17 | 0.08 | 0.06 | 0.06 | 0.07 | 0.26
85 | TC | 836 | 794 | 741 | 680 | 616 | 876 | 834 | 766 | 717 | 650 | 907 | 866 | 792 | 743 | 689 | 923 | 880 | 812 | 747 | 741
| SHC | 250 | 306 | 411 | 502 | 580 | 268 | 336 | 447 | 569 | 636 | 289 | 369 | 493 | 633 | 689 | 302 | 392 | 539 | 677 | 741
| kW | 62.1 | 61 | 59.7 | 58.6 | 57.2 | 63.3 | 62.1 | 60.3 | 59.3 | 57.5 | 64.2 | 63 | 61 | 59.9 | 58.4 | 64.8 | 63.5 | 61.6 | 59.9 | 60
| BF | 0 | 0.02 | 0.02 | 0.02 | 0.04 | 0.07 | 0.04 | 0.03 | 0.03 | 0.1 | 0.07 | 0.05 | 0.04 | 0.05 | 0.18 | 0.08 | 0.06 | 0.06 | 0.07 | 0.27
95 | TC | 798 | 769 | 708 | 649 | 592 | 836 | 804 | 729 | 684 | 619 | 861 | 820 | 765 | 706 | 657 | 880 | 842 | 782 | 711 | 708
| SHC | 222 | 291 | 387 | 480 | 559 | 238 | 317 | 420 | 546 | 607 | 255 | 334 | 477 | 606 | 657 | 271 | 365 | 520 | 647 | 708
| kW | 67.7 | 67 | 65.6 | 64.6 | 64 | 68.9 | 68 | 65.9 | 65.1 | 63.3 | 69.7 | 68.4 | 67 | 65.5 | 64.1 | 70.3 | 69.1 | 67.4 | 65.5 | 65.7
| BF | 0.03 | 0.02 | 0.02 | 0.02 | 0.05 | 0.07 | 0.04 | 0.03 | 0.03 | 0.12 | 0.07 | 0.05 | 0.04 | 0.05 | 0.2 | 0.08 | 0.06 | 0.06 | 0.08 | 0.28
105 | TC | 756 | 729 | 671 | 615 | 565 | 798 | 752 | 702 | 647 | 586 | 818 | 776 | 724 | 670 | 623 | 833 | 796 | 739 | 671 | 674
| SHC | 192 | 263 | 362 | 456 | 533 | 214 | 277 | 405 | 519 | 576 | 226 | 304 | 448 | 580 | 623 | 239 | 333 | 490 | 610 | 674
| kW | 74.2 | 73.5 | 72.6 | 72.1 | 72 | 75.4 | 74.1 | 73 | 72.3 | 70.7 | 76.1 | 74.8 | 73.4 | 72.5 | 71.3 | 76.6 | 75.4 | 73.8 | 72 | 72.7
| BF | 0.03 | 0.02 | 0.02 | 0.02 | 0.07 | 0.06 | 0.04 | 0.03 | 0.04 | 0.13 | 0.07 | 0.05 | 0.05 | 0.05 | 0.22 | 0.08 | 0.06 | 0.06 | 0.1 | 0.3
115 | TC | 711 | 688 | 631 | 578 | 533 | 750 | 706 | 646 | 607 | 574 | 770 | 728 | 680 | 629 | 586 | 781 | 744 | 694 | 631 | 635
| SHC | 162 | 235 | 334 | 429 | 504 | 183 | 247 | 362 | 492 | 568 | 194 | 272 | 418 | 551 | 586 | 205 | 297 | 460 | 573 | 635
| kW | 82 | 81.7 | 81 | 81 | 81.3 | 83 | 81.8 | 80.6 | 80.9 | 80.9 | 83.6 | 82.4 | 81.4 | 81 | 79.8 | 84 | 82.8 | 81.7 | 80.1 | 81
| BF | 0.02 | 0.02 | 0.02 | 0.02 | 0.09 | 0.06 | 0.04 | 0.03 | 0.04 | 0.15 | 0.07 | 0.05 | 0.05 | 0.06 | 0.23 | 0.08 | 0.06 | 0.06 | 0.12 | 0.31
48/50 075 (75 TON) HIGH-CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 28000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 983 | 936 | 862 | 796 | 783 | 990 | 944 | 869 | 806 | 797
| SHC | 351 | 449 | 611 | 755 | 783 | 360 | 465 | 636 | 777 | 797
| kW | 60.7 | 59.4 | 57.3 | 55.5 | 55.2 | 60.9 | 59.6 | 57.5 | 55.8 | 55.6
| BF | 0.09 | 0.08 | 0.07 | 0.1 | 0.33 | 0.1 | 0.08 | 0.08 | 0.13 | 0.36
85 | TC | 939 | 898 | 826 | 764 | 768 | 974 | 902 | 840 | 790 | 761
| SHC | 320 | 422 | 583 | 721 | 768 | 369 | 434 | 615 | 762 | 761
| kW | 65.4 | 64.1 | 62 | 60.3 | 60.6 | 69.7 | 64.2 | 62.4 | 61.2 | 60.1
| BF | 0.09 | 0.08 | 0.07 | 0.11 | 0.34 | 0.12 | 0.08 | 0.08 | 0.14 | 0.37
95 | TC | 895 | 852 | 786 | 747 | 733 | 932 | 856 | 800 | 755 | 747
| SHC | 289 | 388 | 554 | 706 | 733 | 346 | 395 | 586 | 729 | 747
| kW | 70.8 | 69.5 | 67.6 | 66.7 | 66.3 | 75.8 | 69.6 | 68 | 66.9 | 66.7
| BF | 0.09 | 0.08 | 0.07 | 0.13 | 0.35 | 0.12 | 0.08 | 0.08 | 0.15 | 0.38
105 | TC | 846 | 806 | 750 | 709 | 697 | 850 | 812 | 755 | 717 | 709
| SHC | 251 | 356 | 532 | 671 | 697 | 273 | 371 | 555 | 693 | 709
| kW | 77 | 75.8 | 74.2 | 73.2 | 73 | 77.2 | 76 | 74.4 | 73.4 | 73.2
| BF | 0.1 | 0.08 | 0.07 | 0.14 | 0.36 | 0.1 | 0.08 | 0.08 | 0.16 | 0.4
115 | TC | 794 | 755 | 704 | 668 | 658 | 802 | 761 | 708 | 676 | 669
| SHC | 220 | 323 | 500 | 634 | 658 | 222 | 338 | 523 | 656 | 669
| kW | 84.4 | 83.2 | 81.9 | 81.3 | 81.2 | 84.6 | 83.4 | 82 | 81.4 | 81.4
| BF | 0.09 | 0.08 | 0.07 | 0.16 | 0.38 | 0.1 | 0.08 | 0.08 | 0.18 | 0.41
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
112

## page 16
Performance data (cont)
Cooling Capacities (cont)
48/50 090 (90 TON) STANDARD CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 18000 |  |  |  |  | 22500 |  |  |  |  | 27000 |  |  |  |  | 31500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1075 | 1017 | 922 | 863 | 788 | 1154 | 1072 | 1003 | 915 | 836 | 1171 | 1135 | 1017 | 925 | 883 | 1201 | 1142 | 1045 | 952 | 923
| SHC | 396 | 454 | 541 | 656 | 744 | 450 | 493 | 629 | 736 | 819 | 452 | 553 | 658 | 782 | 883 | 475 | 563 | 707 | 846 | 923
| kW | 61.1 | 60.1 | 58.5 | 58.1 | 57.2 | 62.8 | 61.1 | 60.3 | 58.8 | 57.7 | 63 | 62.5 | 60.2 | 58.6 | 58.4 | 63.6 | 62.4 | 60.7 | 59.1 | 59
| BF | 0 | 0.05 | 0.09 | 0.1 | 0.11 | 0.03 | 0.1 | 0.12 | 0.12 | 0.18 | 0.09 | 0.12 | 0.14 | 0.15 | 0.26 | 0.12 | 0.15 | 0.16 | 0.17 | 0.33
85 | TC | 1052 | 964 | 884 | 828 | 752 | 1080 | 1013 | 933 | 876 | 807 | 1117 | 1083 | 995 | 910 | 844 | 1144 | 1088 | 996 | 935 | 887
| SHC | 387 | 413 | 513 | 629 | 712 | 391 | 449 | 570 | 707 | 791 | 414 | 516 | 649 | 778 | 844 | 436 | 525 | 673 | 841 | 887
| kW | 68.2 | 66.3 | 64.9 | 64.9 | 64 | 68.5 | 67.3 | 65.8 | 65.5 | 64.6 | 69.2 | 68.8 | 67.3 | 65.9 | 65.1 | 69.8 | 68.7 | 67 | 66.4 | 65.7
| BF | 0 | 0.06 | 0.09 | 0.1 | 0.11 | 0.04 | 0.1 | 0.12 | 0.12 | 0.19 | 0.09 | 0.13 | 0.14 | 0.15 | 0.26 | 0.12 | 0.15 | 0.16 | 0.18 | 0.34
95 | TC | 977 | 950 | 868 | 790 | 718 | 1026 | 972 | 914 | 835 | 771 | 1080 | 1006 | 946 | 866 | 808 | 1086 | 1053 | 944 | 890 | 849
| SHC | 327 | 413 | 508 | 600 | 686 | 354 | 423 | 564 | 677 | 756 | 396 | 456 | 615 | 746 | 808 | 396 | 508 | 637 | 807 | 849
| kW | 74.7 | 74.6 | 73.6 | 72.8 | 71.9 | 75.7 | 74.6 | 74.1 | 73.3 | 72.4 | 77 | 75.3 | 74.6 | 73.6 | 73 | 77 | 76.5 | 74.2 | 73.9 | 73.5
| BF | 0 | 0.06 | 0.09 | 0.1 | 0.11 | 0.04 | 0.1 | 0.12 | 0.12 | 0.2 | 0.09 | 0.13 | 0.14 | 0.15 | 0.28 | 0.12 | 0.15 | 0.16 | 0.18 | 0.35
105 | TC | 924 | 839 | 823 | 750 | 689 | 991 | 943 | 865 | 790 | 734 | 1000 | 972 | 894 | 819 | 770 | 1041 | 993 | 916 | 843 | 807
| SHC | 291 | 315 | 476 | 570 | 656 | 337 | 410 | 529 | 645 | 721 | 336 | 440 | 579 | 712 | 770 | 372 | 468 | 625 | 773 | 807
| kW | 83 | 81.6 | 82.5 | 81.9 | 81.1 | 84.5 | 83.8 | 82.9 | 82.2 | 81.5 | 84.5 | 84.2 | 83.3 | 82.5 | 82 | 85.6 | 84.6 | 83.5 | 82.8 | 82.4
| BF | 0 | 0.06 | 0.09 | 0.1 | 0.15 | 0.05 | 0.1 | 0.12 | 0.12 | 0.22 | 0.09 | 0.13 | 0.14 | 0.15 | 0.3 | 0.12 | 0.15 | 0.16 | 0.19 | 0.37
115 | TC | 868 | 848 | 774 | 708 | 648 | 931 | 886 | 812 | 742 | 694 | 956 | 912 | 838 | 769 | 728 | 974 | 930 | 858 | 790 | 762
| SHC | 253 | 342 | 442 | 544 | 617 | 297 | 371 | 493 | 611 | 682 | 313 | 399 | 540 | 675 | 728 | 329 | 426 | 586 | 728 | 762
| kW | 92.8 | 93.3 | 92.8 | 92.4 | 91.8 | 94.2 | 93.7 | 93 | 92.6 | 92 | 94.5 | 94 | 93.3 | 92.7 | 92.5 | 94.8 | 94.2 | 93.4 | 92.9 | 92.7
| BF | 0 | 0.06 | 0.09 | 0.1 | 0.16 | 0.05 | 0.1 | 0.12 | 0.13 | 0.24 | 0.1 | 0.13 | 0.14 | 0.16 | 0.31 | 0.13 | 0.15 | 0.16 | 0.2 | 0.39
48/50 090 (90 TON) STANDARD CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
36000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57
75 | TC | 1209 | 1164 | 1068 | 972 | 932
| SHC | 481 | 594 | 757 | 903 | 932
| kW | 63.8 | 62.9 | 61.2 | 59.5 | 58.7
| BF | 0.15 | 0.17 | 0.18 | 0.2 | 0.39
85 | TC | 1165 | 1109 | 1041 | 929 | 923
| SHC | 456 | 555 | 745 | 869 | 923
| kW | 70.2 | 69.1 | 68.1 | 65.8 | 66.2
| BF | 0.15 | 0.17 | 0.18 | 0.21 | 0.4
95 | TC | 1105 | 1051 | 963 | 908 | 882
| SHC | 415 | 516 | 683 | 863 | 882
| kW | 77.4 | 76.3 | 74.6 | 74.2 | 73.9
| BF | 0.15 | 0.17 | 0.18 | 0.21 | 0.41
105 | TC | 1041 | 990 | 932 | 860 | 838
| SHC | 373 | 475 | 669 | 815 | 838
| kW | 85.5 | 84.4 | 83.8 | 82.9 | 82.7
| BF | 0.15 | 0.17 | 0.18 | 0.23 | 0.43
115 | TC | 973 | 926 | 872 | 810 | 791
| SHC | 329 | 433 | 629 | 767 | 791
| kW | 94.6 | 93.8 | 93.6 | 93 | 92.9
| BF | 0.15 | 0.17 | 0.18 | 0.25 | 0.44
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
115

## page 17
Performance data (cont)
Cooling Capacities (cont)
48/50 090 (90 TON) HIGH-CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 18000 |  |  |  |  | 22500 |  |  |  |  | 27000 |  |  |  |  | 31500
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1134 | 1074 | 981 | 894 | 822 | 1191 | 1131 | 1036 | 948 | 878 | 1230 | 1170 | 1075 | 985 | 932 | 1259 | 1198 | 1103 | 1014 | 974
| SHC | 398 | 462 | 566 | 668 | 773 | 425 | 503 | 630 | 755 | 859 | 450 | 540 | 690 | 837 | 932 | 474 | 577 | 748 | 911 | 974
| kW | 62.5 | 61.4 | 59.7 | 58.3 | 57.4 | 63.6 | 62.5 | 60.7 | 59.2 | 57.9 | 64.5 | 63.3 | 61.5 | 59.9 | 58.9 | 65.1 | 63.9 | 62 | 60.4 | 59.7
| BF | 0 | 0.01 | 0.02 | 0.03 | 0.04 | 0 | 0.03 | 0.04 | 0.04 | 0.1 | 0.03 | 0.05 | 0.05 | 0.06 | 0.18 | 0.05 | 0.06 | 0.06 | 0.08 | 0.26
85 | TC | 1080 | 1023 | 935 | 853 | 781 | 1133 | 1076 | 985 | 902 | 843 | 1169 | 1111 | 1021 | 937 | 886 | 1196 | 1138 | 1046 | 964 | 930
| SHC | 358 | 424 | 531 | 636 | 736 | 383 | 462 | 592 | 721 | 826 | 406 | 498 | 650 | 800 | 886 | 429 | 533 | 706 | 872 | 930
| kW | 68.8 | 67.7 | 66.2 | 65.3 | 64.5 | 69.9 | 68.8 | 67.1 | 65.8 | 64.9 | 70.7 | 69.5 | 67.8 | 66.2 | 65.6 | 71.3 | 70.1 | 68.3 | 66.7 | 66.1
| BF | 0 | 0.01 | 0.02 | 0.03 | 0.04 | 0.01 | 0.03 | 0.04 | 0.04 | 0.11 | 0.03 | 0.05 | 0.05 | 0.06 | 0.19 | 0.05 | 0.06 | 0.06 | 0.08 | 0.27
95 | TC | 1025 | 970 | 887 | 810 | 743 | 1072 | 1018 | 933 | 855 | 801 | 1105 | 1050 | 965 | 887 | 843 | 1129 | 1074 | 988 | 912 | 885
| SHC | 318 | 386 | 495 | 603 | 702 | 340 | 420 | 554 | 685 | 785 | 361 | 454 | 610 | 762 | 843 | 382 | 487 | 664 | 831 | 885
| kW | 76.1 | 75.2 | 74.2 | 73.6 | 73 | 77.1 | 76 | 74.7 | 73.9 | 73.2 | 77.9 | 76.7 | 75.2 | 74.2 | 73.8 | 78.4 | 77.3 | 75.5 | 74.5 | 74.1
| BF | 0 | 0.01 | 0.02 | 0.03 | 0.06 | 0.01 | 0.03 | 0.04 | 0.04 | 0.12 | 0.04 | 0.05 | 0.05 | 0.06 | 0.2 | 0.06 | 0.06 | 0.06 | 0.09 | 0.29
105 | TC | 965 | 914 | 835 | 762 | 710 | 1008 | 957 | 877 | 804 | 758 | 1036 | 986 | 905 | 834 | 798 | 1058 | 1006 | 926 | 858 | 836
| SHC | 277 | 345 | 458 | 568 | 672 | 295 | 377 | 513 | 648 | 744 | 313 | 409 | 567 | 722 | 798 | 332 | 440 | 620 | 793 | 836
| kW | 84.9 | 84.4 | 83.8 | 83.7 | 83.4 | 85.5 | 84.8 | 84.1 | 83.7 | 83.2 | 86 | 85.2 | 84.3 | 83.7 | 83.5 | 86.5 | 85.5 | 84.5 | 83.8 | 83.6
| BF | 0 | 0.01 | 0.02 | 0.03 | 0.08 | 0.01 | 0.03 | 0.04 | 0.04 | 0.14 | 0.04 | 0.05 | 0.05 | 0.06 | 0.22 | 0.06 | 0.06 | 0.06 | 0.1 | 0.3
115 | TC | 903 | 855 | 780 | 714 | 664 | 940 | 892 | 817 | 748 | 712 | 965 | 917 | 842 | 777 | 748 | 984 | 935 | 860 | 803 | 783
| SHC | 233 | 304 | 418 | 536 | 626 | 248 | 332 | 471 | 608 | 700 | 264 | 361 | 523 | 680 | 748 | 282 | 391 | 575 | 735 | 783
| kW | 95.3 | 95 | 95 | 95.6 | 95.6 | 95.7 | 95.2 | 94.9 | 95.1 | 94.9 | 96 | 95.4 | 94.9 | 94.8 | 94.9 | 96.3 | 95.6 | 95 | 94.6 | 94.7
| BF | 0 | 0.01 | 0.02 | 0.03 | 0.1 | 0.01 | 0.03 | 0.04 | 0.05 | 0.16 | 0.04 | 0.05 | 0.05 | 0.07 | 0.24 | 0.06 | 0.06 | 0.07 | 0.12 | 0.32
48/50 090 (90 TON) HIGH- CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
36000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57
75 | TC | 1281 | 1220 | 1124 | 1038 | 1014
| SHC | 497 | 611 | 803 | 978 | 1014
| kW | 65.6 | 64.4 | 62.5 | 60.9 | 60.4
| BF | 0.07 | 0.07 | 0.08 | 0.11 | 0.33
85 | TC | 1216 | 1157 | 1066 | 986 | 967
| SHC | 450 | 566 | 760 | 935 | 967
| kW | 71.8 | 70.5 | 68.7 | 67.2 | 66.8
| BF | 0.07 | 0.08 | 0.08 | 0.11 | 0.34
95 | TC | 1148 | 1092 | 1005 | 934 | 919
| SHC | 402 | 520 | 717 | 888 | 919
| kW | 78.8 | 77.7 | 75.9 | 74.7 | 74.5
| BF | 0.07 | 0.08 | 0.08 | 0.13 | 0.35
105 | TC | 1074 | 1022 | 942 | 881 | 867
| SHC | 352 | 471 | 672 | 837 | 867
| kW | 86.9 | 85.8 | 84.7 | 83.9 | 83.8
| BF | 0.07 | 0.08 | 0.08 | 0.14 | 0.37
115 | TC | 998 | 949 | 874 | 824 | 812
| SHC | 300 | 421 | 624 | 783 | 812
| kW | 96.5 | 95.8 | 95 | 94.6 | 94.6
| BF | 0.07 | 0.08 | 0.08 | 0.16 | 0.38
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
118

## page 18
Performance data (cont)
Cooling Capacities (cont)
48/50P2,P3,P4,P5100 (100 TON) STANDARD CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 20000 |  |  |  |  | 25000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1146 | 1084 | 987 | 897 | 815 | 1203 | 1165 | 1042 | 949 | 873 | 1261 | 1167 | 1071 | 986 | 932
| SHC | 418 | 481 | 581 | 680 | 773 | 450 | 548 | 645 | 764 | 850 | 494 | 547 | 693 | 841 | 932
| kW | 67.9 | 66.6 | 64.7 | 63.1 | 61.7 | 69.1 | 68.7 | 65.9 | 64.1 | 62.5 | 70.6 | 68.5 | 66.5 | 64.8 | 63.9
| BF | 0 | 0.07 | 0.1 | 0.11 | 0.12 | 0.05 | 0.11 | 0.13 | 0.13 | 0.21 | 0.1 | 0.14 | 0.15 | 0.16 | 0.27
85 | TC | 1064 | 1005 | 946 | 856 | 779 | 1111 | 1053 | 991 | 913 | 836 | 1141 | 1089 | 1003 | 939 | 892
| SHC | 351 | 414 | 551 | 648 | 735 | 373 | 450 | 607 | 739 | 814 | 390 | 484 | 638 | 805 | 892
| kW | 74.1 | 72.8 | 71.6 | 70.1 | 68.7 | 75.2 | 73.9 | 72.5 | 71.1 | 69.5 | 76 | 74.8 | 73 | 71.5 | 70.8
| BF | 0 | 0.07 | 0.1 | 0.11 | 0.15 | 0.05 | 0.11 | 0.13 | 0.13 | 0.22 | 0.1 | 0.14 | 0.15 | 0.16 | 0.29
95 | TC | 1004 | 941 | 894 | 813 | 762 | 1042 | 995 | 906 | 857 | 814 | 1073 | 1024 | 945 | 889 | 850
| SHC | 306 | 365 | 511 | 614 | 719 | 321 | 408 | 535 | 695 | 793 | 340 | 437 | 596 | 767 | 850
| kW | 81.6 | 80.2 | 79.5 | 78.3 | 77.8 | 82.6 | 81.5 | 79.6 | 78.9 | 78.4 | 83.4 | 82.3 | 80.5 | 79.5 | 79
| BF | 0 | 0.07 | 0.1 | 0.11 | 0.16 | 0.06 | 0.11 | 0.13 | 0.14 | 0.23 | 0.1 | 0.14 | 0.15 | 0.17 | 0.3
105 | TC | 931 | 898 | 843 | 766 | 724 | 976 | 926 | 846 | 807 | 771 | 1003 | 955 | 866 | 836 | 805
| SHC | 251 | 337 | 474 | 579 | 683 | 274 | 356 | 490 | 658 | 753 | 291 | 387 | 533 | 727 | 805
| kW | 90 | 89.4 | 88.9 | 87.8 | 87.5 | 91.1 | 90 | 88.7 | 88.3 | 88 | 91.8 | 90.7 | 89 | 88.8 | 88.5
| BF | 0.01 | 0.07 | 0.1 | 0.11 | 0.18 | 0.06 | 0.11 | 0.13 | 0.14 | 0.25 | 0.11 | 0.14 | 0.15 | 0.17 | 0.32
115 | TC | 867 | 835 | 792 | 715 | 683 | 905 | 859 | 797 | 762 | 726 | 927 | 882 | 823 | 779 | 756
| SHC | 206 | 292 | 439 | 543 | 644 | 225 | 309 | 460 | 628 | 710 | 238 | 335 | 508 | 686 | 756
| kW | 100.2 | 99.7 | 99.9 | 98.8 | 98.7 | 100.9 | 100.1 | 99.5 | 99.5 | 99 | 101.4 | 100.6 | 99.7 | 99.5 | 99.4
| BF | 0.01 | 0.07 | 0.1 | 0.11 | 0.19 | 0.06 | 0.11 | 0.13 | 0.14 | 0.26 | 0.11 | 0.14 | 0.15 | 0.18 | 0.34
48/50P2,P3,P4,P5100 (100 TON) STANDARD CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 35000 |  |  |  |  | 40000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1273 | 1210 | 1133 | 1020 | 973 | 1296 | 1233 | 1157 | 1036 | 998
| SHC | 499 | 597 | 781 | 915 | 973 | 522 | 630 | 834 | 968 | 998
| kW | 70.8 | 69.4 | 68.1 | 65.5 | 64.6 | 71.4 | 70 | 68.7 | 65.9 | 65
| BF | 0.13 | 0.16 | 0.17 | 0.19 | 0.35 | 0.16 | 0.18 | 0.19 | 0.22 | 0.41
85 | TC | 1164 | 1107 | 1024 | 969 | 917 | 1186 | 1130 | 1043 | 967 | 964
| SHC | 408 | 510 | 685 | 875 | 917 | 429 | 543 | 734 | 906 | 964
| kW | 76.6 | 75.3 | 73.4 | 72.2 | 71 | 77.2 | 75.8 | 74 | 72.3 | 72.1
| BF | 0.14 | 0.16 | 0.17 | 0.19 | 0.36 | 0.16 | 0.18 | 0.19 | 0.23 | 0.42
95 | TC | 1096 | 1044 | 961 | 914 | 886 | 1114 | 1059 | 979 | 935 | 876
| SHC | 359 | 465 | 638 | 829 | 886 | 377 | 490 | 687 | 875 | 876
| kW | 84 | 82.8 | 80.9 | 79.9 | 79.5 | 84.5 | 83.2 | 81.4 | 80.3 | 79
| BF | 0.14 | 0.16 | 0.17 | 0.2 | 0.38 | 0.16 | 0.18 | 0.19 | 0.25 | 0.43
105 | TC | 1021 | 974 | 900 | 860 | 838 | 1037 | 990 | 918 | 886 | 825
| SHC | 306 | 415 | 595 | 782 | 838 | 322 | 442 | 644 | 828 | 825
| kW | 92.4 | 91.2 | 89.7 | 89.1 | 88.9 | 92.8 | 91.7 | 90.1 | 89.6 | 88.2
| BF | 0.14 | 0.16 | 0.17 | 0.22 | 0.39 | 0.16 | 0.18 | 0.19 | 0.27 | 0.45
115 | TC | 944 | 901 | 833 | 806 | 787 | 824 | 955 | 913 | 841 | 813
| SHC | 252 | 363 | 547 | 729 | 787 | 765 | 265 | 388 | 586 | 813
| kW | 101.8 | 100.9 | 99.9 | 99.8 | 99.7 | 100 | 102.1 | 101.2 | 100 | 99.9
| BF | 0.14 | 0.16 | 0.17 | 0.24 | 0.41 | 0.27 | 0.16 | 0.18 | 0.2 | 0.46
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
121

## page 19
Performance data (cont)
Cooling Capacities (cont)
48/50P2,P3,P4,P5100 (100 TON) HIGH-CAPACITY COIL — SUBCOOL MODE
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 20000 |  |  |  |  | 25000 |  |  |  |  | 30000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1210 | 1148 | 1077 | 994 | 900 | 1255 | 1205 | 1119 | 1042 | 951 | 1306 | 1243 | 1145 | 1080 | 1025
| SHC | 417 | 489 | 633 | 756 | 848 | 433 | 531 | 687 | 843 | 924 | 470 | 571 | 738 | 929 | 1025
| kW | 69.7 | 68.3 | 66.8 | 65.4 | 64.1 | 70.8 | 69.6 | 67.7 | 66.2 | 64.1 | 72.1 | 70.6 | 68.4 | 67 | 66
| BF | 0 | 0.01 | 0.03 | 0.03 | 0.06 | 0.01 | 0.04 | 0.04 | 0.05 | 0.13 | 0.04 | 0.05 | 0.06 | 0.07 | 0.19
85 | TC | 1152 | 1116 | 1016 | 942 | 863 | 1204 | 1140 | 1077 | 993 | 933 | 1274 | 1213 | 1136 | 1029 | 981
| SHC | 374 | 471 | 584 | 714 | 811 | 398 | 482 | 658 | 806 | 907 | 461 | 560 | 745 | 889 | 981
| kW | 76.4 | 75.5 | 73.3 | 72.6 | 71.7 | 77.7 | 76.2 | 74.8 | 73.2 | 72.4 | 79 | 77.6 | 76.2 | 73.8 | 73.1
| BF | 0 | 0.01 | 0.03 | 0.03 | 0.08 | 0.01 | 0.04 | 0.04 | 0.05 | 0.14 | 0.04 | 0.06 | 0.06 | 0.07 | 0.21
95 | TC | 1091 | 1035 | 965 | 876 | 825 | 1139 | 1083 | 1017 | 926 | 890 | 1171 | 1110 | 1026 | 975 | 935
| SHC | 329 | 405 | 546 | 659 | 774 | 350 | 441 | 614 | 752 | 866 | 370 | 471 | 650 | 848 | 935
| kW | 84.2 | 82.9 | 81.9 | 80.7 | 80.9 | 85.4 | 84.1 | 82.8 | 81.3 | 81.3 | 86.3 | 84.8 | 82.9 | 82.3 | 81.8
| BF | 0 | 0.01 | 0.03 | 0.03 | 0.09 | 0.01 | 0.04 | 0.04 | 0.05 | 0.15 | 0.04 | 0.05 | 0.06 | 0.07 | 0.22
105 | TC | 1027 | 1000 | 909 | 824 | 758 | 1068 | 1013 | 957 | 888 | 844 | 1097 | 1041 | 924 | 919 | 885
| SHC | 283 | 387 | 505 | 621 | 709 | 300 | 390 | 571 | 728 | 823 | 318 | 422 | 567 | 805 | 885
| kW | 93.4 | 93.2 | 92 | 91.3 | 90.3 | 94.3 | 93.2 | 92.7 | 92.2 | 91.8 | 95 | 93.8 | 91.7 | 92.4 | 92.2
| BF | 0 | 0.01 | 0.03 | 0.03 | 0.11 | 0.02 | 0.04 | 0.04 | 0.05 | 0.17 | 0.05 | 0.05 | 0.06 | 0.08 | 0.24
115 | TC | 960 | 935 | 849 | 789 | 715 | 987 | 929 | 892 | 811 | 794 | 1010 | 971 | 893 | 844 | 810
| SHC | 237 | 342 | 476 | 602 | 669 | 242 | 327 | 541 | 668 | 775 | 255 | 374 | 556 | 736 | 810
| kW | 104.3 | 104.5 | 103.8 | 104.7 | 102.8 | 104.7 | 103.8 | 104.2 | 103.5 | 104.2 | 105.2 | 104.6 | 103.7 | 103.3 | 103.1
| BF | 0.01 | 0.02 | 0.03 | 0.03 | 0.13 | 0.02 | 0.04 | 0.05 | 0.06 | 0.19 | 0.05 | 0.05 | 0.06 | 0.1 | 0.26
48/50P2,P3,P4,P5100 (100 TON) HIGH-CAPACITY COIL — SUBCOOL MODE (cont)
Temp (F) Air Entering Condenser (Edb) |  | Evaporator Air Quantity — Cfm
|  | 35000 |  |  |  |  | 40000
Evaporator Air — Ewb (F)
|  | 75 | 72 | 67 | 62 | 57 | 75 | 72 | 67 | 62 | 57
75 | TC | 1334 | 1272 | 1173 | 1099 | 1046 | 1356 | 1293 | 1220 | 1135 | 1114
| SHC | 494 | 609 | 800 | 996 | 1046 | 517 | 646 | 885 | 1072 | 1114
| kW | 72.9 | 71.4 | 69.1 | 67.3 | 66.2 | 73.6 | 72 | 69.8 | 68.2 | 67.7
| BF | 0.06 | 0.07 | 0.07 | 0.09 | 0.28 | 0.08 | 0.08 | 0.09 | 0.13 | 0.35
85 | TC | 1302 | 1263 | 1111 | 1056 | 1018 | 1323 | 1262 | 1129 | 1078 | 1051
| SHC | 487 | 621 | 753 | 962 | 1018 | 510 | 636 | 809 | 1010 | 1051
| kW | 79.7 | 79.1 | 75.7 | 74.4 | 73.5 | 80.3 | 78.9 | 76.2 | 74.9 | 74.2
| BF | 0.06 | 0.07 | 0.07 | 0.1 | 0.29 | 0.08 | 0.09 | 0.09 | 0.14 | 0.36
95 | TC | 1194 | 1138 | 1049 | 991 | 978 | 1208 | 1147 | 1067 | 1014 | 1012
| SHC | 391 | 510 | 708 | 904 | 978 | 407 | 535 | 765 | 949 | 1012
| kW | 87 | 85.6 | 83.5 | 82.3 | 82.3 | 87.5 | 85.9 | 83.9 | 82.6 | 82.8
| BF | 0.06 | 0.07 | 0.07 | 0.11 | 0.3 | 0.08 | 0.09 | 0.09 | 0.15 | 0.37
105 | TC | 1117 | 1058 | 976 | 935 | 925 | 1133 | 1080 | 995 | 972 | 957
| SHC | 337 | 451 | 654 | 850 | 925 | 355 | 490 | 711 | 915 | 957
| kW | 95.6 | 94.2 | 92.7 | 92.2 | 92.4 | 96.1 | 94.7 | 93 | 92.9 | 92.7
| BF | 0.07 | 0.07 | 0.07 | 0.13 | 0.32 | 0.08 | 0.09 | 0.09 | 0.18 | 0.38
115 | TC | 1037 | 980 | 902 | 889 | 869 | 1050 | 994 | 911 | 896 | 898
| SHC | 281 | 396 | 602 | 808 | 869 | 298 | 428 | 649 | 837 | 898
| kW | 105.8 | 104.7 | 103.6 | 104.2 | 104.1 | 106.2 | 105 | 103.7 | 103.8 | 104.1
| BF | 0.07 | 0.07 | 0.08 | 0.15 | 0.34 | 0.08 | 0.09 | 0.09 | 0.19 | 0.4
LEGEND 48/50 VAV units only. BF — Bypass Factor kW — Compressor Motor Power Input Edb — Entering Dry Bulb SHC — Sensible Heat Cap. (1000 Btuh) Ewb — Entering Wet Bulb TC — Total Cap. (1000 Btuh) Gross NOTES: 1. The SHC is based on 80°F edb temperature of air entering evapo- rator coil. For edb temperatures other than 80°F, adjust SHC by multiplying the correction factor and the cfm and then adding or subtracting the value from the SHC.
124